## Appliances (hidden)
Appliance - 0 BTUH | 0 | 1200
Appliance - 1200 BTUH | 1200
Appliance - 2400 BTUH | 2400

## Plants (hidden)
Plants - Small | 10
Plants - Medium | 20
Plants - Large | 30

## Blower (hidden)
Manufacturer's performance data has blower heat discount | 0
Manufacturer's performance data has no blower heat discount | 1707

## Home
Welcome to the electronic spreadsheet version (MJ8AE) of the ACCA
Manual J, 8th Edition, Abridged Version.
A thorough understanding of the printed MJ8AE manual as well as a working knowledge of Microsoft
Excel are prerequisites for using this spreadsheet.
To minimize data entry, this spreadsheet uses revised versions of the printed MJ8AE worksheets.
The header portion of the J1 Form must be populated with design data from your geographical region.
The five tabs labeled Doors, Glass, Walls, Ceilings and Floors must be populated with building
component information that is commonly used in your construction market. This information will then
be used as various lookup tables on the J1 Form and Glass Schedule tabs.
Once the header portion of the J1 Form and the five building attribute tabs are populated you may now
select from these options using lookup tables on the J1 Form and Glass Schedule to create default
templates to minimize data selection for future load calculations.
We strongly suggest that you refer to the training video including on the CD for step-by-step instructions
to quickly learn the features of this spreadsheet.

## Read Me
MJ8AE Capabilities and Sensitivities
MJ8ae is an abridged version of the Eighth Edition of Manual J. It provides an introduction to residential heat-loss and heat gain procedures. Mastery of the material in this guide is a prerequisite for using the unabridged version of Manual J. Mastery of this material is a prerequisite for using third party software products that perform Manual J calculations. MJ8ae assumes the practitioner is acquainted (or will become familiar with) with the basic principles of mathematics and heat transfer; and is conversant with Manual S, Manual D and Manual T design procedures.
Limitations and Guidelines
System design plays an important role in the comfort, health and safety of the occupants. MJ8AE may be used to estimate heat loss and heat gain for residential applications that have the following attributes.
● | Cooling is provided by a central, single-zone, constant volume system (MJ8ae shall not be used for zoned systems).
● | Single family detached dwellings shall have a normal amount of fenestration (total area of windows, glass doors and skylights shall not be more than 15 percent of the floor area).
● | Windows and glass doors shall be equitably distributed around all sides of the dwelling.
● | There shall be no large skylights in any room (skylight load area does not exceed 5% of floor area).
● | The dwelling shall have adequate exposure diversity (see MJ8ae Appendix 3).
● | There shall be no excursion adjustment for the sensible gain produced by the fenestration (see MJ8ae Appendix 3).
● | Windows and glass doors shall have clear glass; skylights shall have a clear glazing.
● | The dwelling shall have wood-frame or block (concrete or cinder) walls with brick, stucco or siding.
● | The dwelling shall have a dark shingle roof.
● | Attics shall be vented to FHA standards and shall have no radiant barrier.
● | Envelope leakage shall be estimated by the Table 5A air-change method (see MJ8ae, Section 3-10).
● | Simple default values for the appliance load shall be used to estimate internal gains.
● | A duct system shall be entirely in the conditioned space, or shall be compatible with one of the system scenarios summarized by Figure 1-1 of MJ8ae Section 1.
● | Duct run leakage shall be equal to the default values (for sealed ducts and unsealed ducts), unless verified by a field leakage test (see MJ8ae, Section 3-12).
● | Engineered ventilation can be provided by piping a small amount (50 CFM or less) of fresh air to the return-side of the duct system (see MJ8ae, Section 3-13).
● | Heating shall be provided by a hot air system or electric baseboard heat.
Procedural Defaults
Procedural complexity increases in proportion to sensitivity to variations in construction detail. Defaults simplify the procedure and make hand calculations possible. The defaults that apply to MJ8AE are listed here.
Design Conditions
● | Indoor: Heating = 70 F; Cooling = 75 db F and 50% RH, unless superceded by code.
● | Outdoor: Use values in Table 1A of this guide, unless superceded by code.
Windows and Glass Doors
● | Window and glass doors shall have clear (single, double or triple pane) glass.
● | Window and glass door framing shall be metal, metal with break, wood or vinyl.
● | Windows can have fixed or operable sash (sliding glass doors have an operable sash).
● | Purpose-built daylight windows and skylights shall have no internal shade.
● | All other windows and glass doors shall have internal shade.
● | The default assumption for internal shade is a medium-color blind with the slats at 45 degrees.
● | Windows and glass doors shall not be equipped with external sunscreens.
● | An overhang adjustment shall be applied to all windows and glass doors.
● | When the information is available, use the actual overhang geometry or use the default geometry.
● | The default length of the overhang is one foot; the default height above the glazing is one foot.
● | The heat-gain adjustment for any type of bug screen shall be 0.90.
● | The heat loss and gain adjustment for a bay window shall be 1.15.
● | The heat loss adjustments for a garden window shall be 2.75 and the heat gain adjustment shall be 2.00.
● | The heat gain adjustment for a French door shall be 0.70.
● | The foreground reflectance for window and glass door heat-gain shall be 0.20.
Skylights
● | Skylight glazing shall be flat.
● | Skylights shall have clear (single pane or double pane) glass.
● | Curb construction shall default to (un-insulated) wood 2x4; four inches high.
● | Skylights shall not be equipped with an internal shade.
● | Skylights shall not be equipped with a light shaft
Wood and Metal Doors
● | Door glass area shall be ignored if the door glass area is less than or equal to 50% of the total door area.
● | The French door option shall apply if the door glass area is more than 50% of the total door area.
Walls
● | Above grade wall construction shall be wood-stud frame or empty-core block.
● | Exterior finish options shall be brick veneer or stucco/siding.
● | Interior finish shall default to gypsum board (i.e. plaster board, dry-wall, sheet rock, etc.)
● | Below grade wall construction shall default to empty-core block.
● | Block walls may have board insulation and/or wood-stud framing with blanket or fill insulation.
Ceilings and Attic Knee Walls
● | The ceiling options shall be: Attic ceiling, ceiling on exposed beams or joist-ceiling sandwich.
● | The roofing material shall be dark-shingles.
● | The roof deck material shall default to plywood for all types of roof construction.
● | Attic construction shall default to FHA-vented with no radiant barrier.
● | Knee walls shall be installed in a FHA-vented attic space.
● | Insulation shall be blanket and/or board or fill (as appropriate for the type of roof construction).
Floors
● | All floors shall be passive (no heating elements below the floor).
● | Floors over an open space shall have carpet or tile cover with floor insulation options.
● | Slab floors shall have vertical insulation that covers the edge, or no insulation.
● | Slab floor soil conditions shall be heavy-moist; heavy-dry; light-wet; or light-dry.
● | Basement floors shall be un-insulated.
● | Floors over a closed space shall default to no wall insulation (for closed space), with floor insulation options.
● | Floors over a closed space shall default to construction 19A (Table 4A, MJ8).
Infiltration
● | All infiltration estimates shall be based on the ACH values provided by Table 5A of this guide.
● | Dwellings shall be rated: very-tight, semi-tight, average, semi-loose and loose (definitions are provided).
● | There shall be no space pressure adjustment for engineered ventilation that affects space pressure
● | Infiltration induced or reduced by duct runs in an unconditioned space is evaluated by the duct-table factors.
Internal Gains
● | The number occupants shall equal the number of bedrooms plus one.
● | The internal appliance-gain options are 1,200 BTU/h or 2,400 BTU/h.
● | The latent gain produced by plants shall be evaluated
Duct Systems
● | All duct runs shall be in the conditioned space, or shall conform to one of the Table 7 scenarios.
● | Duct runs (trunks and runouts) shall be (essentially) installed in one horizontal plane.
● | Leakage rates for sealed ducts shall default to 0.12 (supply-side) and 0.24 (return-side) CFM per Ft2 unless a tighter rating is justified by a duct leakage test.
● | The supply air temperature for heating shall default to 100oF (worst case for the heating load factor).
Engineered Ventilation
● | Engineered ventilation is mandatory when required by code (the ventilation rate also may be determined by code).
● | Table 8 shall be used to evaluate the fresh air requirement (ventilation rate) when there is no code requirement.
● | Table 8 offers guidance with no expressed or implied guarantee or warrantee; compliance is not mandatory.
● | The system designer shall evaluate (by tests specified in codes and standards) the potential for pressure conditions that could cause combustion appliance back-drafting.
● | If the designer elects to provide engineered ventilation, fresh air shall be provided by piping outdoor air to the return-side of the duct system (refer to the unabridged version of Manual J if the flow rate of outdoor air exceeds 50 CFM).
Blower Heat
● | A blower heat adjustment shall be made when manufacturer’s performance data is not discounted for blower heat.
● | The blower heat adjustment shall be 500 Watts (1,707 BTU/h).
Limitation
The principles and procedures presented in this guide apply to any dwelling that is 100 percent compatible with preceding list of limitations, guidelines and defaults. The unabridged version of Manual J shall be used for any and all dwellings that are not compatible with the above list.
Application
A heat loss and heat gain estimate is the mandatory first-step in the system design process. This information is used to select heating and cooling equipment. This information and the information provided by equipment manufacturer performance data is used to determine system airflow rate and room airflow rates, supply outlet and return grille sizes and duct sizes (per Manual S, D and T protocols).
Comfort and Air Quality
Incorrect system design procedures (or installation, commissioning, maintenance and operating practices) may cause comfort and air quality problems. Individuals and organizations not familiar with Manual J, Manual S and Manual D procedures tend to assume the problem is caused by equipment that is too small. This is normally not the case. See Appendix 7 (Trouble Shooting) for more information on this subject.
Hand Calculations
The tables and equations in this guide are a subset of the tables and equations provided by the unabridged edition of Manual J. This simplification produces a procedure that can be performed without the aid of a computer. A computer is strongly recommended for full, unrestricted applications of Manual J (refer to www.acca.org for recommended third-party software recognized by ACCA).

## Cities (hidden)
Location | Elevation | Latitude | 99%db | 1% db | wb | 55 | 50 | 45 | DR |  | Alabama | 0 | Alabama | Alaska | Arizona | Arkansas | California | Colorado | Connecticut | Delaware | DC | Florida | Georgia | Hawaii | Idaho | Illinois | Indiana | Iowa | Kansas | Kentucky | Louisiana | Maine | Maryland | Massachusetts | Michigan | Minnesota | Mississippi | Missouri | Montana | Nebraska | Nevada | New Hampshire | New Jersey | New Mexico | New York | North Carolina | North Dakota | Ohio | Oklahoma | Oregon | Pennsylvania | Rhode Island | South Carolina | South Dakota | Tennessee | Texas | Utah | Vermont | Virginia | Washington | West Virginia | Wisconsin | Wyoming | 45% | 9 | 8
, | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 | Alaska | #N/A | Alexander City | Adak, NAS | Douglas AP | Blytheville AFB | Alameda, NAS | Alamosa AP | Bridgeport AP | Dover AFB | Andrews AFB | Apalachicola | Albany, Turner | Ewa, Barbers Point NAS | Boise AP | Aurora | Anderson | Ames | Atchison | Ashland | Alexandria AP | Augusta AP | Balitimore AP | Boston AP | Adrian 798 | Albert Lea | Biloxi, Keesler AFB | Cape Girardeau | Billings AP | Beatrice | Carson City | Berlin | Atlantic City CO | Alamagordo Holloman AFB | Albany AP | Asheville AP | Bismark AP | Akron-Canton AP | Ada | Albany | Allentown AP | Newport | Anderson | Aberdeen AP | Athens | Abilene AP | Cedar City AP | Barre | Charlottsville | Aberdeen | Beckley | Appleton | Big Piney | 50% | 8
Database | [9 empty] | 3 | Arizona | #N/A | Anniston AP | Anchorage IAP | Flagstaff Ap | Camden | Bakersfield AP | Boulder | Hartford, Brainard Field | Wilmington AP | Reagan National AP | Belle Glade | Americus | Hilo AP | Burley | Belleville, Scott AFB | Bedford | Burlington AP | Chante AP | Bowling Green AP | Baton Rouge AP | Bangor, Dow AFB | Balitimore CO | Clinton | Alpena AP | Alexandria AP | Clarksdale | Columbia AP | Bozeman | Bellevue, Offutt AFB | Elko AP | Claremont | Long Branch | Albuquerque AP | Albany CO | Cape Hatteras | Devil’s Lake | Ashtabula | Altus AFB | Astoria AP | Altoona CO | Providence AP | Beaufort, MCAS | Brookings | Bristol-Tri City AP | Alice AP | Logan | Burlington AP | Danville AP | Bellingham AP | Bluefield AP | Ashland | Casper AP | 55% | 7
Alabama, Alexander City | 686 | 33 | 22 | 93 | 76 | 39 | 46 | 52 | Medium | 4 | Arkansas | #N/A | Auburn | Anchorage, Elemendorf AFB | Fort Huachuca AP | El Dorado AP | Barstow | Colarado Springs AP | New Haven AP |  |  | Cape Kennedy AP | Athens | Honolulu AP | Coeur D’Alene AP | Bloomington | Bloomington | Cedar Rapids AP | Concordia | Corbin AP | Bogalusa | Brunswick, NAS | Cumberland | East Falmouth, Otis ANGB | Battle Creek AP | Bemidji AP | Columbus AFB | Farmington AP | Butte AP | Chadron AP | Ely AP | Concord AP | Millville | Artesia | Auburn | Charlotte AP | Dickinson AP | Athens | Ardmore | Baker AP | Bradford |  | Charleston AFB | Chamberlain | Chattanooga AP | Amarillo AP | Moab | Montpelier/ Barre | Fort Belvoir | Bremerton | Charleston AP | Beloit | Cheyene AP
Alabama, Anniston AP | 612 | 33 | 24 | 93 | 76 | 39 | 46 | 52 | Medium | 5 | California | #N/A | Birmingham AP | Anchorage, Fort Richardson | Kingman AP | Fayetteville AP | Blue Canyon | Craig | New London |  |  | Daytona Beach AP | Atlanta AP | Kahului | Idaho Falls AP | Carbondale | Columbus, Bakalar AFB | Clinton | Dodge City AP | Covington AP | Bossier City, Barksdale AFB | Caribou AP | Fredrick AP | Fall River | Benton Harbor AP | Brainerd | Greenville AFB | Hannibal | Cut Bank AP | Columbus | Las Vegas AP | Keene | Newark AP | Carlsbad AP | Bafavia | Cherry Point MCAS | Fargo AP | Bowling Green | Bartlesville | Bend | Butler |  | Charleston CO | Huron AP | Clarksville | Austin AP | Ogden, Hill AFB | Rutland | Fredricksburg | Ellensburg AP | Clarksburg | Eau Claire AP | Cody AP | Low | L
Alabama, Auburn | 776 | 32 | 22 | 93 | 76 | 39 | 46 | 52 | Medium | 6 | Colorado | #N/A | Decatur | Annette | Nogalas | Fort Smith AP | Blythe AP | Denver AP | Norwalk |  |  | Fort Lauderdale | Augusta AP | Kaneohe Bay MCAS | Kamiah | Champaign/Urbana | Crawfordsville | Council Bluffs | El Dorado | Fort Knox, Godman AAF | Houma | Lewiston | Hagerstown | Framingham | Detroit | Duluth AP | Greenwood | Jefferson City | Glasgow AP | Fremont | Lovelock AP | Laconia | New Brunswick | Clayton | Binghampton AP | Durham | Grands Forks AP | Cambridge | Chickasha | Corvallis | Chambersburg |  | Columbia AP | Mitchell | Columbia | Bay City | Price |  | Hampton, Langley AFB | Everett-Paine AFB | Elkins AP | Fond du Lac | Evanston | Medium | M
Alabama, Birmingham AP | 644 | 33 | 23 | 92 | 75 | 34 | 41 | 47 | Medium | 7 | Connecticut | #N/A | Dothan AP | Barrow | Page | Hot Springs | Burbank AP | Durango | Norwich |  |  | Fort Myers AP | Brunswick | Lihue | Lewiston AP | Chicago, Meigs Field | Evansville AP | Des Moines AP | Emporia | Hopkinsville, Campbell AFB | Lafayette AP | Limestone, Loring AFB | Lex Park, Patuxent River NAS | Gloucester | Escanaba | Fairbault | Hattiesburg | Joplin AP | Glendive | Grand Island AP | Mercury | Lebanon | Patterson | Clovis, Cannon AFB | Buffalo AP | Elizabeth City AP | Jamestown AP | Chilicothe | Enid-Vance AFB | Eugene AP | DuBois |  | Florence AP | Pierre AP | Crossville | Beaumont | Provo |  | Harrisonburg | Hanford | Huntington CO | Green Bay AP | Gillette | High | H
Alabama, Decatur | 592 | 34 | 16 | 93 | 74 | 27 | 34 | 40 | Medium | 8 | Delaware | #N/A | Florence AP | Bethel | Phoenix AP | Jonesboro 262 | Chico | Eagle | Waterbury |  |  | Fort Pierce | Columbus, Fort Benning | Molokai | Moscow | Chicago, Midway AP | Fort Wayne AP | Debuque | Garden City AP | Jackson | Lake Charles AP | Millinocket AP | Salisbury | Greenfield | Flint AP | Fergus Falls | Jackson AP | Kansas City AP | Great Falls AP | Hastings | North Las Vega , Nellis AFB | Manchester, Grenier AFB | Phillipsburg | Farmington AP | Central Islip | Fayetteville, Pope AFB | Minot AP | Cincinnati, Lunken Field | Lawton AP | Grants Pass | Erie AP |  | Georgetown | Rapid City AP | Dyersburg | Beeville | Richfield |  | Lynchburg AP | Kennewick | Martinsburg AP | LaCrosse AP | Lander AP
Alabama, Dothan AP | 401 | 31 | 32 | 93 | 76 | 39 | 46 | 52 | Medium | 9 | DC | #N/A | Gadsden | Bettles | Phoenix, Luke AFB | Little Rock AP | Concord | Fort Collins | Windsor Locks, Bradlet Field |  |  | Gainsville AP | Columbus, Lawson AFB | Wahaiwa | Mountain Home AFB | Chicago, O’Hare AP | Goshen AP | Fort Dodge | Goodland AP | Lexington AP | Leesville, Fort Polk | Portland |  | Lawrence | Grand Rapids AP | Hibbing | Laurel | Kirksville AP | Great Falls, Malmstrom AFB | Kearney | Reno AP | Mount Washington | Teterboro | Gallup | Cortland | Goldsboro, Seymour | Minot, AFB | Cleveland AP | McAlester | Hillsboro | Harrisburg AP |  | Greenville AP/Greer | Sioux Falls AP | Greenville | Big Springs AP | St. George CO |  | Newport News | Longview | Morgantown AP | Madison AP | Laramie AP
Alabama, Florence AP | 581 | 34 | 21 | 94 | 75 | 31 | 38 | 44 | Medium | 10 | Florida | #N/A | Huntsville AP | Big Delta, Ft. Greely | Prescott AP | Pine Bluff AP | Covina | Grand Junction AP |  |  |  | Homestead, AFB | Columbus, Metro AP |  | Mullan | Chicago CO | Hobart | Iowa City | Great Bend | Louisville AP | Minden | Waterville |  | Lowell | Hancock | International Falls AP | McComb AP | Mexico | Havre | Lincoln CO | Reno CO | Portsmouth, Pease AFB | Trenton, McQuire AFB | Grants | Dunkirk | Goldsboro, Johnson AFB | Williston | Columbus AP | Muskogee AP | Klamath Falls AP | Johnstown |  | Greenwood | Watertown AP | Jackson AP | Brownsville AP | Salt Lake City AP |  | Norfolk AP | Moses Lake, Larson AFB | Parkersburg CO | Manitowoc | Newcastle
Alabama, Gadsden | 569 | 34 | 20 | 94 | 75 | 31 | 38 | 44 | Medium | 11 | Georgia | #N/A | Mobile AP | Cold Bay | Safford, Agri. Center | Texarkana AP | Crescent City AP | Greeley |  |  |  | Jacksonville AP | Dalton |  | Pocatello AP | Danville | Huntington | Keokuk | Hutchinson AP | Madisonville | Monroe AP |  |  | New Bedford | Harbour Beach | Mankato 1020 | Meridian AP | Moberly | Helena AP | McCook | Tonapah AP |  | Vineland | Hobbs AP | Elmira AP | Greensboro AP |  | Columbus, Rickenbckr AFB | Norman 1181 | Meacham | Lancaster |  | Myrtle Beach, AFB | Yankton | Knoxville AP | Brownwood | Vernal AP |  | Oceana, NAS | Olympia AP | Wheeling | Marinette | Rawlins
Alabama, Huntsville AP | 629 | 34 | 20 | 92 | 74 | 28 | 35 | 41 | Medium | 12 | Hawaii | #N/A | Mobile CO | Cordova | Tuscon Ap |  | Downey | LaJunta AP |  |  |  | Jacksonville/Cecil Field NAS | Dublin |  | Twin Falls AP | Decatur | Indianapolis AP (S) | Lamoni | Liberal | Owensboro | Natchitoches |  |  | Pittsfield AP | Holland | Minneapolis/St. Paul AP | Natchez | Poplar Bluff | Kalispell AP | Norfolk | Winnemucca AP |  |  | Las Cruces | Geneva | Greenville |  | Dayton AP | Oklahoma City AP | Medford AP | Meadville |  | Orangeburg |  | Memphis AP | Bryan AP |  |  | Petersburg | Port Angeles |  | Milwaukee AP | Rock Springs AP
Alabama, Mobile AP | 218 | 30 | 30 | 92 | 76 | 41 | 48 | 54 | Medium | 13 | Idaho | #N/A | Montgomery AP | Deadhorse | Winslow AP |  | El Cajon | Leadville |  |  |  | Jacksonville, Mayport Naval | Gainesville |  |  | Dixon | Jeffersonville | Marshalltown | Manhattan, Fort Riley | Paducah AP | New Orleans AP |  |  | Springfield, Westover AFB | Jackson AP | Redwood Falls | Tupelo | Rolla | Lewiston AP | North Platte AP |  |  |  | Los Alamos | Glens Falls | Henderson |  | Dayton, Wright/Paterson AFB | Oklahoma City, W.Rogers AP | North Bend | New Castle |  | Rock Hill |  | Murfreesboro | Corpus Christi AP |  |  | Quantico MCAS | Quillayute |  | Racine | Sheridan AP
Alabama, Mobile CO | 26 | 30 | 29 | 93 | 77 | 46 | 53 | 59 | Medium | 14 | Illinois | #N/A | Ozark, Fort Rucker | Dillingham | Yuma AP |  | El Centro AP | Limon |  |  |  | Key West AP | Griffin |  |  | Elgin | Kokoma | Mason City AP | Parsons |  | New Orleans, Lakefront AP |  |  | Tauton | Kalamazoo | Rochester AP | Vicksburg CO | St. Joseph AP | Livingston AP | Omaha AP |  |  |  | Raton AP | Gloversville | Hickory |  | Defiance | Ponca City | Pendleton AP | Philadelphia AP |  | Spartanburg AP |  | Nashville AP | Corsicana |  |  | Richmond AP | Seattle-Boeing Fld |  | Sheboygan | Torrington
Alabama, Montgomery AP | 221 | 32 | 27 | 93 | 76 | 39 | 46 | 52 | Medium | 15 | Indiana | #N/A | Selma-Craig AFB | Fairbanks IAP |  |  | Escondido | Pueblo AP |  |  |  | Lakeland CO | La Grange |  |  | Freeport | Layfayette | Newton | Russel AP |  | Shreveport AP |  |  | Weymouth, S. Weymouth Nas | Lansing AP | St. Cloud AP |  | St. Louis AP | Miles City AP | Omaha WSO |  |  |  | Roswell, Walker AFB | Hornell | Jacksonville |  | Finlay AP | Seminole | Portland AP | Philadelphia, Northeast AP |  | Sumter-Shaw AFB |  | Tullahoma | Dallas, Fort Worth AP |  |  | Roanoke AP | Seattle CO |  | Stevens Point | Worland
Alabama, Ozark, Fort Rucker | 356 | 31 | 31 | 94 | 77 | 44 | 51 | 57 | Medium | 16 | Iowa | #N/A | Talladega | Fairbanks, Eielson AFB |  |  | Eureaka/Arcata AP | Sterling |  |  |  | Melbourne | Macon AP |  |  | Galesburg | LaPorte | Ottumwa AP | Salina |  |  |  |  | Worcester AP | Marquette CO | Tofte |  | St. Louis CO | Missoula AP | Scottsbluff AP |  |  |  | Santa Fe CO | Ithaca | Lumberton |  | Fremont | Stillwater | Portland CO | Philadelphia, Willow Gr NAS |  |  |  |  | Del Rio, Laughlin AFB |  |  | Staunton | Seattle-Tacoma AP |  | Waukesha
Alabama, Selma-Craig AFB | 166 | 32 | 26 | 95 | 77 | 42 | 49 | 55 | Medium | 17 | Kansas | #N/A | Tuscaloosa AP | Galena |  |  | Fairfield-Travis AFB | Trinidad AP |  |  |  | Miami AP | Marietta, Dobbins AFB |  |  | Glenview, NAS | Marion | Sioux City AP | Topeka AP | [5 empty] | Marquette, Sawyer AFB | Virginia |  | Sedalia, Whiteman AFB |  | Sidney AP |  |  |  | Silver City AP | Jamestown | New Bern AP |  | Hamilton | Tulsa AP | Redmond | Pittsburgh AP |  |  |  |  | Denton |  |  | Sterling | Spokane AP |  | Wausau AP
Alabama, Talladega | 528 | 33 | 22 | 94 | 76 | 37 | 44 | 50 | Medium | 18 | Kentucky | #N/A |  | Gulkana |  |  | Fresno AP |  |  |  |  | Miami CO | Moultrie |  |  | Greenville | Muncie | Spencer | Wichita AP | [5 empty] | Mount Clemens ANGB | Willmar |  | Sikeston |  | Valentine |  |  |  | Socorro AP | Kingston | Raleigh/Durham AP |  | Lancaster | Woodward | Roseburg AP | Pittsburgh, Allegheny AP |  |  |  |  | Eagle Pass |  |  | Reagan, National AP | Stampede Pass
Alabama, Tuscaloosa AP | 170 | 33 | 24 | 94 | 77 | 44 | 51 | 57 | Medium | 19 | Louisiana | #N/A |  | Homer |  |  | Hamiltion AFB |  |  |  |  | Miami, New Tamiami AP | Rome AP |  |  | Joliet | Peru, Bunker Hill AFB | Waterloo | Wichita, McConnell AFB | [5 empty] | Mt. Pleasant | Winona |  | Spickard/Trenton | [5 empty] | Truth or Consequences | Lockport | Rocky Mount |  | Lima |  | Salem AP | Reading CO |  |  |  |  | El Paso AP |  |  | Winchester | Tacoma-McChord AFB
Alaska, Adak, NAS | 19 | 52 | 23 | 57 | 53 | -18 | -11 | -5 | Low | 20 | Maine | #N/A |  | Juneau IAP |  |  | Laguna Beach |  |  |  |  | Milton, Whiting Field NAS | Savannah, Travis AP |  |  | Kankakee | Peru, Grsssom AFB | [7 empty] | Muskegon AP |  |  | Springfield AP | [5 empty] | Tucumcari AP | Massena AP | Wilmington AP |  | Mansfield AP |  | Sexton Summit | Scranton/Wilkes-Barre |  |  |  |  | Fort Worth, Carswell AFB |  |  |  | Walla Walla AP
Alaska, Anchorage IAP | 144 | 61 | -9 | 68 | 57 | -20 | -13 | -7 | Low | 21 | Maryland | #N/A |  | Kenai |  |  | Lemoore, Reeves NAS |  |  |  |  | Ocala | Valdosta, Moody AFB |  |  | LaSalle/Peru | Richmond AP | [7 empty] | Oscoda, Wurtsmith AFB |  |  | Warrensburg, Whiteman AFB | [6 empty] | Newburg-Stewart AFB | Winston-Salem AP |  | Marion |  | The Dalles | State College |  |  |  |  | Fort Worth, Meacham Field |  |  |  | Wenatchee
Alaska, Anchorage, Elemendorf AFB | 212 | 61 | -8 | 69 | 57 | -21 | -14 | -8 | Low | 22 | Massachusetts | #N/A |  | Ketchikan IAP |  |  | Livermore 500 |  |  |  |  | Orlando AP | Valdosta, Regional AP |  |  | Macomb | Shelbyville | [7 empty] | Pellston | [9 empty] | NYC-Central Park |  |  | Middletown |  |  | Sunbury |  |  |  |  | Galveston AP |  |  |  | Yakima AP
Alaska, Anchorage, Fort Richardson | 342 | 61 | -13 | 71 | 58 | -20 | -13 | -7 | Medium | 23 | Michigan | #N/A |  | King Salmon |  |  | Lompoc, Vandenburg AFB |  |  |  |  | Panama City, Tyndall AFB | Waycross |  |  | Marseilles | South Bend AP | [7 empty] | Pontiac | [9 empty] | NYC-Kennedy AP |  |  | Newark |  |  | Uniontown |  |  |  |  | Greenville
Alaska, Annette | 110 | 55 | 17 | 70 | 59 | -14 | -7 | -1 | Low | 24 | Minnesota | #N/A |  | Kodiak |  |  | Long Beach AP |  |  |  |  | Pensacola CO |  |  |  | Moline, Davenport AP | Terre Haute AP | [7 empty] | Port Huron | [9 empty] | NYC-La Guardia AP |  |  | Norwalk |  |  | Warren |  |  |  |  | Guadalupe Pass
Alaska, Barrow | 44 | 71 | 36 | 52 | 49 | -25 | -18 | -12 | Low | 25 | Mississippi | #N/A |  | Kotzebue |  |  | Los Angeles AP |  |  |  |  | St. Augustine |  |  |  | Mt. Vernon | Valparaiso | [7 empty] | Saginaw AP | [9 empty] | Niagra Falls AP |  |  | Portsmouth |  |  | West Chester |  |  |  |  | Harlingen
Alaska, Bethel | 123 | 61 | -24 | 68 | 57 | -20 | -13 | -7 | Medium | 26 | Missouri | #N/A |  | McGrath |  |  | Los Angeles CO |  |  |  |  | St. Petersburg |  |  |  | Peoria AP | Vincennes | [7 empty] | Sault Ste. Marie AP | [9 empty] | Olean |  |  | Sandusky CO |  |  | Williamsport AP |  |  |  |  | Houston AP
Alaska, Bettles | 643 | 67 | -44 | 75 | 59 | -22 | -15 | -9 | Medium | 27 | Montana | #N/A |  | Middleton Island |  |  | Marysville, Beale AFB |  |  |  |  | Sanford |  |  |  | Quincy AP | [8 empty] | Seul Choix Point | [9 empty] | Oneonta |  |  | Springfield |  |  | York |  |  |  |  | Houston, Hobby AP
Alaska, Big Delta, Ft. Greely | 1277 | 64 | -39 | 75 | 58 | -27 | -20 | -14 | Medium | 28 | Nebraska | #N/A |  | Nenana |  |  | Merced-Castle AFB |  |  |  |  | Sarasota/Bradenton |  |  |  | Rantoul, Chanute AFB | [8 empty] | Traverse City AP | [9 empty] | Oswego CO |  |  | Stubenville | [7 empty] | Huntsville
Alaska, Cold Bay | 98 | 55 | 10 | 57 | 53 | -18 | -11 | -5 | Low | 29 | Nevada | #N/A |  | Nome AP |  |  | Modesto |  |  |  |  | Tallahassee AP |  |  |  | Rockford | [8 empty] | Yipsilanti | [9 empty] | Plattsburg AFB |  |  | Toledo AP | [7 empty] | Junction
Alaska, Cordova | 42 | 60 | 1 | 67 | 57 | -18 | -11 | -5 | Medium | 30 | New Hampshire | #N/A |  | Northway |  |  | Monterey |  |  |  |  | Tampa AP |  |  |  | Springfield AP | [18 empty] | Poughkeepsie |  |  | Warren | [7 empty] | Killeen-Gray AFB
Alaska, Deadhorse | 61 | 70 | -34 | 61 | 54 | -21 | -14 | -8 | Medium | 31 | New Jersey | #N/A |  | Port Heiden |  |  | Mount Shasta |  |  |  |  | Valpariso, Eglin AFB |  |  |  | Waukegan | [18 empty] | Rochester AP |  |  | Wooster | [7 empty] | Kingsville, NAS
Alaska, Dillingham | 86 | 59 | -13 | 66 | 56 | -21 | -14 | -8 | Medium | 32 | New Mexico | #N/A |  | Saint Paul Island |  |  | Mountain View, Moffet NAS |  |  |  |  | Vero Beach |  |  |  | West Chicago | [18 empty] | Rome-Griffiss AFB |  |  | Youngstown AP | [7 empty] | Lamesa
Alaska, Fairbanks IAP | 434 | 64 | -41 | 77 | 59 | -26 | -19 | -13 | Medium | 33 | New York | #N/A |  | Sitka |  |  | Napa |  |  |  |  | West Palm Beach AP | [22 empty] | Schenectady |  |  | Zanesville AP | [7 empty] | Laredo AFB
Alaska, Fairbanks, Eielson AFB | 545 | 64 | -31 | 78 | 60 | -23 | -16 | -10 | Medium | 34 | North Carolina | #N/A |  | Talkeetna |  |  | Needles AP | [27 empty] | Suffolk County AFB | [10 empty] | Longview 365
Alaska, Galena | 152 | 64 | -31 | 74 | 59 | -21 | -14 | -8 | Medium | 35 | North Dakota | #N/A |  | Valdez |  |  | Oakland AP | [27 empty] | Syracuse AP | [10 empty] | Lubbock AP
Alaska, Gulkana | 1579 | 62 | -39 | 73 | 56 | -32 | -25 | -19 | Medium | 36 | Ohio | #N/A |  | Yakutat |  |  | Oceanside | [27 empty] | Utica | [10 empty] | Lubbock, Reese AFB
Alaska, Homer | 78 | 59 | 4 | 62 | 55 | -18 | -11 | -5 | Low | 37 | Oklahoma | #N/A |  |  |  |  | Ontario IAP | [27 empty] | Watertown | [10 empty] | Lufkin AP
Alaska, Juneau IAP | 19 | 58 | 7 | 69 | 58 | -17 | -10 | -4 | Low | 38 | Oregon | #N/A |  |  |  |  | Oxnard | [27 empty] | White Plains | [10 empty] | Marfa
Alaska, Kenai | 92 | 60 | -14 | 65 | 55 | -23 | -16 | -10 | Medium | 39 | Pennsylvania | #N/A |  |  |  |  | Palmdale AP | [38 empty] | McAllen
Alaska, Ketchikan IAP | 88 | 55 | 20 | 68 | 59 | -11 | -4 | 2 | Low | 40 | Rhode Island | #N/A |  |  |  |  | Palm Springs | [38 empty] | Midland AP
Alaska, King Salmon | 57 | 58 | -19 | 67 | 56 | -22 | -15 | -9 | Medium | 41 | South Carolina | #N/A |  |  |  |  | Pasadena | [38 empty] | Mineral Wells AP
Alaska, Kodiak | 73 | 57 | 12 | 65 | 56 | -19 | -12 | -6 | Low | 42 | South Dakota | #N/A |  |  |  |  | Paso Robles | [38 empty] | Palestine CO
Alaska, Kotzebue | 11 | 66 | -31 | 64 | 58 | -9 | -2 | 4 | Low | 43 | Tennessee | #N/A |  |  |  |  | Petaluma | [38 empty] | Pampa
Alaska, McGrath | 337 | 62 | -42 | 73 | 58 | -23 | -16 | -10 | Medium | 44 | Texas | #N/A |  |  |  |  | Pomona CO | [38 empty] | Pecos
Alaska, Middleton Island | 87 | 59 | 21 | 60 | 51 | -31 | -24 | -18 | Low | 45 | Utah | #N/A |  |  |  |  | Red Bluff | [38 empty] | Plainview
Alaska, Nenana | 362 | 64 | -44 | 76 | 59 | -24 | -17 | -11 | Medium | 46 | Vermont | #N/A |  |  |  |  | Redding AP | [38 empty] | Port Arthur AP
Alaska, Nome AP | 37 | 64 | -26 | 65 | 55 | -23 | -16 | -10 | Low | 47 | Virginia | #N/A |  |  |  |  | Redlands | [38 empty] | San Angelo, Goodfellow AFB
Alaska, Northway | 1716 | 62 | -32 | 74 | 57 | -29 | -22 | -16 | Medium | 48 | Washington | #N/A |  |  |  |  | Richmond | [38 empty] | San Antonio AP
Alaska, Port Heiden | 105 | 56 | -2 | 61 | 52 | -29 | -22 | -16 | Low | 49 | West Virginia | #N/A |  |  |  |  | Riverside-March AFB | [38 empty] | San Antonio, Kelly AFB
Alaska, Saint Paul Island | 63 | 57 | 3 | 52 | 50 | -22 | -15 | -9 | Low | 50 | Wisconsin | #N/A |  |  |  |  | Sacramento AP | [38 empty] | San Antonio, Randolph AFB
Alaska, Sitka | 21 | 57 | 21 | 64 | 58 | -9 | -2 | 4 | Low | 51 | Wyoming | #N/A |  |  |  |  | Sacramento, McClellan AFB | [38 empty] | Sanderson
Alaska, Talkeetna | 358 | 62 | -21 | 73 | 58 | -23 | -16 | -10 | Medium | 52 |  | #N/A |  |  |  |  | Sacramento, Metro | [38 empty] | Sherman-Perrin AFB
Alaska, Valdez | 120 | 61 | 7 | 66 | 55 | -25 | -18 | -12 | Low | 53 |  | #N/A |  |  |  |  | Salinas AP | [38 empty] | Snyder
Alaska, Yakutat | 33 | 59 | 2 | 63 | 55 | -20 | -13 | -7 | Low | 54 |  | #N/A |  |  |  |  | San Bernadino, Norton AFB | [38 empty] | Temple
Arizona, Douglas AP | 4173 | 31 | 31 | 95 | 63 | -34 | -27 | -21 | High | 55 |  | #N/A |  |  |  |  | San Diego AP | [38 empty] | Tyler AP
Arizona, Flagstaff Ap | 7011 | 35 | 8 | 83 | 55 | -54 | -47 | -41 | High | 56 |  | #N/A |  |  |  |  | San Diego, Miramar NAS | [38 empty] | Vernon
Arizona, Fort Huachuca AP | 4716 | 31 | 28 | 92 | 62 | -34 | -27 | -21 | High | 57 |  | #N/A |  |  |  |  | San Fernando | [38 empty] | Victoria AP
Arizona, Kingman AP | 3446 | 35 | 27 | 97 | 63 | -38 | -31 | -25 | High | 58 |  | #N/A |  |  |  |  | San Francisco AP | [38 empty] | Waco AP
Arizona, Nogalas | 3932 | 31 | 32 | 96 | 64 | -32 | -25 | -19 | High | 59 |  | #N/A |  |  |  |  | San Francisco CO | [38 empty] | Wichita Falls AP
Arizona, Page | 4310 | 36 | 24 | 97 | 62 | -43 | -36 | -30 | High | 60 |  | #N/A |  |  |  |  | San Jose AP
Arizona, Phoenix AP | 1133 | 33 | 37 | 108 | 70 | -21 | -14 | -8 | High | 61 |  | #N/A |  |  |  |  | San Luis Obispo
Arizona, Phoenix, Luke AFB | 1101 | 33 | 38 | 107 | 71 | -14 | -7 | -1 | High | 62 |  | #N/A |  |  |  |  | Santa Ana AP
Arizona, Prescott AP | 5042 | 34 | 20 | 91 | 60 | -42 | -35 | -29 | High | 63 |  | #N/A |  |  |  |  | Santa Barbara AP
Arizona, Safford, Agri. Center | 3176 | 32 | 26 | 99 | 66 | -25 | -18 | -12 | High | 64 |  | #N/A |  |  |  |  | Santa Cruz
Arizona, Tuscon Ap | 2641 | 32 | 24 | 102 | 65 | -39 | -30 | -24 | High | 65 |  | #N/A |  |  |  |  | Santa Maria AP
Arizona, Winslow AP | 4938 | 35 | 14 | 93 | 60 | -46 | -39 | -33 | High | 66 |  | #N/A |  |  |  |  | Santa Monica CO
Arizona, Yuma AP | 213 | 32 | 44 | 109 | 72 | -15 | -8 | -2 | High | 67 |  | #N/A |  |  |  |  | Santa Paula
Arkansas, Blytheville AFB | 264 | 36 | 18 | 95 | 77 | 42 | 49 | 55 | Medium | 68 |  | #N/A |  |  |  |  | Santa Rosa
Arkansas, Camden | 130 | 33 | 23 | 96 | 76 | 34 | 41 | 47 | Medium | 69 |  | #N/A |  |  |  |  | Stockton AP
Arkansas, El Dorado AP | 277 | 33 | 23 | 96 | 76 | 34 | 41 | 47 | Medium | 70 |  | #N/A |  |  |  |  | Ukiah
Arkansas, Fayetteville AP | 1251 | 36 | 13 | 93 | 75 | 33 | 40 | 46 | Medium | 71 |  | #N/A |  |  |  |  | Victorville, George AFB
Arkansas, Fort Smith AP | 469 | 35 | 19 | 96 | 76 | 34 | 41 | 47 | Medium | 72 |  | #N/A |  |  |  |  | Visalia
Arkansas, Hot Springs | 540 | 34 | 23 | 97 | 77 | 39 | 46 | 52 | Medium | 73 |  | #N/A |  |  |  |  | Yreka
Arkansas, Jonesboro 262 | 35 | 15 | 94 | 77 | 44 | 51 | 57 | M |  | 74 |  | #N/A |  |  |  |  | Yuba City
Arkansas, Little Rock AP | 260 | 34 | 21 | 95 | 77 | 42 | 49 | 55 | Medium
Arkansas, Pine Bluff AP | 206 | 34 | 22 | 97 | 77 | 39 | 46 | 52 | Medium
Arkansas, Texarkana AP | 389 | 33 | 25 | 95 | 77 | 42 | 49 | 55 | Medium
California, Alameda, NAS | 15 | 37 | 42 | 79 | 64 | -6 | 1 | 7 | Medium
California, Bakersfield AP | 507 | 35 | 35 | 101 | 69 | -15 | -8 | -2 | High
California, Barstow | 1927 | 34 | 32 | 105 | 67 | -32 | -25 | -19 | High
California, Blue Canyon | 5280 | 39 | 24 | 81 | 57 | -41 | -34 | -28 | Medium
California, Blythe AP | 397 | 33 | 33 | 110 | 71 | -18 | -11 | -5 | High
California, Burbank AP | 775 | 34 | 41 | 95 | 69 | -6 | 1 | 7 | Medium
California, Chico | 238 | 39 | 30 | 101 | 68 | -22 | -15 | -9 | High
California, Concord | 23 | 38 | 27 | 97 | 68 | -14 | -7 | -1 | High
California, Covina | 575 | 34 | 35 | 95 | 68 | -11 | -5 | 2 | High
California, Crescent City AP | 57 | 41 | 33 | 65 | 59 | -6 | 1 | 7 | Medium
California, Downey | 110 | 34 | 40 | 89 | 70 | 9 | 15 | 22 | Medium
California, El Cajon | 387 | 32 | 44 | 80 | 69 | 19 | 26 | 32 | High
California, El Centro AP | -30 | 32 | 38 | 110 | 74 | -3 | 4 | 10 | High
California, Escondido | 660 | 33 | 41 | 85 | 68 | 5 | 12 | 18 | High
California, Eureaka/Arcata AP | 217 | 41 | 32 | 67 | 59 | -10 | -3 | 3 | Low
California, Fairfield-Travis AFB | 62 | 38 | 34 | 94 | 67 | -15 | -8 | -2 | High
California, Fresno AP | 328 | 36 | 32 | 101 | 70 | -10 | -3 | 3 | High
California, Hamiltion AFB | 3 | 38 | 32 | 84 | 66 | -4 | 3 | 9 | High
California, Laguna Beach | 35 | 33 | 43 | 80 | 68 | 0 | 3 | 6 | Medium
California, Lemoore, Reeves NAS | 237 | 36 | 32 | 101 | 71 | -4 | 3 | 9 | High
California, Livermore 500 | 37 | 27 | 97 | 68 | -14 | -7 | -1 | M
California, Lompoc, Vandenburg AFB | 87 | 34 | 38 | 70 | 61 | -5 | 2 | 8 | Medium
California, Long Beach AP | 30 | 33 | 43 | 88 | 67 | -5 | 2 | 8 | Medium
California, Los Angeles AP | 97 | 34 | 45 | 81 | 64 | -9 | -2 | 8 | Low
California, Los Angeles CO | 270 | 34 | 40 | 89 | 70 | 10 | 17 | 23 | Medium
California, Marysville, Beale AFB | 119 | 39 | 34 | 98 | 69 | -10 | -3 | 3 | High
California, Merced-Castle AFB | 188 | 37 | 32 | 97 | 69 | -9 | -2 | 4 | High
California, Modesto | 97 | 37 | 30 | 98 | 68 | -16 | -9 | -3 | High
California, Monterey | 162 | 36 | 38 | 71 | 61 | -7 | 0 | 6 | Medium
California, Mount Shasta | 3543 | 41 | 21 | 88 | 61 | -33 | -26 | -20 | High
California, Mountain View, Moffet NAS | 34 | 37 | 39 | 84 | 65 | -9 | -2 | 4 | Medium
California, Napa | 33 | 38 | 32 | 96 | 68 | -12 | -5 | 1 | High
California, Needles AP | 983 | 34 | 33 | 110 | 71 | -18 | -11 | -5 | High
California, Oakland AP | 6 | 37 | 36 | 80 | 63 | -12 | -5 | 1 | Medium
California, Oceanside | 28 | 33 | 43 | 80 | 68 | 13 | 20 | 26 | Low
California, Ontario IAP | 952 | 34 | 38 | 98 | 70 | -5 | 2 | 8 | High
California, Oxnard | 7 | 34 | 41 | 79 | 64 | -6 | 1 | 7 | Medium
California, Palmdale AP | 2542 | 34 | 24 | 98 | 65 | -31 | -24 | -18 | High
California, Palm Springs | 462 | 33 | 35 | 110 | 70 | -24 | -17 | -11 | High
California, Pasadena | 864 | 34 | 35 | 95 | 68 | -11 | -4 | 2 | High
California, Paso Robles | 837 | 35 | 29 | 98 | 67 | -21 | -14 | -8 | High
California, Petaluma | 87 | 38 | 29 | 90 | 66 | -13 | -6 | 0 | High
California, Pomona CO | 934 | 34 | 30 | 99 | 69 | -12 | -5 | 1 | High
California, Red Bluff | 342 | 40 | 32 | 102 | 69 | -17 | -10 | -4 | High
California, Redding AP | 502 | 40 | 31 | 102 | 67 | -27 | -20 | -14 | High
California, Redlands | 1571 | 34 | 33 | 99 | 69 | -12 | -5 | 1 | High
California, Richmond | 55 | 38 | 36 | 80 | 63 | -12 | -6 | 1 | Medium
California, Riverside-March AFB | 1533 | 33 | 36 | 98 | 68 | -16 | -9 | -3 | High
California, Sacramento AP | 95 | 38 | 32 | 97 | 68 | -14 | -7 | -1 | High
California, Sacramento, McClellan AFB | 75 | 38 | 34 | 98 | 67 | -21 | -14 | -8 | High
California, Sacramento, Metro | 23 | 38 | 33 | 97 | 69 | -9 | -2 | 4 | High
California, Salinas AP | 85 | 36 | 35 | 78 | 62 | -14 | -7 | -1 | Medium
California, San Bernadino, Norton AFB | 1156 | 34 | 36 | 101 | 70 | -10 | -3 | 3 | High
California, San Diego AP | 13 | 32 | 46 | 81 | 67 | 6 | 13 | 19 | Low
California, San Diego, Miramar NAS | 477 | 32 | 42 | 88 | 67 | -5 | 2 | 8 | Medium
California, San Fernando | 977 | 34 | 39 | 91 | 68 | -4 | 2 | 9 | High
California, San Francisco AP | 8 | 37 | 39 | 78 | 62 | -14 | -7 | -1 | Medium
California, San Francisco CO | 20 | 37 | 40 | 71 | 62 | -2 | 5 | 11 | Low
California, San Jose AP | 56 | 37 | 38 | 89 | 66 | -12 | -5 | 1 | High
California, San Luis Obispo | 250 | 35 | 35 | 88 | 70 | 11 | 18 | 24 | High
California, Santa Ana AP | 54 | 33 | 39 | 85 | 68 | 5 | 12 | 18 | High
California, Santa Barbara AP | 10 | 34 | 37 | 80 | 64 | -8 | 1 | 5 | Medium
California, Santa Cruz | 125 | 37 | 38 | 71 | 61 | -7 | 2 | 6 | High
California, Santa Maria AP | 240 | 34 | 35 | 82 | 62 | -20 | -13 | -7 | Medium
California, Santa Monica CO | 236 | 34 | 43 | 80 | 68 | 13 | 20 | 26 | Medium
California, Santa Paula | 245 | 34 | 35 | 86 | 67 | -2 | 5 | 11 | High
California, Santa Rosa | 125 | 38 | 29 | 95 | 67 | -16 | -9 | -3 | High
California, Stockton AP | 22 | 37 | 32 | 97 | 68 | -14 | -7 | -1 | High
California, Ukiah | 614 | 39 | 29 | 95 | 68 | -11 | -4 | 2 | High
California, Victorville, George AFB | 2875 | 34 | 30 | 98 | 65 | -31 | -24 | -18 | High
California, Visalia | 292 | 36 | 30 | 100 | 69 | -14 | -7 | -1 | High
California, Yreka | 2625 | 41 | 17 | 92 | 64 | -25 | -18 | -11 | High
California, Yuba City | 58 | 39 | 31 | 101 | 67 | -26 | -19 | -13 | High
Colorado, Alamosa AP | 7543 | 37 | -11 | 82 | 55 | -53 | -46 | -40 | High
Colorado, Boulder | 5385 | 40 | 0 | 91 | 59 | -47 | -40 | -34 | High
Colorado, Colarado Springs AP | 6171 | 38 | 4 | 87 | 58 | -46 | -39 | -33 | High
Colorado, Craig | 6283 | 40 | -12 | 85 | 56 | -52 | -45 | -39 | High
Colorado, Denver AP | 5283 | 39 | -3 | 90 | 59 | -46 | -39 | -33 | High
Colorado, Durango | 6684 | 37 | -1 | 87 | 59 | -41 | -34 | -28 | High
Colorado, Eagle | 6539 | 39 | -7 | 86 | 57 | -49 | -42 | -36 | High
Colorado, Fort Collins | 4935 | 40 | 1 | 91 | 59 | -48 | -41 | -35 | High
Colorado, Grand Junction AP | 4843 | 39 | 7 | 94 | 60 | -47 | -40 | -34 | High
Colorado, Greeley | 4820 | 40 | 4 | 94 | 60 | -47 | -40 | -34 | High
Colorado, LaJunta AP | 4238 | 38 | 3 | 98 | 68 | -11 | -4 | 2 | High
Colorado, Leadville | 9927 | 39 | -14 | 81 | 51 | -71 | -64 | -58 | High
Colorado, Limon | 5364 | 39 | 1 | 88 | 60 | -37 | -30 | -24 | High
Colorado, Pueblo AP | 4684 | 38 | 5 | 94 | 62 | -37 | -30 | -24 | High
Colorado, Sterling | 4038 | 40 | -2 | 93 | 62 | -36 | -29 | -23 | High
Colorado, Trinidad AP | 5761 | 37 | 6 | 90 | 60 | -40 | -33 | -27 | High
Connecticut, Bridgeport AP | 10 | 41 | 12 | 84 | 72 | 29 | 36 | 42 | Medium
Connecticut, Hartford, Brainard Field | 19 | 41 | 6 | 88 | 72 | 23 | 30 | 36 | Medium
Connecticut, New Haven AP | 14 | 41 | 7 | 84 | 73 | 35 | 42 | 48 | Medium
Connecticut, New London | 10 | 41 | 9 | 85 | 72 | 26 | 32 | 39 | Medium
Connecticut, Norwalk | 397 | 41 | 9 | 84 | 71 | 22 | 29 | 36 | Medium
Connecticut, Norwich | 197 | 41 | 7 | 86 | 73 | 30 | 37 | 44 | Medium
Connecticut, Waterbury | 850 | 41 | 2 | 85 | 71 | 22 | 29 | 35 | Medium
Connecticut, Windsor Locks, Bradlet Field | 197 | 42 | 8 | 88 | 71 | 16 | 22 | 29 | Medium
Delaware, Dover AFB | 28 | 39 | 18 | 89 | 75 | 39 | 46 | 52 | Medium
Delaware, Wilmington AP | 78 | 39 | 14 | 89 | 74 | 33 | 40 | 46 | Medium
DC, Andrews AFB | 283 | 38 | 18 | 91 | 74 | 30 | 37 | 43 | Medium
DC, Reagan National AP | 66 | 38 | 20 | 92 | 76 | 41 | 48 | 54 | Medium
Florida, Apalachicola | 20 | 29 | 35 | 90 | 78 | 57 | 64 | 70 | Medium
Florida, Belle Glade | 17 | 26 | 44 | 91 | 76 | 42 | 49 | 55 | Medium
Florida, Cape Kennedy AP | 10 | 28 | 42 | 90 | 78 | 57 | 64 | 70 | Low
Florida, Daytona Beach AP | 31 | 29 | 37 | 90 | 77 | 51 | 58 | 64 | Low
Florida, Fort Lauderdale | 10 | 26 | 50 | 90 | 78 | 57 | 64 | 70 | Low
Florida, Fort Myers AP | 15 | 26 | 47 | 93 | 77 | 46 | 53 | 59 | Medium
Florida, Fort Pierce | 25 | 27 | 42 | 90 | 78 | 57 | 64 | 70 | Medium
Florida, Gainsville AP | 152 | 29 | 33 | 92 | 77 | 47 | 54 | 60 | Medium
Florida, Homestead, AFB | 7 | 25 | 52 | 90 | 78 | 57 | 64 | 70 | Low
Florida, Jacksonville AP | 26 | 30 | 32 | 93 | 77 | 46 | 53 | 59 | Medium
Florida, Jacksonville/Cecil Field NAS | 80 | 30 | 34 | 95 | 76 | 36 | 43 | 49 | Medium
Florida, Jacksonville, Mayport Naval | 16 | 30 | 39 | 92 | 78 | 54 | 61 | 67 | Medium
Florida, Key West AP | 4 | 24 | 58 | 89 | 79 | 66 | 73 | 79 | Low
Florida, Lakeland CO | 214 | 28 | 41 | 91 | 76 | 42 | 49 | 55 | Medium
Florida, Melbourne | 15 | 28 | 43 | 91 | 79 | 62 | 69 | 75 | Medium
Florida, Miami AP | 11 | 25 | 50 | 90 | 77 | 51 | 58 | 64 | Low
Florida, Miami CO | 8 | 25 | 48 | 89 | 77 | 52 | 59 | 65 | Low
Florida, Miami, New Tamiami AP | 10 | 25 | 49 | 91 | 78 | 56 | 59 | 65 | Low
Florida, Milton, Whiting Field NAS | 200 | 30 | 31 | 93 | 77 | 46 | 53 | 59 | Medium
Florida, Ocala | 90 | 29 | 34 | 93 | 77 | 46 | 53 | 59 | Medium
Florida, Orlando AP | 100 | 28 | 42 | 93 | 76 | 39 | 46 | 52 | Medium
Florida, Panama City, Tyndall AFB | 18 | 30 | 37 | 89 | 79 | 66 | 73 | 79 | Low
Florida, Pensacola CO | 30 | 30 | 32 | 92 | 78 | 54 | 61 | 67 | Low
Florida, St. Augustine | 10 | 29 | 35 | 89 | 78 | 59 | 66 | 72 | Medium
Florida, St. Petersburg | 11 | 28 | 47 | 93 | 79 | 59 | 66 | 72 | Medium
Florida, Sanford | 55 | 28 | 38 | 93 | 76 | 39 | 46 | 52 | Medium
Florida, Sarasota/Bradenton | 30 | 27 | 43 | 92 | 79 | 61 | 68 | 74 | Medium
Florida, Tallahassee AP | 55 | 30 | 28 | 93 | 76 | 39 | 46 | 52 | Medium
Florida, Tampa AP | 19 | 28 | 40 | 91 | 77 | 49 | 56 | 62 | Medium
Florida, Valpariso, Eglin AFB | 85 | 30 | 33 | 90 | 78 | 57 | 64 | 70 | Medium
Florida, Vero Beach | 13 | 27 | 43 | 90 | 78 | 57 | 64 | 70 | Medium
Florida, West Palm Beach AP | 15 | 26 | 47 | 90 | 78 | 57 | 64 | 70 | Medium
Georgia, Albany, Turner | AFB | 223 | 31 | 30 | 95 | 76 | 49 | 56 | 62
Georgia, Americus | 466 | 32 | 25 | 94 | 76 | 37 | 44 | 50 | Medium
Georgia, Athens | 802 | 34 | 25 | 92 | 75 | 34 | 41 | 47 | Medium
Georgia, Atlanta AP | 1010 | 33 | 23 | 91 | 74 | 30 | 37 | 43 | Medium
Georgia, Augusta AP | 148 | 33 | 25 | 94 | 76 | 37 | 44 | 50 | Medium
Georgia, Brunswick | 20 | 31 | 34 | 91 | 79 | 62 | 69 | 75 | Medium
Georgia, Columbus, Fort Benning | 232 | 32 | 27 | 94 | 76 | 37 | 44 | 50 | Medium
Georgia, Columbus, Lawson AFB | 971 | 32 | 24 | 93 | 76 | 39 | 46 | 53 | Medium
Georgia, Columbus, Metro AP | 397 | 32 | 27 | 93 | 75 | 33 | 40 | 46 | Medium
Georgia, Dalton | 710 | 34 | 22 | 93 | 76 | 39 | 46 | 52 | Medium
Georgia, Dublin | 310 | 32 | 25 | 93 | 76 | 39 | 46 | 52 | Medium
Georgia, Gainesville | 1275 | 34 | 21 | 91 | 74 | 30 | 37 | 43 | Medium
Georgia, Griffin | 980 | 33 | 22 | 90 | 75 | 38 | 45 | 51 | Medium
Georgia, La Grange | 693 | 33 | 23 | 91 | 75 | 36 | 43 | 49 | Medium
Georgia, Macon AP | 354 | 32 | 27 | 94 | 75 | 31 | 38 | 44 | Medium
Georgia, Marietta, Dobbins AFB | 1068 | 34 | 26 | 91 | 74 | 30 | 37 | 43 | Medium
Georgia, Moultrie | 292 | 31 | 30 | 95 | 77 | 42 | 49 | 55 | Medium
Georgia, Rome AP | 637 | 34 | 21 | 94 | 74 | 25 | 32 | 38 | Medium
Georgia, Savannah, Travis AP | 49 | 32 | 29 | 93 | 76 | 39 | 46 | 52 | Medium
Georgia, Valdosta, Moody AFB | 233 | 31 | 34 | 94 | 77 | 44 | 51 | 57 | Medium
Georgia, Valdosta, Regional AP | 203 | 30 | 31 | 94 | 76 | 37 | 44 | 50 | Medium
Georgia, Waycross | 151 | 31 | 32 | 94 | 76 | 37 | 44 | 50 | Medium
Hawaii, Ewa, Barbers Point NAS | 34 | 21 | 61 | 90 | 72 | 19 | 26 | 32 | Medium
Hawaii, Hilo AP | 36 | 19 | 63 | 84 | 74 | 41 | 48 | 54 | Low
Hawaii, Honolulu AP | 16 | 21 | 63 | 88 | 73 | 29 | 36 | 42 | Low
Hawaii, Kahului | 56 | 20 | 61 | 88 | 74 | 35 | 42 | 48 | Medium
Hawaii, Kaneohe Bay MCAS | 18 | 21 | 68 | 85 | 74 | 40 | 47 | 53 | Low
Hawaii, Lihue | 148 | 21 | 62 | 85 | 74 | 40 | 47 | 53 | Low
Hawaii, Molokai | 449 | 21 | 61 | 87 | 73 | 30 | 37 | 43 | Medium
Hawaii, Wahaiwa | 900 | 21 | 59 | 85 | 72 | 28 | 35 | 41 | Low
Idaho, Boise AP | 2838 | 43 | 9 | 94 | 63 | -34 | -27 | -21 | High
Idaho, Burley | 4150 | 42 | 2 | 90 | 62 | -22 | -15 | -9 | High
Idaho, Coeur D’Alene AP | 3002 | 47 | -1 | 86 | 61 | -30 | -23 | -17 | High
Idaho, Idaho Falls AP | 4741 | 43 | -6 | 89 | 60 | -39 | -32 | -26 | High
Idaho, Kamiah | 1196 | 46 | 15 | 93 | 64 | -28 | -21 | -14 | High
Idaho, Lewiston AP | 1413 | 46 | 15 | 93 | 64 | -28 | -21 | -15 | High
Idaho, Moscow | 2583 | 46 | 0 | 87 | 62 | -27 | -20 | -13 | High
Idaho, Mountain Home AFB | 2996 | 43 | 5 | 96 | 62 | -42 | -35 | -29 | High
Idaho, Mullan | 3317 | 47 | 7 | 84 | 61 | -27 | -20 | -14 | High
Idaho, Pocatello AP | 4454 | 43 | 0 | 90 | 60 | -41 | -34 | -28 | High
Idaho, Twin Falls AP | 4150 | 42 | 2 | 95 | 61 | -44 | -37 | -31 | High
Illinois, Aurora | 706 | 41 | -1 | 91 | 76 | 42 | 49 | 55 | Medium
Illinois, Belleville, Scott AFB | 453 | 38 | 10 | 93 | 77 | 46 | 53 | 59 | Medium
Illinois, Bloomington | 875 | 40 | -2 | 90 | 74 | 31 | 38 | 44 | Medium
Illinois, Carbondale | 411 | 37 | 7 | 93 | 77 | 46 | 53 | 59 | Medium
Illinois, Champaign/Urbana | 754 | 40 | 2 | 92 | 74 | 28 | 35 | 41 | Medium
Illinois, Chicago, Meigs Field | 593 | 41 | 3 | 89 | 73 | 27 | 34 | 40 | Medium
Illinois, Chicago, Midway AP | 620 | 41 | 0 | 91 | 73 | 24 | 31 | 37 | Medium
Illinois, Chicago, O’Hare AP | 668 | 42 | -1 | 88 | 73 | 29 | 36 | 42 | Medium
Illinois, Chicago CO | 647 | 41 | 2 | 91 | 74 | 30 | 37 | 43 | Low
Illinois, Danville | 696 | 40 | 1 | 90 | 74 | 31 | 38 | 44 | Medium
Illinois, Decatur | 682 | 39 | 3 | 91 | 75 | 36 | 43 | 49 | Medium
Illinois, Dixon | 785 | 41 | -2 | 90 | 74 | 31 | 38 | 43 | Medium
Illinois, Elgin |  | 42 | -2 | 88 | 74 | 35 | 42 | 48 | Medium
Illinois, Freeport | 856 | 42 | -4 | 89 | 73 | 27 | 34 | 40 | Medium
Illinois, Galesburg | 764 | 41 | -2 | 91 | 75 | 36 | 43 | 49 | Medium
Illinois, Glenview, NAS | 653 | 42 | 4 | 89 | 73 | 27 | 34 | 40 | Medium
Illinois, Greenville | 541 | 39 | 4 | 92 | 75 | 34 | 41 | 47 | Medium
Illinois, Joliet | 581 | 41 | 0 | 90 | 74 | 31 | 38 | 43 | Medium
Illinois, Kankakee | 629 | 41 | 1 | 90 | 74 | 31 | 38 | 43 | Medium
Illinois, LaSalle/Peru | 654 | 41 | -2 | 91 | 75 | 36 | 43 | 49 | Medium
Illinois, Macomb | 705 | 40 | 0 | 92 | 76 | 41 | 48 | 54 | Medium
Illinois, Marseilles | 738 | 41 | 1 | 89 | 73 | 27 | 34 | 40 | Medium
Illinois, Moline, Davenport AP | 590 | 41 | -3 | 90 | 74 | 31 | 38 | 43 | Medium
Illinois, Mt. Vernon | 480 | 38 | 5 | 92 | 75 | 34 | 41 | 47 | Medium
Illinois, Peoria AP | 663 | 40 | -1 | 89 | 74 | 33 | 40 | 46 | Medium
Illinois, Quincy AP | 768 | 40 | 2 | 91 | 75 | 36 | 43 | 49 | Medium
Illinois, Rantoul, Chanute AFB | 737 | 40 | 1 | 91 | 74 | 30 | 37 | 42 | Medium
Illinois, Rockford | 741 | 42 | -4 | 88 | 73 | 29 | 36 | 41 | Medium
Illinois, Springfield AP | 641 | 39 | 2 | 91 | 75 | 36 | 43 | 49 | Medium
Illinois, Waukegan | 727 | 42 | -3 | 89 | 74 | 33 | 40 | 46 | Medium
Illinois, West Chicago | 758 | 41 | 0 | 88 | 74 | 35 | 42 | 48 | Medium
Indiana, Anderson | 919 | 40 | 6 | 92 | 75 | 34 | 41 | 47 | Medium
Indiana, Bedford | 728 | 38 | 5 | 92 | 75 | 34 | 41 | 47 | Medium
Indiana, Bloomington | 846 | 39 | 5 | 92 | 75 | 34 | 41 | 47 | Medium
Indiana, Columbus, Bakalar AFB | 656 | 39 | 7 | 92 | 75 | 34 | 41 | 47 | Medium
Indiana, Crawfordsville | 799 | 40 | 3 | 91 | 74 | 30 | 37 | 43 | Medium
Indiana, Evansville AP | 387 | 38 | 9 | 92 | 76 | 41 | 48 | 54 | Medium
Indiana, Fort Wayne AP | 815 | 41 | 2 | 88 | 73 | 29 | 36 | 42 | Medium
Indiana, Goshen AP | 827 | 41 | 1 | 89 | 73 | 27 | 34 | 40 | Medium
Indiana, Hobart | 644 | 41 | 2 | 88 | 73 | 29 | 36 | 42 | Medium
Indiana, Huntington | 806 | 40 | 1 | 89 | 72 | 21 | 28 | 34 | Medium
Indiana, Indianapolis AP (S) | 807 | 39 | 3 | 88 | 74 | 35 | 42 | 48 | Medium
Indiana, Jeffersonville | 474 | 38 | 10 | 93 | 74 | 27 | 34 | 40 | Medium
Indiana, Kokoma | 830 | 40 | 0 | 90 | 73 | 25 | 32 | 38 | Medium
Indiana, Layfayette | 607 | 40 | 3 | 90 | 75 | 38 | 45 | 51 | Medium
Indiana, LaPorte | 812 | 41 | 3 | 90 | 74 | 31 | 38 | 44 | Medium
Indiana, Marion | 859 | 40 | 0 | 90 | 73 | 31 | 38 | 44 | Medium
Indiana, Muncie | 937 | 40 | 2 | 90 | 73 | 25 | 32 | 38 | Medium
Indiana, Peru, Bunker Hill AFB | 737 | 40 | -1 | 88 | 73 | 29 | 36 | 42 | Medium
Indiana, Peru, Grsssom AFB | 810 | 40 | 4 | 89 | 75 | 39 | 46 | 52 | Medium
Indiana, Richmond AP | 1140 | 39 | 2 | 90 | 74 | 31 | 48 | 44 | Medium
Indiana, Shelbyville | 804 | 39 | 3 | 91 | 74 | 30 | 37 | 43 | Medium
Indiana, South Bend AP | 774 | 41 | 3 | 87 | 72 | 24 | 31 | 32 | Medium
Indiana, Terre Haute AP | 585 | 39 | 5 | 90 | 76 | 44 | 51 | 57 | Medium
Indiana, Valparaiso | 771 | 41 | 3 | 90 | 74 | 31 | 38 | 44 | Medium
Indiana, Vincennes | 414 | 38 | 6 | 92 | 74 | 28 | 30 | 41 | Medium
Iowa, Ames | 955 | 42 | -6 | 90 | 74 | 31 | 38 | 44 | Medium
Iowa, Burlington AP | 692 | 40 | 1 | 91 | 76 | 42 | 49 | 55 | Medium
Iowa, Cedar Rapids AP | 863 | 41 | -5 | 89 | 74 | 33 | 40 | 46 | Medium
Iowa, Clinton | 708 | 41 | -3 | 90 | 75 | 38 | 45 | 51 | Medium
Iowa, Council Bluffs | 1253 | 41 | -3 | 91 | 75 | 36 | 43 | 49 | Medium
Iowa, Des Moines AP | 938 | 41 | -4 | 90 | 74 | 31 | 38 | 44 | Medium
Iowa, Debuque | 1056 | 42 | -7 | 88 | 73 | 29 | 36 | 42 | Medium
Iowa, Fort Dodge | 1162 | 42 | -7 | 88 | 73 | 29 | 36 | 42 | Medium
Iowa, Iowa City | 661 | 41 | -6 | 89 | 76 | 46 | 53 | 59 | Medium
Iowa, Keokuk | 671 | 40 | 0 | 92 | 75 | 34 | 41 | 47 | Medium
Iowa, Lamoni | 1122 | 40 | 0 | 92 | 74 | 28 | 35 | 45 | Medium
Iowa, Marshalltown | 974 | 42 | -7 | 90 | 75 | 38 | 45 | 51 | Medium
Iowa, Mason City AP | 1213 | 43 | -10 | 88 | 73 | 29 | 36 | 42 | Medium
Iowa, Newton | 953 | 41 | -5 | 91 | 74 | 30 | 37 | 43 | Medium
Iowa, Ottumwa AP | 846 | 41 | 0 | 92 | 75 | 34 | 41 | 47 | Medium
Iowa, Sioux City AP | 1095 | 42 | -6 | 90 | 74 | 31 | 38 | 44 | Medium
Iowa, Spencer | 1339 | 43 | -11 | 88 | 73 | 29 | 36 | 41 | Medium
Iowa, Waterloo | 868 | 42 | -9 | 88 | 73 | 29 | 36 | 41 | Medium
Kansas, Atchison | 1073 | 39 | 2 | 93 | 76 | 39 | 46 | 52 | Medium
Kansas, Chante AP | 981 | 34 | 7 | 97 | 74 | 20 | 27 | 33 | Medium
Kansas, Concordia | 1483 | 39 | 3 | 96 | 72 | 10 | 17 | 23 | Medium
Kansas, Dodge City AP | 2582 | 37 | 6 | 97 | 70 | -3 | 4 | 10 | Medium
Kansas, El Dorado | 1378 | 37 | 7 | 98 | 73 | 12 | 19 | 25 | Medium
Kansas, Emporia | 1206 | 38 | 5 | 97 | 74 | 20 | 27 | 33 | Medium
Kansas, Garden City AP | 2890 | 38 | 4 | 97 | 69 | -9 | -2 | 4 | High
Kansas, Goodland AP | 3654 | 39 | 2 | 94 | 66 | -17 | -10 | -4 | High
Kansas, Great Bend | 1887 | 38 | 4 | 98 | 73 | 12 | 19 | 25 | High
Kansas, Hutchinson AP | 1542 | 38 | 8 | 99 | 72 | 5 | 12 | 18 | High
Kansas, Liberal | 2883 | 37 | 7 | 96 | 68 | -12 | -5 | 1 | High
Kansas, Manhattan, Fort Riley | 1065 | 39 | 5 | 96 | 74 | 22 | 29 | 35 | Medium
Kansas, Parsons | 899 | 37 | 9 | 97 | 74 | 20 | 27 | 33 | Medium
Kansas, Russel AP | 1864 | 38 | 3 | 96 | 72 | 10 | 17 | 23 | High
Kansas, Salina | 1272 | 38 | 4 | 97 | 73 | 14 | 21 | 27 | High
Kansas, Topeka AP | 877 | 39 | 4 | 93 | 75 | 33 | 40 | 46 | Medium
Kansas, Wichita AP | 1321 | 37 | 8 | 97 | 73 | 14 | 21 | 27 | Medium
Kansas, Wichita, McConnell AFB | 1371 | 37 | 10 | 97 | 73 | 14 | 21 | 27 | Medium
Kentucky, Ashland | 546 | 38 | 10 | 91 | 74 | 30 | 37 | 43 | Medium
Kentucky, Bowling Green AP | 547 | 37 | 14 | 91 | 75 | 36 | 43 | 49 | Medium
Kentucky, Corbin AP | 1188 | 37 | 9 | 92 | 73 | 23 | 29 | 36 | Medium
Kentucky, Covington AP | 869 | 39 | 7 | 89 | 73 | 27 | 34 | 40 | Medium
Kentucky, Fort Knox, Godman AAF | 753 | 37 | 15 | 92 | 74 | 28 | 35 | 41 | Medium
Kentucky, Hopkinsville, Campbell AFB | 571 | 15 | 15 | 93 | 76 | 39 | 46 | 52 | Medium
Kentucky, Jackson | 1381 | 37 | 14 | 87 | 73 | 30 | 37 | 43 | Medium
Kentucky, Lexington AP | 966 | 38 | 10 | 89 | 73 | 27 | 34 | 40 | Medium
Kentucky, Louisville AP | 477 | 38 | 12 | 90 | 75 | 38 | 45 | 51 | Medium
Kentucky, Madisonville | 439 | 37 | 10 | 93 | 75 | 33 | 40 | 46 | Medium
Kentucky, Owensboro | 407 | 37 | 10 | 94 | 75 | 31 | 38 | 44 | Medium
Kentucky, Paducah AP | 413 | 37 | 12 | 93 | 76 | 39 | 46 | 52 | Medium
Louisiana, Alexandria AP | 89 | 31 | 30 | 94 | 78 | 51 | 58 | 64 | Medium
Louisiana, Baton Rouge AP | 64 | 30 | 30 | 92 | 77 | 47 | 54 | 60 | Medium
Louisiana, Bogalusa | 119 | 30 | 28 | 93 | 77 | 46 | 53 | 59 | Medium
Louisiana, Bossier City, Barksdale AFB | 167 | 32 | 27 | 94 | 77 | 44 | 51 | 57 | Medium
Louisiana, Houma | 9 | 29 | 35 | 93 | 78 | 52 | 59 | 65 | Low
Louisiana, Lafayette AP | 42 | 30 | 32 | 93 | 78 | 52 | 59 | 65 | Medium
Louisiana, Lake Charles AP | 9 | 30 | 32 | 91 | 78 | 56 | 63 | 69 | Medium
Louisiana, Leesville, Fort Polk | 330 | 31 | 30 | 94 | 76 | 37 | 44 | 50 | Medium
Louisiana, Minden | 278 | 32 | 25 | 96 | 76 | 34 | 41 | 47 | Medium
Louisiana, Monroe AP | 79 | 32 | 27 | 94 | 78 | 51 | 58 | 64 | Medium
Louisiana, Natchitoches | 121 | 31 | 26 | 95 | 77 | 42 | 49 | 55 | Medium
Louisiana, New Orleans AP | 4 | 30 | 34 | 92 | 78 | 54 | 61 | 67 | Medium
Louisiana, New Orleans, Lakefront AP | 10 | 30 | 39 | 92 | 78 | 54 | 61 | 67 | Low
Louisiana, Shreveport AP | 254 | 32 | 26 | 95 | 77 | 42 | 49 | 55 | Medium
Maine, Augusta AP | 353 | 44 | 1 | 84 | 69 | 12 | 19 | 25 | Medium
Maine, Bangor, Dow AFB | 192 | 44 | -2 | 84 | 69 | 12 | 19 | 25 | Medium
Maine, Brunswick, NAS | 75 | 43 | 2 | 84 | 69 | 12 | 19 | 25 | Medium
Maine, Caribou AP | 624 | 46 | -10 | 82 | 67 | 5 | 12 | 18 | Medium
Maine, Lewiston | 358 | 44 | -2 | 85 | 70 | 15 | 22 | 29 | Medium
Maine, Limestone, Loring AFB | 745 | 46 | -9 | 80 | 66 | 3 | 10 | 16 | Medium
Maine, Millinocket AP | 413 | 45 | -9 | 83 | 68 | 8 | 15 | 21 | Medium
Maine, Portland | 43 | 43 | 2 | 83 | 70 | 19 | 26 | 32 | Medium
Maine, Waterville | 333 | 44 | -4 | 84 | 69 | 12 | 19 | 25 | Medium
Maryland, Balitimore AP | 148 | 39 | 15 | 91 | 74 | 30 | 37 | 43 | Medium
Maryland, Balitimore CO | 24 | 39 | 17 | 89 | 76 | 46 | 53 | 59 | Medium
Maryland, Cumberland | 790 | 39 | 10 | 89 | 74 | 33 | 40 | 46 | Medium
Maryland, Fredrick AP | 313 | 39 | 12 | 91 | 75 | 36 | 43 | 49 | Medium
Maryland, Hagerstown | 704 | 39 | 12 | 91 | 74 | 30 | 37 | 43 | Medium
Maryland, Lex Park, Patuxent River NAS | 39 | 38 | 21 | 90 | 75 | 38 | 45 | 51 | Medium
Maryland, Salisbury | 52 | 38 | 18 | 90 | 76 | 44 | 50 | 56 | Medium
Massachusetts, Boston AP | 20 | 42 | 12 | 87 | 71 | 19 | 26 | 32 | Medium
Massachusetts, Clinton | 366 | 42 | 2 | 87 | 71 | 18 | 24 | 31 | Medium
Massachusetts, East Falmouth, Otis ANGB | 132 | 41 | 14 | 82 | 72 | 32 | 39 | 45 | Medium
Massachusetts, Fall River | 190 | 41 | 9 | 84 | 71 | 23 | 30 | 36 | Medium
Massachusetts, Framingham | 197 | 42 | 6 | 86 | 71 | 22 | 29 | 35 | Medium
Massachusetts, Gloucester | 11 | 42 | 5 | 86 | 71 | 19 | 25 | 32 | Low
Massachusetts, Greenfield | 250 | 42 | -2 | 85 | 71 | 21 | 27 | 34 | Medium
Massachusetts, Lawrence | 148 | 42 | 0 | 87 | 72 | 24 | 31 | 37 | Medium
Massachusetts, Lowell | 102 | 42 | 1 | 88 | 72 | 21 | 28 | 34 | Medium
Massachusetts, New Bedford | 80 | 41 | 9 | 82 | 71 | 27 | 34 | 40 | Medium
Massachusetts, Pittsfield AP | 1194 | 42 | -3 | 84 | 70 | 18 | 25 | 31 | Medium
Massachusetts, Springfield, Westover AFB | 195 | 42 | 0 | 87 | 71 | 19 | 26 | 32 | Medium
Massachusetts, Tauton | 43 | 41 | 9 | 86 | 72 | 26 | 33 | 39 | Medium
Massachusetts, Weymouth, S. Weymouth Nas | 161 | 42 | 11 | 87 | 72 | 24 | 31 | 37 | Medium
Massachusetts, Worcester AP | 986 | 42 | 5 | 83 | 69 | 14 | 21 | 27 | Medium
Michigan, Adrian 798 | 41 | 3 | 88 | 72 | 23 | 30 | 36 | M
Michigan, Alpena AP | 689 | 45 | -1 | 84 | 69 | 12 | 19 | 25 | High
Michigan, Battle Creek AP | 941 | 42 | 5 | 88 | 72 | 23 | 30 | 36 | Medium
Michigan, Benton Harbor AP | 643 | 42 | 5 | 88 | 72 | 23 | 30 | 36 | Medium
Michigan, Detroit | 619 | 42 | 5 | 87 | 72 | 24 | 31 | 37 | Medium
Michigan, Escanaba | 609 | 45 | -7 | 83 | 69 | 14 | 21 | 27 | Medium
Michigan, Flint AP | 771 | 42 | 3 | 86 | 71 | 20 | 27 | 33 | Medium
Michigan, Grand Rapids AP | 784 | 42 | 5 | 86 | 71 | 20 | 27 | 33 | Medium
Michigan, Hancock | 1091 | 47 | -4 | 83 | 69 | 14 | 21 | 27 | Medium
Michigan, Harbour Beach | 600 | 44 | 12 | 86 | 69 | 9 | 16 | 22 | Medium
Michigan, Holland | 603 | 42 | 6 | 86 | 71 | 20 | 27 | 33 | Medium
Michigan, Jackson AP | 1001 | 42 | 4 | 86 | 73 | 32 | 39 | 45 | Medium
Michigan, Kalamazoo | 874 | 42 | 5 | 88 | 72 | 23 | 30 | 36 | Medium
Michigan, Lansing AP | 841 | 42 | 2 | 86 | 72 | 26 | 33 | 39 | Medium
Michigan, Marquette CO | 1424 | 46 | -8 | 82 | 67 | 5 | 12 | 18 | Medium
Michigan, Marquette, Sawyer AFB | 1220 | 46 | -6 | 83 | 69 | 14 | 21 | 27 | Medium
Michigan, Mount Clemens ANGB | 583 | 42 | 7 | 87 | 72 | 24 | 31 | 37 | Medium
Michigan, Mt. Pleasant | 755 | 43 | 4 | 87 | 72 | 24 | 31 | 37 | Medium
Michigan, Muskegon AP | 625 | 43 | 7 | 83 | 70 | 19 | 26 | 32 | High
Michigan, Oscoda, Wurtsmith AFB | 634 | 44 | 3 | 86 | 71 | 20 | 27 | 33 | Medium
Michigan, Pellston | 719 | 45 | -3 | 86 | 69 | 9 | 16 | 22 | High
Michigan, Pontiac | 980 | 42 | 4 | 87 | 72 | 24 | 31 | 37 | Medium
Michigan, Port Huron | 586 | 43 | 4 | 87 | 72 | 24 | 31 | 37 | High
Michigan, Saginaw AP | 667 | 43 | 4 | 87 | 72 | 24 | 31 | 37 | Medium
Michigan, Sault Ste. Marie AP | 721 | 46 | -7 | 80 | 68 | 13 | 20 | 26 | Medium
Michigan, Seul Choix Point | 591 | 45 | 4 | 76 | 65 | 4 | 11 | 17 | Medium
Michigan, Traverse City AP | 624 | 44 | 2 | 86 | 70 | 14 | 21 | 27 | Medium
Michigan, Yipsilanti | 716 | 42 | 5 | 89 | 71 | 15 | 22 | 28 | Medium
Minnesota, Albert Lea | 1259 | 43 | -12 | 87 | 72 | 24 | 31 | 37 | Medium
Minnesota, Alexandria AP | 1424 | 45 | -15 | 86 | 70 | 14 | 21 | 27 | Medium
Minnesota, Bemidji AP | 1389 | 47 | -26 | 85 | 69 | 11 | 18 | 24 | Medium
Minnesota, Brainerd | 1280 | 46 | -17 | 85 | 68 | 5 | 12 | 18 | Medium
Minnesota, Duluth AP | 1428 | 46 | -16 | 81 | 67 | 6 | 13 | 19 | Medium
Minnesota, Fairbault | 1060 | 44 | -12 | 88 | 72 | 23 | 30 | 36 | Medium
Minnesota, Fergus Falls | 1182 | 46 | -17 | 88 | 72 | 23 | 30 | 36 | Medium
Minnesota, Hibbing | 1352 | 47 | -20 | 81 | 68 | 12 | 19 | 25 | Medium
Minnesota, International Falls AP | 1179 | 48 | -23 | 83 | 67 | 3 | 10 | 16 | Medium
Minnesota, Mankato 1020 | 44 | -12 | 88 | 72 | 23 | 30 | 36 | M
Minnesota, Minneapolis/St. Paul AP | 834 | 44 | -11 | 88 | 71 | 17 | 24 | 30 | Medium
Minnesota, Redwood Falls | 1024 | 44 | -12 | 88 | 72 | 23 | 30 | 36 | Medium
Minnesota, Rochester AP | 1297 | 44 | -12 | 85 | 71 | 22 | 29 | 35 | Medium
Minnesota, St. Cloud AP | 1024 | 45 | -14 | 88 | 71 | 17 | 24 | 30 | Medium
Minnesota, Tofte | 791 | 47 | -6 | 75 | 62 | -9 | -2 | 4 | Medium
Minnesota, Virginia | 909 | 47 | -21 | 83 | 68 | 8 | 15 | 22 | Medium
Minnesota, Willmar | 1127 | 45 | -11 | 88 | 72 | 23 | 30 | 36 | Medium
Minnesota, Winona | 656 | 44 | -10 | 88 | 73 | 29 | 36 | 42 | Medium
Mississippi, Biloxi, Keesler AFB | 26 | 30 | 35 | 91 | 78 | 56 | 63 | 69 | Medium
Mississippi, Clarksdale | 173 | 34 | 19 | 94 | 77 | 44 | 51 | 57 | Medium
Mississippi, Columbus AFB | 219 | 33 | 25 | 94 | 76 | 37 | 44 | 50 | Medium
Mississippi, Greenville AFB | 131 | 33 | 20 | 93 | 77 | 46 | 53 | 59 | Medium
Mississippi, Greenwood | 154 | 33 | 24 | 94 | 78 | 51 | 58 | 64 | Medium
Mississippi, Hattiesburg | 151 | 31 | 27 | 94 | 77 | 44 | 51 | 57 | Medium
Mississippi, Jackson AP | 310 | 32 | 25 | 93 | 76 | 36 | 46 | 52 | Medium
Mississippi, Laurel | 238 | 31 | 27 | 94 | 77 | 44 | 51 | 57 | Medium
Mississippi, McComb AP | 413 | 31 | 28 | 92 | 76 | 41 | 48 | 54 | Medium
Mississippi, Meridian AP | 317 | 32 | 25 | 94 | 76 | 37 | 44 | 50 | Medium
Mississippi, Natchez | 272 | 31 | 27 | 94 | 78 | 51 | 58 | 64 | Medium
Mississippi, Tupelo | 361 | 34 | 22 | 94 | 76 | 37 | 44 | 50 | Medium
Mississippi, Vicksburg CO | 106 | 32 | 26 | 95 | 78 | 49 | 56 | 62 | Medium
Missouri, Cape Girardeau | 341 | 37 | 13 | 94 | 77 | 44 | 51 | 57 | Medium
Missouri, Columbia AP | 778 | 39 | 5 | 92 | 75 | 34 | 41 | 47 | Medium
Missouri, Farmington AP | 946 | 37 | 8 | 93 | 75 | 33 | 40 | 46 | Medium
Missouri, Hannibal | 712 | 39 | 3 | 93 | 76 | 39 | 46 | 52 | Medium
Missouri, Jefferson City | 770 | 38 | 7 | 95 | 74 | 23 | 30 | 36 | Medium
Missouri, Joplin AP | 980 | 37 | 11 | 94 | 75 | 31 | 38 | 44 | Medium
Missouri, Kansas City AP | 791 | 39 | 4 | 93 | 75 | 33 | 40 | 46 | Medium
Missouri, Kirksville AP | 966 | 40 | 0 | 93 | 74 | 27 | 34 | 40 | Medium
Missouri, Mexico | 823 | 39 | 4 | 94 | 74 | 25 | 32 | 38 | Medium
Missouri, Moberly | 867 | 39 | 3 | 94 | 74 | 25 | 32 | 38 | Medium
Missouri, Poplar Bluff | 479 | 36 | 13 | 92 | 76 | 41 | 48 | 54 | Medium
Missouri, Rolla | 987 | 38 | 9 | 91 | 75 | 36 | 43 | 49 | Medium
Missouri, St. Joseph AP | 825 | 39 | 2 | 93 | 76 | 39 | 46 | 52 | Medium
Missouri, St. Louis AP | 535 | 38 | 8 | 93 | 75 | 33 | 40 | 46 | Medium
Missouri, St. Louis CO | 580 | 38 | 8 | 94 | 75 | 31 | 38 | 44 | Medium
Missouri, Sedalia, Whiteman AFB | 909 | 38 | 4 | 92 | 76 | 41 | 48 | 54 | Medium
Missouri, Sikeston | 315 | 36 | 15 | 95 | 76 | 36 | 43 | 49 | Medium
Missouri, Spickard/Trenton | 886 | 40 | 6 | 93 | 73 | 20 | 27 | 33 | Medium
Missouri, Springfield AP | 1268 | 37 | 9 | 92 | 74 | 28 | 35 | 41 | Medium
Missouri, Warrensburg, Whiteman AFB | 869 | 38 | 7 | 93 | 76 | 39 | 46 | 52 | Medium
Montana, Billings AP | 3567 | 45 | -7 | 90 | 62 | -31 | -24 | -18 | High
Montana, Bozeman | 4475 | 45 | -12 | 87 | 60 | -36 | -29 | -23 | High
Montana, Butte AP | 5553 | 46 | -14 | 84 | 56 | -51 | -44 | -38 | High
Montana, Cut Bank AP | 3838 | 48 | -16 | 84 | 59 | -36 | -29 | -23 | High
Montana, Glasgow AP | 2760 | 48 | -17 | 90 | 63 | -28 | -21 | -15 | High
Montana, Glendive | 2456 | 47 | -13 | 92 | 64 | -26 | -19 | -13 | High
Montana, Great Falls AP | 3652 | 47 | -13 | 88 | 60 | -38 | -31 | -25 | High
Montana, Great Falls, Malmstrom AFB | 3525 | 47 | -11 | 89 | 61 | -11 | -4 | 2 | High
Montana, Havre | 3200 | 48 | -19 | 90 | 62 | -33 | -26 | -20 | High
Montana, Helena AP | 3828 | 46 | -10 | 87 | 59 | -41 | -34 | -28 | High
Montana, Kalispell AP | 6780 | 48 | -3 | 86 | 61 | -29 | -22 | -16 | High
Montana, Lewiston AP | 4122 | 47 | -12 | 86 | 60 | -34 | -27 | -21 | High
Montana, Livingston AP | 4656 | 45 | -14 | 87 | 60 | -36 | -29 | -23 | High
Montana, Miles City AP | 2634 | 46 | -13 | 93 | 65 | -23 | -16 | -10 | High
Montana, Missoula AP | 3190 | 46 | -1 | 88 | 61 | -33 | -26 | -20 | High
Nebraska, Beatrice | 1323 | 40 | -2 | 95 | 74 | 28 | 35 | 41 | Medium
Nebraska, Bellevue, Offutt AFB | 1047 | 41 | 1 | 91 | 75 | 36 | 43 | 49 | Medium
Nebraska, Chadron AP | 3296 | 42 | -3 | 94 | 65 | -22 | -15 | -9 | High
Nebraska, Columbus | 1443 | 41 | -2 | 95 | 73 | 17 | 24 | 30 | Medium
Nebraska, Fremont | 1203 | 41 | -2 | 95 | 74 | 23 | 30 | 36 | Medium
Nebraska, Grand Island AP | 1841 | 41 | -2 | 93 | 72 | 15 | 22 | 28 | High
Nebraska, Hastings | 1954 | 40 | -3 | 94 | 71 | 7 | 14 | 20 | High
Nebraska, Kearney | 2131 | 40 | -4 | 93 | 70 | 3 | 10 | 16 | High
Nebraska, Lincoln CO | 1180 | 40 | -2 | 94 | 74 | 25 | 32 | 38 | Medium
Nebraska, McCook | 2579 | 40 | -2 | 95 | 69 | -11 | -4 | 2 | High
Nebraska, Norfolk | 1552 | 42 | -5 | 92 | 72 | 16 | 23 | 29 | High
Nebraska, North Platte AP | 2775 | 41 | -4 | 92 | 69 | -1 | 6 | 12 | High
Nebraska, Omaha AP | 977 | 41 | -2 | 92 | 75 | 34 | 41 | 47 | Medium
Nebraska, Omaha WSO | 1332 | 41 | -2 | 90 | 75 | 38 | 45 | 51 | Medium
Nebraska, Scottsbluff AP | 3958 | 41 | -3 | 92 | 64 | -25 | -18 | -12 | High
Nebraska, Sidney AP | 4304 | 41 | -1 | 92 | 63 | -29 | -22 | -16 | High
Nebraska, Valentine | 2598 | 42 | -8 | 94 | 67 | -15 | -8 | -2 | High
Nevada, Carson City | 4675 | 39 | 9 | 91 | 59 | -47 | -40 | -34 | High
Nevada, Elko AP | 5050 | 40 | 1 | 92 | 59 | -48 | -41 | -35 | High
Nevada, Ely AP | 6263 | 39 | 0 | 87 | 56 | -55 | -48 | -42 | High
Nevada, Las Vegas AP | 2162 | 36 | 30 | 106 | 66 | -39 | -32 | -26 | High
Nevada, Lovelock AP | 3904 | 40 | 12 | 96 | 63 | -35 | -28 | -22 | High
Nevada, Mercury | 3310 | 36 | 28 | 100 | 64 | -38 | -31 | -25 | High
Nevada, North Las Vega , Nellis AFB | 1868 | 36 | 31 | 106 | 67 | -34 | -27 | -21 | High
Nevada, Reno AP | 4412 | 39 | 13 | 92 | 60 | -44 | -37 | -31 | High
Nevada, Reno CO | 5046 | 39 | 11 | 93 | 60 | -45 | -38 | -32 | High
Nevada, Tonapah AP | 5426 | 38 | 13 | 92 | 57 | -58 | -51 | -45 | High
Nevada, Winnemucca AP | 4301 | 40 | 7 | 94 | 60 | -48 | -41 | -35 | High
New Hampshire, Berlin | 1161 | 44 | -9 | 84 | 69 | 12 | 19 | 25 | Medium
New Hampshire, Claremont | 545 | 43 | -4 | 86 | 70 | 14 | 21 | 27 | Medium
New Hampshire, Concord AP | 342 | 43 | -2 | 87 | 70 | 13 | 20 | 26 | High
New Hampshire, Keene | 488 | 43 | -7 | 87 | 70 | 13 | 20 | 26 | Medium
New Hampshire, Laconia | 545 | 43 | -5 | 86 | 70 | 14 | 21 | 27 | Medium
New Hampshire, Lebanon | 597 | 43 | -3 | 86 | 69 | 9 | 16 | 22 | Medium
New Hampshire, Manchester, Grenier AFB | 234 | 43 | -3 | 88 | 71 | 17 | 24 | 30 | Medium
New Hampshire, Mount Washington | 6266 | 44 | -19 | 58 | 54 | -18 | -11 | -5 | Low
New Hampshire, Portsmouth, Pease AFB | 101 | 43 | 9 | 85 | 70 | 16 | 23 | 29 | Medium
New Jersey, Atlantic City CO | 64 | 39 | 13 | 88 | 73 | 29 | 36 | 42 | Medium
New Jersey, Long Branch | 36 | 40 | 13 | 90 | 73 | 24 | 30 | 37 | Medium
New Jersey, Millville | 82 | 39 | 15 | 89 | 74 | 33 | 40 | 46 | Medium
New Jersey, Newark AP | 7 | 40 | 14 | 90 | 73 | 25 | 32 | 38 | Medium
New Jersey, New Brunswick | 100 | 40 | 10 | 89 | 73 | 25 | 32 | 38 | Medium
New Jersey, Patterson | 186 | 40 | 10 | 91 | 73 | 22 | 29 | 35 | Medium
New Jersey, Phillipsburg | 314 | 40 | 6 | 89 | 72 | 20 | 27 | 33 | Medium
New Jersey, Teterboro | 9 | 40 | 14 | 89 | 74 | 33 | 40 | 46 | Medium
New Jersey, Trenton, McQuire AFB | 133 | 40 | 15 | 90 | 74 | 31 | 38 | 44 | Medium
New Jersey, Vineland | 88 | 39 | 11 | 89 | 74 | 33 | 40 | 46 | Medium
New Mexico, Alamagordo Holloman AFB | 4093 | 32 | 23 | 96 | 63 | -36 | -29 | -23 | High
New Mexico, Albuquerque AP | 5311 | 35 | 18 | 93 | 60 | -46 | -39 | -33 | High
New Mexico, Artesia | 3548 | 32 | 19 | 100 | 67 | -21 | -14 | -8 | High
New Mexico, Carlsbad AP | 3293 | 32 | 23 | 98 | 66 | -23 | -16 | -10 | High
New Mexico, Clayton | 4970 | 36 | 9 | 91 | 62 | -33 | -26 | -20 | High
New Mexico, Clovis, Cannon AFB | 4295 | 34 | 15 | 93 | 64 | -26 | -19 | -13 | High
New Mexico, Farmington AP | 5503 | 36 | 13 | 92 | 60 | -57 | -50 | -44 | High
New Mexico, Gallup | 6470 | 35 | 5 | 87 | 56 | -55 | -48 | -42 | High
New Mexico, Grants | 6521 | 35 | 4 | 88 | 58 | -47 | -40 | -34 | High
New Mexico, Hobbs AP | 3659 | 32 | 18 | 99 | 66 | -25 | -18 | -12 | High
New Mexico, Las Cruces | 4544 | 32 | 20 | 96 | 64 | -30 | -23 | -17 | High
New Mexico, Los Alamos | 6089 | 35 | 9 | 87 | 60 | -36 | -27 | -19 | High
New Mexico, Raton AP | 6349 | 36 | 1 | 89 | 60 | -38 | -31 | -25 | High
New Mexico, Roswell, Walker AFB | 3676 | 33 | 20 | 96 | 65 | -26 | -19 | -13 | High
New Mexico, Santa Fe CO | 6345 | 35 | 10 | 88 | 61 | -32 | -25 | -19 | High
New Mexico, Silver City AP | 6126 | 32 | 10 | 94 | 60 | -47 | -40 | -34 | High
New Mexico, Socorro AP | 4850 | 34 | 17 | 95 | 62 | -38 | -31 | -25 | High
New Mexico, Truth or Consequences | 4858 | 33 | 26 | 95 | 61 | -43 | -36 | -30 | High
New Mexico, Tucumcari AP | 4039 | 35 | 15 | 95 | 65 | -24 | -17 | -11 | High
New York, Albany AP | 285 | 42 | -2 | 86 | 70 | 14 | 21 | 27 | Medium
New York, Albany CO | 275 | 42 | 1 | 88 | 72 | 23 | 30 | 36 | Medium
New York, Auburn | 417 | 43 | 2 | 87 | 71 | 18 | 24 | 31 | Medium
New York, Bafavia | 913 | 43 | 5 | 87 | 71 | 19 | 26 | 32 | Medium
New York, Binghampton AP | 1590 | 42 | 2 | 82 | 69 | 15 | 22 | 28 | Medium
New York, Buffalo AP | 705 | 43 | 5 | 84 | 69 | 12 | 19 | 25 | Medium
New York, Central Islip | 98 | 40 | 15 | 85 | 72 | 28 | 35 | 41 | Medium
New York, Cortland | 1198 | 42 | 0 | 85 | 71 | 22 | 29 | 35 | Medium
New York, Dunkirk | 692 | 42 | 9 | 85 | 72 | 28 | 35 | 41 | Medium
New York, Elmira AP | 955 | 42 | 3 | 87 | 71 | 19 | 26 | 32 | Medium
New York, Geneva | 417 | 42 | 2 | 87 | 71 | 18 | 24 | 31 | Medium
New York, Glens Falls | 328 | 43 | -4 | 85 | 71 | 22 | 29 | 35 | Medium
New York, Gloversville | 417 | 43 | -2 | 86 | 71 | 19 | 26 | 33 | Medium
New York, Hornell | 1220 | 42 | 0 | 85 | 70 | 16 | 23 | 29 | Medium
New York, Ithaca | 1099 | 42 | 0 | 85 | 71 | 22 | 29 | 35 | Medium
New York, Jamestown | 1723 | 42 | 3 | 86 | 70 | 14 | 21 | 27 | Medium
New York, Kingston | 149 | 42 | 2 | 88 | 72 | 23 | 30 | 36 | Medium
New York, Lockport | 638 | 43 | 7 | 86 | 72 | 26 | 33 | 39 | Medium
New York, Massena AP | 213 | 44 | -10 | 84 | 71 | 23 | 30 | 36 | Medium
New York, Newburg-Stewart AFB | 471 | 41 | 10 | 85 | 72 | 28 | 35 | 41 | Medium
New York, NYC-Central Park | 7 | 40 | 15 | 89 | 73 | 27 | 34 | 40 | Medium
New York, NYC-Kennedy AP | 13 | 40 | 15 | 88 | 72 | 23 | 30 | 36 | Medium
New York, NYC-La Guardia AP | 22 | 40 | 17 | 89 | 73 | 27 | 34 | 40 | Medium
New York, Niagra Falls AP | 590 | 43 | 7 | 85 | 71 | 22 | 29 | 35 | Medium
New York, Olean | 2135 | 42 | 2 | 84 | 71 | 23 | 30 | 36 | Medium
New York, Oneonta | 1764 | 42 | -4 | 83 | 69 | 14 | 21 | 27 | Medium
New York, Oswego CO | 300 | 43 | 7 | 83 | 71 | 25 | 32 | 38 | Medium
New York, Plattsburg AFB | 235 | 44 | -4 | 83 | 69 | 14 | 21 | 27 | Medium
New York, Poughkeepsie | 165 | 41 | 6 | 88 | 72 | 23 | 30 | 36 | Medium
New York, Rochester AP | 547 | 43 | 5 | 86 | 71 | 20 | 27 | 33 | Medium
New York, Rome-Griffiss AFB | 514 | 43 | 1 | 86 | 70 | 14 | 21 | 27 | Medium
New York, Schenectady | 378 | 42 | 1 | 87 | 72 | 24 | 31 | 37 | Medium
New York, Suffolk County AFB | 67 | 40 | 10 | 83 | 71 | 25 | 32 | 38 | Medium
New York, Syracuse AP | 410 | 43 | 2 | 85 | 71 | 22 | 29 | 35 | Medium
New York, Utica | 742 | 43 | -6 | 85 | 71 | 22 | 29 | 35 | Medium
New York, Watertown | 325 | 44 | -6 | 83 | 7O | 19 | 26 | 32 | Medium
New York, White Plains | 439 | 41 | 12 | 87 | 72 | 24 | 31 | 37 | Medium
North Carolina, Asheville AP | 2140 | 35 | 16 | 85 | 71 | 22 | 29 | 35 | Medium
North Carolina, Cape Hatteras | 7 | 35 | 29 | 86 | 77 | 57 | 64 | 70 | Low
North Carolina, Charlotte AP | 736 | 35 | 23 | 91 | 74 | 30 | 37 | 43 | Medium
North Carolina, Cherry Point MCAS | 29 | 34 | 28 | 92 | 78 | 54 | 61 | 67 | Medium
North Carolina, Durham | 427 | 36 | 20 | 92 | 75 | 33 | 40 | 46 | Medium
North Carolina, Elizabeth City AP | 12 | 36 | 19 | 91 | 77 | 49 | 56 | 62 | Medium
North Carolina, Fayetteville, Pope AFB | 218 | 35 | 27 | 94 | 76 | 37 | 44 | 50 | Medium
North Carolina, Goldsboro, Seymour | 154 | 35 | 27 | 94 | 76 | 35 | 42 | 49
North Carolina, Goldsboro, Johnson AFB | 108 | 35 | 27 | 94 | 76 | 35 | 42 | 49 | Medium
North Carolina, Greensboro AP | 897 | 36 | 19 | 90 | 74 | 30 | 37 | 43 | Medium
North Carolina, Greenville | 27 | 35 | 21 | 91 | 76 | 42 | 49 | 55 | Medium
North Carolina, Henderson | 2084 | 36 | 15 | 92 | 76 | 41 | 48 | 54 | Medium
North Carolina, Hickory | 1188 | 35 | 23 | 91 | 72 | 18 | 25 | 31 | Medium
North Carolina, Jacksonville | 26 | 34 | 27 | 92 | 78 | 54 | 61 | 67 | Medium
North Carolina, Lumberton | 126 | 34 | 21 | 92 | 76 | 41 | 48 | 54 | Medium
North Carolina, New Bern AP | 19 | 35 | 27 | 92 | 78 | 54 | 61 | 67 | Medium
North Carolina, Raleigh/Durham AP | 434 | 35 | 20 | 90 | 75 | 38 | 45 | 51 | Medium
North Carolina, Rocky Mount | 159 | 36 | 21 | 91 | 76 | 42 | 49 | 55 | Medium
North Carolina, Wilmington AP | 28 | 34 | 27 | 91 | 78 | 56 | 63 | 69 | Medium
North Carolina, Winston-Salem AP | 969 | 36 | 23 | 89 | 74 | 33 | 40 | 46 | Medium
North Dakota, Bismark AP | 1647 | 46 | -16 | 90 | 67 | -8 | -1 | 5 | High
North Dakota, Devil’s Lake | 1453 | 48 | -19 | 87 | 67 | -3 | 4 | 10 | Medium
North Dakota, Dickinson AP | 2585 | 46 | -17 | 90 | 66 | -13 | -6 | 0 | Medium
North Dakota, Fargo AP | 869 | 46 | -17 | 88 | 70 | 11 | 18 | 24 | Medium
North Dakota, Grands Forks AP | 911 | 48 | -16 | 88 | 69 | 6 | 13 | 19 | Medium
North Dakota, Jamestown AP | 1498 | 47 | -18 | 90 | 69 | 3 | 10 | 16 | High
North Dakota, Minot AP | 1668 | 48 | -16 | 88 | 66 | -10 | -3 | 3 | Medium
North Dakota, Minot, AFB | 1667 | 48 | -16 | 90 | 67 | -8 | -1 | 5 | High
North Dakota, Williston | 1906 | 48 | -18 | 92 | 66 | -16 | -9 | -3 | Medium
Ohio, Akron-Canton AP | 1228 | 41 | 5 | 85 | 71 | 22 | 29 | 35 | Medium
Ohio, Ashtabula | 924 | 41 | 9 | 85 | 72 | 28 | 35 | 41 | Medium
Ohio, Athens | 766 | 39 | 6 | 92 | 74 | 28 | 35 | 41 | Medium
Ohio, Bowling Green | 673 | 41 | 2 | 89 | 73 | 27 | 34 | 40 | Medium
Ohio, Cambridge | 800 | 40 | 7 | 90 | 74 | 31 | 38 | 44 | Medium
Ohio, Chilicothe | 640 | 39 | 6 | 92 | 74 | 28 | 35 | 41 | Medium
Ohio, Cincinnati, Lunken Field | 869 | 39 | 12 | 90 | 75 | 38 | 45 | 51 | Medium
Ohio, Cleveland AP | 777 | 41 | 6 | 86 | 72 | 26 | 33 | 39 | Medium
Ohio, Columbus AP | 812 | 40 | 6 | 88 | 73 | 29 | 36 | 42 | Medium
Ohio, Columbus, Rickenbckr AFB | 744 | 39 | 10 | 89 | 73 | 27 | 34 | 40 | Medium
Ohio, Dayton AP | 1002 | 39 | 5 | 88 | 73 | 29 | 36 | 42 | Medium
Ohio, Dayton, Wright/Paterson AFB | 824 | 39 | 8 | 89 | 74 | 33 | 40 | 46 | Medium
Ohio, Defiance | 708 | 41 | 4 | 91 | 73 | 24 | 31 | 37 | Medium
Ohio, Finlay AP | 810 | 41 | 4 | 87 | 72 | 24 | 31 | 37 | Medium
Ohio, Fremont | 663 | 41 | 1 | 88 | 73 | 29 | 36 | 42 | Medium
Ohio, Hamilton | 634 | 39 | 5 | 90 | 72 | 19 | 26 | 32 | Medium
Ohio, Lancaster | 869 | 39 | 5 | 91 | 73 | 24 | 31 | 37 | Medium
Ohio, Lima | 975 | 40 | 4 | 91 | 73 | 24 | 31 | 37 | Medium
Ohio, Mansfield AP | 1295 | 40 | 4 | 85 | 72 | 28 | 35 | 41 | Medium
Ohio, Marion | 994 | 40 | 5 | 91 | 73 | 24 | 31 | 37 | Medium
Ohio, Middletown | 651 | 39 | 5 | 90 | 72 | 19 | 26 | 32 | Medium
Ohio, Newark | 880 | 40 | 5 | 92 | 73 | 22 | 29 | 35 | Medium
Ohio, Norwalk | 852 | 41 | 1 | 88 | 73 | 29 | 36 | 42 | Medium
Ohio, Portsmouth | 540 | 38 | 10 | 92 | 74 | 28 | 35 | 41 | Medium
Ohio, Sandusky CO | 580 | 41 | 6 | 91 | 72 | 18 | 25 | 31 | Medium
Ohio, Springfield | 1052 | 40 | 3 | 89 | 73 | 27 | 34 | 40 | Medium
Ohio, Stubenville | 1194 | 40 | 5 | 86 | 71 | 20 | 27 | 33 | Medium
Ohio, Toledo AP | 669 | 41 | 3 | 87 | 72 | 24 | 31 | 37 | Medium
Ohio, Warren | 905 | 41 | 5 | 87 | 71 | 19 | 26 | 32 | Medium
Ohio, Wooster | 1136 | 40 | 6 | 86 | 71 | 20 | 27 | 33 | Medium
Ohio, Youngstown AP | 1178 | 41 | 4 | 85 | 70 | 16 | 23 | 29 | Medium
Ohio, Zanesville AP | 900 | 40 | 9 | 88 | 73 | 29 | 36 | 42 | Medium
Oklahoma, Ada | 1016 | 34 | 14 | 97 | 74 | 20 | 27 | 33 | Medium
Oklahoma, Altus AFB | 1378 | 34 | 19 | 100 | 73 | 9 | 16 | 22 | Medium
Oklahoma, Ardmore | 844 | 34 | 17 | 98 | 74 | 18 | 25 | 31 | Medium
Oklahoma, Bartlesville | 713 | 36 | 10 | 98 | 74 | 18 | 25 | 31 | Medium
Oklahoma, Chickasha | 1150 | 35 | 14 | 98 | 74 | 18 | 25 | 31 | Medium
Oklahoma, Enid-Vance AFB | 1307 | 36 | 12 | 98 | 74 | 18 | 25 | 31 | Medium
Oklahoma, Lawton AP | 1188 | 34 | 19 | 97 | 73 | 14 | 21 | 27 | Medium
Oklahoma, McAlester | 776 | 34 | 17 | 96 | 76 | 34 | 41 | 47 | Medium
Oklahoma, Muskogee AP | 610 | 35 | 15 | 98 | 75 | 25 | 32 | 38 | Medium
Oklahoma, Norman 1181 | 35 | 13 | 96 | 74 | 22 | 29 | 35 | M
Oklahoma, Oklahoma City AP | 1262 | 35 | 17 | 96 | 75 | 28 | 35 | 41 | Medium
Oklahoma, Oklahoma City, W.Rogers AP | 1285 | 35 | 15 | 96 | 74 | 22 | 29 | 35 | Medium
Oklahoma, Ponca City | 1007 | 36 | 9 | 97 | 74 | 20 | 27 | 33 | Medium
Oklahoma, Seminole | 1021 | 35 | 15 | 96 | 74 | 22 | 29 | 41 | Medium
Oklahoma, Stillwater | 984 | 36 | 13 | 96 | 74 | 22 | 29 | 41 | Medium
Oklahoma, Tulsa AP | 650 | 36 | 14 | 97 | 76 | 33 | 40 | 46 | Medium
Oklahoma, Woodward | 2188 | 36 | 10 | 97 | 73 | 14 | 21 | 27 | High
Oregon, Albany | 223 | 44 | 22 | 89 | 66 | -12 | -5 | 1 | High
Oregon, Astoria AP | 8 | 46 | 29 | 72 | 63 | 0 | -7 | -13 | Medium
Oregon, Baker AP | 3369 | 44 | 6 | 89 | 61 | -35 | -28 | -22 | High
Oregon, Bend | 3453 | 44 | 4 | 87 | 60 | -36 | -29 | -23 | High
Oregon, Corvallis | 246 | 44 | 22 | 89 | 66 | -12 | -5 | 1 | High
Oregon, Eugene AP | 359 | 44 | 26 | 87 | 65 | -14 | -7 | -1 | High
Oregon, Grants Pass | 925 | 42 | 24 | 96 | 68 | -12 | -5 | 1 | High
Oregon, Hillsboro | 203 | 45 | 24 | 88 | 67 | -5 | 2 | 8 | High
Oregon, Klamath Falls AP | 4092 | 42 | 10 | 87 | 62 | -26 | -19 | -13 | High
Oregon, Meacham | 4055 | 45 | 0 | 84 | 58 | -41 | -34 | -28 | High
Oregon, Medford AP | 1298 | 42 | 24 | 95 | 66 | -21 | -14 | -8 | High
Oregon, North Bend | 748 | 43 | 32 | 69 | 60 | -8 | -1 | 5 | Medium
Oregon, Pendleton AP | 1482 | 45 | 11 | 93 | 63 | -33 | -26 | -20 | High
Oregon, Portland AP | 30 | 45 | 27 | 86 | 66 | -7 | 0 | 6 | Medium
Oregon, Portland CO | 35 | 45 | 24 | 86 | 67 | -2 | 5 | 11 | Medium
Oregon, Redmond | 3084 | 44 | 9 | 89 | 61 | -35 | -28 | -22 | High
Oregon, Roseburg AP | 525 | 43 | 23 | 90 | 66 | -13 | -6 | 0 | High
Oregon, Salem AP | 196 | 45 | 25 | 87 | 66 | -8 | -1 | 5 | High
Oregon, Sexton Summit | 3842 | 42 | 24 | 80 | 59 | -30 | -23 | -17 | Medium
Oregon, The Dalles | 243 | 45 | 19 | 89 | 68 | -1 | 6 | 12 | High
Pennsylvania, Allentown AP | 387 | 40 | 10 | 88 | 72 | 23 | 30 | 36 | Medium
Pennsylvania, Altoona CO | 1504 | 40 | 10 | 86 | 70 | 14 | 21 | 27 | Medium
Pennsylvania, Bradford | 2142 | 41 | -1 | 80 | 68 | 13 | 20 | 26 | Medium
Pennsylvania, Butler | 1248 | 40 | 6 | 87 | 72 | 24 | 31 | 37 | Medium
Pennsylvania, Chambersburg | 697 | 40 | 8 | 90 | 74 | 31 | 38 | 44 | Medium
Pennsylvania, DuBois | 1818 | 41 | 5 | 84 | 69 | 12 | 19 | 25 | Medium
Pennsylvania, Erie AP | 731 | 42 | 7 | 83 | 70 | 19 | 26 | 32 | Medium
Pennsylvania, Harrisburg AP | 308 | 40 | 13 | 89 | 73 | 27 | 34 | 40 | Medium
Pennsylvania, Johnstown | 2284 | 40 | 2 | 83 | 70 | 19 | 26 | 32 | Medium
Pennsylvania, Lancaster | 403 | 40 | 8 | 90 | 74 | 31 | 38 | 44 | Medium
Pennsylvania, Meadville | 1400 | 41 | 4 | 85 | 70 | 16 | 23 | 29 | Medium
Pennsylvania, New Castle | 825 | 41 | 7 | 88 | 72 | 23 | 30 | 36 | Medium
Pennsylvania, Philadelphia AP | 5 | 39 | 15 | 89 | 74 | 33 | 40 | 46 | Medium
Pennsylvania, Philadelphia, Northeast AP | 121 | 40 | 15 | 90 | 74 | 31 | 38 | 44 | Medium
Pennsylvania, Philadelphia, Willow Gr NAS | 361 | 40 | 14 | 90 | 74 | 31 | 38 | 44 | Medium
Pennsylvania, Pittsburgh AP | 1137 | 40 | 7 | 86 | 70 | 14 | 21 | 27 | Medium
Pennsylvania, Pittsburgh, Allegheny AP | 1353 | 40 | 7 | 88 | 71 | 17 | 24 | 30 | Medium
Pennsylvania, Reading CO | 266 | 40 | 13 | 89 | 72 | 210 | 28 | 34 | Medium
Pennsylvania, Scranton/Wilkes-Barre | 930 | 41 | 7 | 85 | 70 | 16 | 20 | 26 | Medium
Pennsylvania, State College | 1239 | 40 | 7 | 87 | 71 | 19 | 26 | 32 | Medium
Pennsylvania, Sunbury | 430 | 40 | 7 | 89 | 72 | 21 | 28 | 34 | Medium
Pennsylvania, Uniontown | 815 | 39 | 9 | 88 | 73 | 29 | 36 | 42 | Medium
Pennsylvania, Warren | 1193 | 41 | 4 | 86 | 71 | 20 | 27 | 33 | Medium
Pennsylvania, West Chester | 466 | 40 | 13 | 89 | 74 | 33 | 40 | 46 | Medium
Pennsylvania, Williamsport AP | 524 | 41 | 7 | 87 | 71 | 19 | 26 | 32 | Medium
Pennsylvania, York | 480 | 40 | 12 | 91 | 74 | 30 | 37 | 43 | Medium
Rhode Island, Newport | 10 | 41 | 9 | 85 | 72 | 28 | 35 | 41 | Medium
Rhode Island, Providence AP | 51 | 41 | 10 | 86 | 71 | 20 | 27 | 33 | Medium
South Carolina, Anderson | 782 | 34 | 23 | 92 | 74 | 28 | 35 | 41 | Medium
South Carolina, Beaufort, MCAS | 38 | 32 | 31 | 93 | 78 | 52 | 59 | 65 | Medium
South Carolina, Charleston AFB | 45 | 32 | 28 | 92 | 77 | 47 | 54 | 60 | Medium
South Carolina, Charleston CO | 3 | 32 | 28 | 92 | 78 | 54 | 61 | 67 | Low
South Carolina, Columbia AP | 213 | 34 | 24 | 94 | 75 | 31 | 38 | 44 | Medium
South Carolina, Florence AP | 147 | 34 | 27 | 94 | 76 | 37 | 44 | 50 | Medium
South Carolina, Georgetown | 14 | 33 | 26 | 90 | 78 | 57 | 64 | 70 | Medium
South Carolina, Greenville AP/Greer | 957 | 34 | 23 | 91 | 74 | 30 | 37 | 43 | Medium
South Carolina, Greenwood | 631 | 34 | 22 | 93 | 74 | 27 | 34 | 40 | Medium
South Carolina, Myrtle Beach, AFB | 25 | 33 | 29 | 90 | 78 | 57 | 64 | 70 | Medium
South Carolina, Orangeburg | 197 | 33 | 24 | 95 | 75 | 29 | 36 | 42 | Medium
South Carolina, Rock Hill | 667 | 35 | 23 | 94 | 74 | 25 | 32 | 38 | Medium
South Carolina, Spartanburg AP | 801 | 35 | 22 | 91 | 74 | 30 | 37 | 43 | Medium
South Carolina, Sumter-Shaw AFB | 252 | 34 | 29 | 93 | 75 | 33 | 40 | 46 | Medium
South Dakota, Aberdeen AP | 1296 | 45 | -15 | 91 | 72 | 18 | 25 | 31 | High
South Dakota, Brookings | 1647 | 44 | -13 | 92 | 72 | 16 | 23 | 29 | Medium
South Dakota, Chamberlain | 1739 | 43 | -7 | 94 | 71 | 7 | 14 | 20 | High
South Dakota, Huron AP | 1281 | 44 | -12 | 91 | 71 | 12 | 19 | 25 | High
South Dakota, Mitchell | 1303 | 43 | -10 | 93 | 71 | 9 | 16 | 22 | High
South Dakota, Pierre AP | 1742 | 44 | -9 | 95 | 69 | -6 | 1 | 7 | High
South Dakota, Rapid City AP | 3162 | 44 | -5 | 91 | 65 | -18 | -11 | -5 | High
South Dakota, Sioux Falls AP | 1418 | 43 | -11 | 90 | 72 | 19 | 26 | 32 | Medium
South Dakota, Watertown AP | 1748 | 45 | -15 | 91 | 72 | 18 | 25 | 31 | High
South Dakota, Yankton | 1305 | 43 | -7 | 91 | 72 | 28 | 35 | 41 | Medium
Tennessee, Athens | 858 | 33 | 18 | 92 | 73 | 22 | 29 | 35 | Medium
Tennessee, Bristol-Tri City AP | 1507 | 36 | 14 | 87 | 72 | 24 | 31 | 37 | Medium
Tennessee, Chattanooga AP | 665 | 35 | 20 | 92 | 75 | 34 | 41 | 47 | Medium
Tennessee, Clarksville | 550 | 36 | 12 | 93 | 74 | 27 | 34 | 40 | Medium
Tennessee, Columbia | 681 | 35 | 15 | 94 | 74 | 25 | 32 | 38 | Medium
Tennessee, Crossville | 1880 | 35 | 15 | 87 | 72 | 24 | 31 | 37 | Medium
Tennessee, Dyersburg | 338 | 36 | 15 | 94 | 77 | 44 | 51 | 57 | Medium
Tennessee, Greenville | 1608 | 35 | 16 | 90 | 72 | 19 | 26 | 32 | Medium
Tennessee, Jackson AP | 433 | 35 | 18 | 93 | 76 | 39 | 46 | 52 | Medium
Tennessee, Knoxville AP | 980 | 35 | 19 | 90 | 74 | 31 | 38 | 44 | Medium
Tennessee, Memphis AP | 258 | 35 | 21 | 94 | 77 | 44 | 51 | 57 | Medium
Tennessee, Murfreesboro | 615 | 35 | 14 | 94 | 74 | 25 | 32 | 38 | Medium
Tennessee, Nashville AP | 590 | 36 | 16 | 92 | 75 | 34 | 41 | 47 | Medium
Tennessee, Tullahoma | 1072 | 35 | 13 | 93 | 73 | 20 | 27 | 33 | Medium
Texas, Abilene AP | 1790 | 32 | 22 | 97 | 71 | 2 | 9 | 15 | Medium
Texas, Alice AP | 178 | 27 | 34 | 98 | 77 | 37 | 44 | 50 | Medium
Texas, Amarillo AP | 3604 | 35 | 12 | 94 | 66 | -17 | -10 | -4 | High
Texas, Austin AP | 597 | 30 | 30 | 96 | 74 | 22 | 29 | 35 | Medium
Texas, Bay City | 45 | 29 | 33 | 94 | 77 | 59 | 66 | 72 | Medium
Texas, Beaumont | 16 | 30 | 32 | 92 | 79 | 61 | 68 | 74 | Medium
Texas, Beeville | 190 | 28 | 33 | 98 | 77 | 37 | 44 | 50 | Medium
Texas, Big Springs AP | 2561 | 32 | 20 | 97 | 69 | -9 | -2 | 4 | Medium
Texas, Brownsville AP | 19 | 25 | 40 | 94 | 77 | 44 | 51 | 57 | High
Texas, Brownwood | 1386 | 31 | 22 | 99 | 73 | 11 | 18 | 24 | Medium
Texas, Bryan AP | 322 | 30 | 29 | 96 | 75 | 28 | 35 | 41 | Medium
Texas, Corpus Christi AP | 19 | 27 | 36 | 94 | 78 | 51 | 58 | 64 | Medium
Texas, Corsicana | 448 | 32 | 25 | 98 | 75 | 25 | 32 | 38 | Medium
Texas, Dallas, Fort Worth AP | 537 | 32 | 24 | 98 | 74 | 18 | 25 | 31 | Medium
Texas, Del Rio, Laughlin AFB | 1026 | 29 | 32 | 98 | 73 | 12 | 19 | 25 | Medium
Texas, Denton | 642 | 33 | 22 | 99 | 74 | 17 | 24 | 30 | Medium
Texas, Eagle Pass | 884 | 28 | 32 | 99 | 73 | 11 | 18 | 24 | Medium
Texas, El Paso AP | 3918 | 31 | 25 | 98 | 64 | -33 | -26 | -20 | High
Texas, Fort Worth, Carswell AFB | 650 | 32 | 22 | 99 | 74 | 17 | 24 | 30 | Medium
Texas, Fort Worth, Meacham Field | 709 | 32 | 24 | 98 | 74 | 18 | 25 | 31 | Medium
Texas, Galveston AP | 7 | 29 | 36 | 89 | 79 | 51 | 58 | 64 | Low
Texas, Greenville | 535 | 33 | 22 | 99 | 74 | 17 | 24 | 30 | Medium
Texas, Guadalupe Pass | 5453 | 31 | 19 | 89 | 60 | -39 | -32 | -26 | Medium
Texas, Harlingen | 35 | 26 | 39 | 94 | 77 | 44 | 51 | 57 | Medium
Texas, Houston AP | 96 | 29 | 31 | 94 | 77 | 44 | 51 | 57 | Medium
Texas, Houston, Hobby AP | 46 | 29 | 34 | 93 | 77 | 46 | 53 | 59 | Medium
Texas, Huntsville | 363 | 30 | 27 | 98 | 75 | 25 | 32 | 38 | Medium
Texas, Junction | 1713 | 30 | 23 | 98 | 71 | 1 | 8 | 14 | High
Texas, Killeen-Gray AFB | 1014 | 31 | 27 | 96 | 73 | 16 | 23 | 29 | Medium
Texas, Kingsville, NAS | 50 | 27 | 36 | 96 | 78 | 47 | 54 | 60 | Medium
Texas, Lamesa | 2998 | 32 | 17 | 96 | 69 | -7 | 0 | 6 | High
Texas, Laredo AFB | 512 | 27 | 36 | 101 | 74 | 14 | 21 | 27 | Medium
Texas, Longview 365 | 32 | 24 | 97 | 76 | 33 | 40 | 46 | M
Texas, Lubbock AP | 3254 | 33 | 17 | 95 | 67 | -13 | -6 | 0 | High
Texas, Lubbock, Reese AFB | 3338 | 33 | 18 | 95 | 67 | -14 | -7 | -1 | High
Texas, Lufkin AP | 277 | 31 | 27 | 95 | 77 | 42 | 49 | 55 | Medium
Texas, Marfa | 4859 | 30 | 19 | 92 | 61 | -39 | -32 | -26 | High
Texas, McAllen | 108 | 26 | 40 | 98 | 76 | 31 | 38 | 44 | Medium
Texas, Midland AP | 2851 | 32 | 22 | 97 | 67 | -19 | -12 | -6 | High
Texas, Mineral Wells AP | 972 | 32 | 22 | 99 | 74 | 17 | 24 | 30 | Medium
Texas, Palestine CO | 422 | 31 | 27 | 98 | 76 | 31 | 38 | 44 | Medium
Texas, Pampa | 3244 | 35 | 12 | 96 | 67 | -15 | -8 | -2 | High
Texas, Pecos | 2611 | 31 | 21 | 98 | 69 | -10 | -3 | 3 | High
Texas, Plainview | 3374 | 34 | 13 | 96 | 68 | -10 | -3 | 3 | High
Texas, Port Arthur AP | 16 | 30 | 31 | 93 | 78 | 52 | 59 | 65 | Medium
Texas, San Angelo, Goodfellow AFB | 1877 | 31 | 24 | 97 | 70 | -3 | 4 | 10 | Medium
Texas, San Antonio AP | 788 | 29 | 30 | 96 | 73 | 16 | 23 | 29 | Medium
Texas, San Antonio, Kelly AFB | 690 | 29 | 32 | 97 | 74 | 20 | 27 | 33 | Medium
Texas, San Antonio, Randolph AFB | 761 | 29 | 31 | 96 | 74 | 22 | 29 | 35 | Medium
Texas, Sanderson | 2838 | 30 | 28 | 95 | 68 | -11 | -4 | 2 | Medium
Texas, Sherman-Perrin AFB | 763 | 33 | 20 | 98 | 75 | 25 | 32 | 38 | Medium
Texas, Snyder | 2430 | 32 | 18 | 98 | 70 | -5 | 2 | 8 | Medium
Texas, Temple | 682 | 31 | 27 | 99 | 74 | 17 | 24 | 30 | Medium
Texas, Tyler AP | 544 | 32 | 24 | 97 | 76 | 33 | 40 | 46 | Medium
Texas, Vernon | 1264 | 34 | 17 | 100 | 73 | 9 | 16 | 22 | Medium
Texas, Victoria AP | 115 | 28 | 33 | 94 | 76 | 37 | 44 | 50 | Medium
Texas, Waco AP | 501 | 31 | 26 | 99 | 75 | 23 | 30 | 36 | Medium
Texas, Wichita Falls AP | 994 | 34 | 19 | 100 | 73 | 9 | 16 | 22 | Medium
Utah, Cedar City AP | 5626 | 37 | 8 | 91 | 59 | -47 | -40 | -34 | High
Utah, Logan | 4454 | 41 | 2 | 91 | 61 | -37 | -30 | -24 | High
Utah, Moab | 4553 | 38 | 11 | 98 | 60 | -53 | -46 | -40 | High
Utah, Ogden, Hill AFB | 4785 | 41 | 11 | 90 | 60 | -41 | -34 | -28 | High
Utah, Price | 5921 | 39 | 5 | 91 | 60 | -42 | -35 | -29 | High
Utah, Provo | 4448 | 40 | 6 | 96 | 62 | -40 | -33 | -27 | High
Utah, Richfield | 5279 | 38 | 5 | 91 | 60 | -42 | -35 | -29 | High
Utah, St. George CO | 2941 | 37 | 21 | 101 | 65 | -36 | -29 | -23 | High
Utah, Salt Lake City AP | 4220 | 40 | 11 | 94 | 62 | -37 | -30 | -24 | High
Utah, Vernal AP | 5274 | 40 | 0 | 89 | 60 | -39 | -32 | -26 | High
Vermont, Barre | 1165 | 44 | -11 | 81 | 69 | 17 | 24 | 30 | Medium
Vermont, Burlington AP | 332 | 44 | -6 | 84 | 69 | 12 | 19 | 25 | Medium
Vermont, Montpelier/ Barre | 1165 | 44 | -6 | 83 | 68 | 8 | 15 | 21 | Medium
Vermont, Rutland | 787 | 43 | -8 | 84 | 70 | 18 | 25 | 31 | Medium
Virginia, Charlottsville | 870 | 38 | 18 | 91 | 74 | 30 | 37 | 43 | Medium
Virginia, Danville AP | 572 | 36 | 16 | 92 | 73 | 22 | 29 | 35 | Medium
Virginia, Fort Belvoir | 69 | 38 | 18 | 93 | 76 | 39 | 46 | 52 | Medium
Virginia, Fredricksburg | 85 | 38 | 14 | 93 | 75 | 33 | 40 | 46 | Medium
Virginia, Hampton, Langley AFB | 10 | 37 | 24 | 91 | 77 | 49 | 56 | 62 | Medium
Virginia, Harrisonburg | 1201 | 38 | 16 | 91 | 72 | 18 | 25 | 31 | Medium
Virginia, Lynchburg AP | 916 | 37 | 17 | 90 | 74 | 31 | 38 | 44 | Medium
Virginia, Newport News | 41 | 37 | 22 | 92 | 77 | 47 | 54 | 60 | Medium
Virginia, Norfolk AP | 22 | 36 | 24 | 91 | 76 | 42 | 49 | 55 | Medium
Virginia, Oceana, NAS | 22 | 36 | 25 | 91 | 76 | 42 | 49 | 55 | Medium
Virginia, Petersburg | 193 | 37 | 17 | 92 | 76 | 41 | 48 | 54 | Medium
Virginia, Quantico MCAS | 12 | 38 | 21 | 92 | 76 | 41 | 48 | 54 | Medium
Virginia, Richmond AP | 164 | 37 | 18 | 92 | 75 | 34 | 41 | 47 | Medium
Virginia, Roanoke AP | 1193 | 37 | 17 | 89 | 72 | 21 | 28 | 34 | Medium
Virginia, Staunton | 1201 | 38 | 16 | 91 | 72 | 18 | 25 | 31 | Medium
Virginia, Sterling | 322 | 38 | 14 | 90 | 74 | 31 | 38 | 44 | Medium
Virginia, Reagan, National AP | 66 | 38 | 20 | 92 | 76 | 41 | 48 | 54 | Medium
Virginia, Winchester | 727 | 39 | 10 | 90 | 74 | 31 | 38 | 44 | Medium
Washington, Aberdeen | 12 | 47 | 28 | 77 | 62 | -12 | -5 | 1 | Medium
Washington, Bellingham AP | 158 | 48 | 21 | 76 | 64 | -1 | 6 | 12 | Medium
Washington, Bremerton | 7 | 47 | 25 | 78 | 64 | -4 | 3 | 9 | Medium
Washington, Ellensburg AP | 1760 | 47 | 6 | 91 | 64 | -25 | -18 | -12 | High
Washington, Everett-Paine AFB | 596 | 47 | 25 | 76 | 64 | -1 | 6 | 12 | Medium
Washington, Hanford | 732 | 46 | 12 | 96 | 65 | -28 | -21 | -15 | High
Washington, Kennewick | 531 | 46 | 11 | 96 | 67 | -18 | -11 | -5 | High
Washington, Longview | 12 | 46 | 24 | 85 | 67 | 0 | 7 | 13 | High
Washington, Moses Lake, Larson AFB | 1185 | 47 | 7 | 94 | 65 | -25 | -18 | -12 | High
Washington, Olympia AP | 215 | 47 | 23 | 83 | 65 | -7 | 0 | 6 | High
Washington, Port Angeles | 288 | 48 | 27 | 69 | 61 | -4 | 3 | 9 | Medium
Washington, Quillayute | 201 | 47 | 27 | 74 | 61 | -12 | -5 | 1 | Medium
Washington, Seattle-Boeing Fld | 18 | 47 | 28 | 81 | 64 | -9 | -2 | 4 | Medium
Washington, Seattle CO | 14 | 47 | 27 | 82 | 66 | 0 | 7 | 13 | Medium
Washington, Seattle-Tacoma AP | 429 | 47 | 26 | 80 | 64 | -7 | 0 | 6 | Medium
Washington, Spokane AP | 2366 | 47 | 7 | 89 | 61 | -36 | -29 | -23 | Medium
Washington, Stampede Pass | 3967 | 47 | 10 | 74 | 56 |  |  |  | Medium
Washington, Tacoma-McChord AFB | 322 | 47 | 24 | 82 | 63 | -15 | -8 | -2 | Medium
Washington, Walla Walla AP | 1206 | 46 | 12 | 95 | 65 | -26 | -19 | -13 | High
Washington, Wenatchee | 1243 | 47 | 9 | 92 | 65 | -21 | -14 | -8 | High
Washington, Yakima AP | 1052 | 46 | 11 | 92 | 64 | -26 | -19 | -13 | High
West Virginia, Beckley | 2504 | 37 | 4 | 81 | 69 | 17 | 24 | 30 | Medium
West Virginia, Bluefield AP | 2858 | 37 | 12 | 83 | 69 | 14 | 21 | 27 | Medium
West Virginia, Charleston AP | 939 | 38 | 11 | 88 | 73 | 29 | 36 | 42 | Medium
West Virginia, Clarksburg | 1203 | 39 | 10 | 90 | 73 | 25 | 32 | 38 | Medium
West Virginia, Elkins AP | 1948 | 38 | 5 | 83 | 70 | 19 | 26 | 32 | Medium
West Virginia, Huntington CO | 828 | 38 | 11 | 89 | 73 | 27 | 34 | 40 | Medium
West Virginia, Martinsburg AP | 556 | 39 | 14 | 91 | 73 | 24 | 33 | 39 | Medium
West Virginia, Morgantown AP | 1247 | 39 | 11 | 87 | 71 | 19 | 26 | 32 | High
West Virginia, Parkersburg CO | 858 | 39 | 11 | 88 | 72 | 23 | 32 | 38 | Medium
West Virginia, Wheeling | 1195 | 40 | 5 | 86 | 71 | 20 | 27 | 33 | Medium
Wisconsin, Appleton | 918 | 44 | -9 | 86 | 72 | 26 | 33 | 39 | Medium
Wisconsin, Ashland | 826 | 46 | -16 | 82 | 68 | 10 | 17 | 23 | Medium
Wisconsin, Beloit | 817 | 42 | -3 | 90 | 75 | 38 | 45 | 51 | Medium
Wisconsin, Eau Claire AP | 907 | 44 | -13 | 87 | 71 | 19 | 26 | 32 | Medium
Wisconsin, Fond du Lac | 809 | 43 | -8 | 86 | 72 | 26 | 33 | 39 | Medium
Wisconsin, Green Bay AP | 682 | 44 | -8 | 85 | 72 | 28 | 35 | 41 | Medium
Wisconsin, LaCrosse AP | 651 | 43 | -8 | 88 | 73 | 29 | 36 | 42 | Medium
Wisconsin, Madison AP | 858 | 43 | -6 | 87 | 72 | 24 | 31 | 37 | Medium
Wisconsin, Manitowoc | 651 | 44 | -7 | 86 | 72 | 26 | 33 | 39 | Medium
Wisconsin, Marinette | 703 | 45 | -11 | 84 | 71 | 23 | 30 | 36 | Medium
Wisconsin, Milwaukee AP | 723 | 43 | -2 | 86 | 72 | 26 | 33 | 39 | Medium
Wisconsin, Racine | 674 | 42 | -2 | 88 | 73 | 29 | 36 | 42 | Medium
Wisconsin, Sheboygan | 749 | 43 | -6 | 86 | 73 | 32 | 39 | 45 | Medium
Wisconsin, Stevens Point | 1110 | 43 | -11 | 89 | 73 | 27 | 34 | 40 | Medium
Wisconsin, Waukesha | 911 | 43 | -5 | 87 | 73 | 33 | 40 | 46 | Medium
Wisconsin, Wausau AP | 1201 | 44 | -9 | 85 | 70 | 16 | 23 | 29 | Medium
Wyoming, Big Piney | 6990 | 42 | -15 | 80 | 53 | -58 | -51 | -45 | High
Wyoming, Casper AP | 5348 | 42 | -5 | 89 | 58 | -49 | -42 | -36 | High
Wyoming, Cheyene AP | 6156 | 41 | 0 | 85 | 57 | -47 | -40 | -34 | High
Wyoming, Cody AP | 5098 | 44 | -7 | 87 | 58 | -45 | -38 | -32 | High
Wyoming, Evanston | 7163 | 41 | -3 | 84 | 55 | -55 | -48 | -42 | High
Wyoming, Gillette | 4363 | 44 | -7 | 91 | 61 | -38 | -31 | -25 | High
Wyoming, Lander AP | 5586 | 42 | -7 | 87 | 58 | -46 | -39 | -33 | High
Wyoming, Laramie AP | 7278 | 41 | -6 | 81 | 56 | -46 | -39 | -33 | High
Wyoming, Newcastle | 4174 | 43 | -12 | 87 | 63 | -21 | -14 | -8 | High
Wyoming, Rawlins | 6813 | 41 | -4 | 83 | 57 | -44 | -37 | -31 | High
Wyoming, Rock Springs AP | 6760 | 41 | -2 | 84 | 54 | -60 | -53 | -47 | High
Wyoming, Sheridan AP | 4024 | 44 | -8 | 90 | 61 | -36 | -29 | -23 | High
Wyoming, Torrington | 4205 | 42 | -8 | 91 | 62 | -32 | -25 | -19 | High
Wyoming, Worland | 4227 | 43 | -13 | 93 | 63 | -30 | -23 | -17 | High

## J1 Form
FORM J1AE ● ABRIDGED VERSION of MANUAL J, 8TH EDITION
Project |  |  |  |  | Design State & City
Indoor Design Heating db |  |  |  | 70 | Outdoor 99% db | #N/A | HTD |  | #N/A
Indoor Design Cooling db |  |  |  | 75 | Outdoor 1% db | #N/A | CTD |  | #N/A
Indoor Design Cooling RH |  |  |  | 50% | Grains Difference | #N/A | Daily Range |  | #N/A
Latitude |  |  |  | #N/A | Elevation | #N/A | ACF |  | #N/A | Block Load |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room--> |  |  | Room-->
|  | Glass |  | . |  |  | Heating | Cooling | Net | Heating | Cooling | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH |  | Net | BTUH
|  | Direction |  | Construction Detail |  |  | HTM | HTM | Area | BTUH | BTUH | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling | Area | Heating | Cooling
6A | Windows | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| & Glass | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| Doors | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
6B | Skylights | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
|  | 0 |  | 0 |  |  |  |  | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
7 | Wood & |  | a | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
| Metal |  | b | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
| Doors |  | c | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
8 | Above Grade Walls |  | a | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  | b | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  | c | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  | d | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  | e | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A
| Partition Walls |  | f | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
|  |  | g | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
9 | Below Grade Walls |  | a | [5 empty] | 0 | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  | 0 | #VALUE! | 0 | #N/A
|  |  | b | [5 empty] | 0 | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  | 0 | #VALUE! | 0 | #N/A
10 | Ceilings |  | a | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
|  |  | b | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
|  |  | c | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
| Partition Ceilings |  | d | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
|  |  | e | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
11 | Passive Floors |  | a | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
|  |  | b | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
| Exposed Floors |  | c | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
| Slab (Perimeter Ft.) |  | d | [5 empty] | 0 | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  | 0 | #VALUE! | 0 | #N/A
| Basement Floor |  | e | [5 empty] | 0 | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  | 0 |  |  | #N/A
| Partition Floors |  | f | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
|  |  | g | [5 empty] | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #N/A | #N/A
12 | Infiltration | Envelope Leakage |  | Average | Heated & Cooled Floor Area = Sq. Ft. |  | Above Grade = Cu. Ft. |  |  | #N/A | #N/A | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | WAR | #N/A |  | #VALUE! | #N/A | 0
|  | No. of Fireplaces |  | 0 | [7 empty] | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | #DIV/0! |  | #N/A | 0 | 0 | #N/A
[13 empty] | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A |  | #VALUE! | #N/A
13 | Internal Gains |  |  | Number of Bedrooms |  | 3 | Occupants |  | 4 |  | #N/A |  |  | 0 | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 |  | 0 | 920
|  |  |  | Appliance - 1200 BTUH | [6 empty] | #N/A | [45 empty] | 0 | 0 | #VALUE! | 1200 | 0
14 | Sub Totals | [8 empty] | #VALUE! | #N/A |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE!
15 | Duct Loss & Gain |  |  | 7E-T&B SA in Attic, RA Riser in Floor to Ceiling Chase, Perimeter Supply Outlets | [5 empty] | #VALUE! | #N/A |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE!
|  |  |  | R-Value = 6 | Leakage Class .12/.24 |  | #N/A | #N/A | [48 empty] | TRUE | TRUE
|  |  |  | Installed Square Feet of Surface or Default = 1 |  | Supply | 1 | Return | 1
16 | Ventilation | Combustion Air From Conditioned Space |  |  |  |  | None |  | 0 | #N/A | #N/A | [45 empty] | FALSE | FALSE
19 | Blower Heat Gain |  |  | Manufacturer's performance data has no blower heat discount | [6 empty] | 1707
20 | Total Sensible Loss or Gain | [8 empty] | #N/A | #N/A |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE!
[6 empty] | 21 | Latent Infiltration load for cooling |  |  |  | #N/A
Enter Company Name Here | [6 empty] | Latent load for occupants |  |  |  | 800
Enter Company Address Here | [6 empty] | Latent load for plants | Small | Medium | Large | 0
Enter Company City, State and Zip Code Here
Enter Company Phone Numbers Here | [6 empty] | Latent load for duct in unconditioned space |  |  |  | #N/A
Enter Website or Email Address Here | [6 empty] | Latent ventilation load for cooling |  |  |  | #N/A
[7 empty] | Total Latent Gain |  |  |  | #N/A
Furnace
Water Heater

## Summary
MANUAL J8AE ● SUMMARY REPORT
Project | 0 |  | Mfg. Equipment Sensible Heat Ratio |  | 0.75 | ACCA Manual D CFM |  |  |  | 0
|  |  | Manual Overide Entry for Design CFM |  | 0 |  |  |  |  | #N/A
Room Name |  | HEAT LOSS | HTG CFM | HEAT GAIN | CLG CFM |  |  |  | #N/A | #N/A
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 1 | 200
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 6000 | 400
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 12000 | 600
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 18000 | 800
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 24000 | 1000
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 30000 | 1200
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 36000 | 1400
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 42000 | 1600
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 48000 | 1800
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 54000 | 2000
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 60000 | 2200
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 66000 | 2400
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 72000 | 2600
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 78000 | 2800
0 |  | #VALUE! | #N/A | #VALUE! | #N/A | #N/A | #VALUE! | #VALUE! | 84000 | 3000
Room Envelope Totals |  | #VALUE! | #N/A | #VALUE! | #N/A |  | #VALUE! | #VALUE!
Total Area | Construction Components | HEAT LOSS |  | HEAT GAIN
0 | Windows & Glass Doors | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Skylights | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Wood & Metal Doors | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Above Grade Walls | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Partition Walls | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Below Grade Walls | #VALUE! | #VALUE!
0 | Ceilings | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Partition Ceilings | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Passive Floors | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Exposed Floors | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | Slab Floors | #VALUE! | #VALUE!
0 | Basement Floors | #VALUE! | #VALUE!
0 | Partition Floors | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Infiltration | #N/A | #N/A | #N/A | #N/A
| Internal Gains |  |  | #N/A | #N/A
| Duct Loss & Gain | #VALUE! | #VALUE! | #N/A | #N/A
| Ventilation | #N/A | #N/A | #N/A | #N/A
| Blower Heat Gain |  |  | 1707 | #N/A
| Total Sensible | #N/A | #N/A | #N/A | #N/A
| Total Latent |  |  | #N/A
| Total Cooling Load |  |  | #N/A

## Glass Sched
VERTICAL GLASS | [12 empty] | X (Ft.)
# | Heating Table 2A Construction Numbers and Details that Apply to this Load Estimate | Direction Glass Faces | Htg HTM | Clg Unshaded HTM | Clg Shaded HTM | Clg Avg HTM | Width of opening (Ft) | Height of opening H (Ft) | Overhang Distance X (Ft) | Top of Opening to Overhang Y (Ft) | Adjustment for Projected Window or French Door | Clg HTM Adjustment |  |  | SLM Value | Shade Line (Z) = (X x SLM) | Shaded glass height (S) = (Z - Y) | Unshaded glass height (U) = (H - S) | Shaded area (S x W) | Unshaded area (U x W) | HTM Adj. | Clg HTM Adj. | Cooling Shaded BTUH | Cooling Unshaded BTUH | Heating BTUH
#1 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | Lat | #N/A |  | N | NE/NW | E/W | SE/SW | S
#2 | [6 empty] | 1 |  |  |  | None | None |  | Y (FT.) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! |  |  | 25 | 0 | 1.06 | 0.83 | 1.89 | 10.1
#3 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | E/W | 1 | 26 | 0 | 1.06 | 0.83 | 1.89 | 10.1
#4 | [6 empty] | 1 |  |  |  | None | None |  | H (Ft.) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | N | 4 | 27 | 0 | 1.06 | 0.83 | 1.89 | 10.1
#5 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | NE/NW | 5 | 28 | 0 | 1.14 | 0.83 | 1.63 | 5.4
#6 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | S | 3 | 29 | 0 | 1.14 | 0.83 | 1.63 | 5.4
#7 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | SE/SW | 2 | 30 | 0 | 1.14 | 0.83 | 1.63 | 5.4
#8 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! |  |  | 31 | 0 | 1.14 | 0.83 | 1.63 | 5.4
#9 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | None | 1 | 32 | 0 | 1.14 | 0.83 | 1.63 | 5.4
#10 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | Bug Screen | 0.9 | 33 | 0 | 1.22 | 0.81 | 1.13 | 3.53
#11 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! |  |  | 34 | 0 | 1.22 | 0.81 | 1.13 | 3.53
#12 | [6 empty] | 1 |  |  |  | None | None |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | #N/A | #N/A | #VALUE! | None | 1 | 35 | 0 | 1.22 | 0.81 | 1.13 | 3.53
[26 empty] | Bay Window | 1.15 | 36 | 0 | 1.22 | 0.81 | 1.13 | 3.53
SKYLIGHTS | [25 empty] | Garden Window | 2 | 37 | 0 | 1.22 | 0.81 | 1.13 | 3.53
# | Heating Table 2A Construction Numbers and Details that Apply to this Load Estimate | Direction Glass Faces | Htg HTM | Clg HTM | [21 empty] | French Door | 0.7 | 38 | 0 | 1.31 | 0.81 | 1.13 | 2.6
#1 | [27 empty] | 39 | 0 | 1.31 | 0.81 | 1.13 | 2.6
#2 | [27 empty] | 40 | 0 | 1.31 | 0.81 | 1.13 | 2.6
#3 | [25 empty] | N |  | 41 | 0 | 1.31 | 0.81 | 1.13 | 2.6
#4 | [25 empty] | NE/NW |  | 42 | 0 | 1.31 | 0.81 | 1.13 | 2.6
[26 empty] | E/W |  | 43 | 0 | 1.4 | 0.8 | 1.13 | 2.05
For Heat Loss | [25 empty] | SE/SW |  | 44 | 0 | 1.4 | 0.8 | 1.13 | 2.05
* Use the Heating column "look-up" menus to list the windows and glass doors, and to select a projected window / French door | [25 empty] | S |  | 45 | 0 | 1.4 | 0.8 | 1.13 | 2.05
adjustment. | [27 empty] | 46 | 0 | 1.4 | 0.8 | 1.13 | 2.05
* Use the "look-up" menu in the Heating column to list the skylights. | [27 empty] | 47 | 0 | 1.4 | 0.8 | 1.13 | 2.05
* Enter values for the width and height of the rough opening in decimal feet. | [27 empty] | 48 | 0 | 1.49 | 0.79 | 1.01 | 1.7
For Heat Gain | [27 empty] | 49 | 0 | 1.49 | 0.79 | 1.01 | 1.7
* Use the Cooling column "look-up" menus to list the windows and glass doors and to select exposure directions; and to select | [27 empty] | 50 | 0 | 1.49 | 0.79 | 1.01 | 1.7
an insect screen adjustment (the projected window or French door adjustment for heating also applies to cooling).
* Enter values for the width and height of the rough opening and the overhang dimensions (X & Y) in decimal feet.
* Use the "look-up" menu in the Cooling column to list the skylights and to select exposure directions.
Note: For heating-only, leave the cooling column selections blank.

## Doors
Table 4A -- Construction Number 11 -- Wood and Metal Doors | U-Value
Construction Number; Door Type; Core Insulation
Population Instructions for Wood and Metal Doors
1) Input values are entered in the white cells (as requested by column headings; notes provide additional guidance).
2) Input values for wood and metal doors are extracted from Table 4A (Construction #11) in the printed MJ8ae book.
* Construction attributes are extracted from plans or by site inspection.
* You can enter up to 6 different door types (construction number 11A and 11B).
* For example:
Construction Number; Door Type; Core Insulation | U-Value
11N, Metal, Polystyrene Core | 0.35
Notes
Door Glass
* Ignore door glass if the glass area is less than 51 percent of the door area.
* Classify as a French door (under the "Glass" tab if the glass area exceeds
50 percent of the door area.

## Glass
Table 2A/3A -- Construction Numbers 1 through 7 & 10 -- Vertical Glass Heat Loss | Heating U-Value | Cooling HTM
Enter Construction Number, Glass Type, # Panes, Sash Type, Frame Type, Shading |  | N | NE/NW | E/W | SE/SW | S
N
NE/NW
E/W
SE/SW
S
Table 2A/3A -- Construction Numbers 8 & 9 -- Skylight Heat Loss | Heating U-Value | Cooling HTM
Enter Construction Number, Glass Type, # Panes, Sash Type |  | N | NE/NW | E/W | SE/SW | S
Population Instructions for Windows, Glass Doors and Skylights
1) Input values are entered in the white cells (as requested by column headings; notes provide additional guidance).
2) Input values for windows and glass doors are extracted from Table 2A and Table 3A in the printed MJ8ae book; Table 3C applies to skylights.
3) Begin with Table 2A (the construction number applies to heating and cooling, the U-value applies to heating).
* Construction attributes are extracted from plans or by site inspection.
* The construction number and U-value are extracted from Table 2A.
* Input values from Table 2A or Appendix 10 of the unabridged version of Manual J are valid entries.
* You can enter up to 8 different vertical glass types for heat loss
* For example
Construction Number; Glass Type; Number of Panes; Type of Sash; Type of Frame | U-Value
1C-cm, Clear, Single Pane / Storm, Operable, Metal no Break | 0.87
* You can enter up to 5 different skylight types for heat loss
* For example
Construction Number; Glass Type; Number of Panes; Type of Sash | U-Value
8Bc-4, Flat Clear, Double Pane, Wood | 0.94
4) Refer to Table 3A for cooling HTM values for windows and glass doors.
* You can enter up to 5 different glass types for vertical glass heat gain
* HTM values from Table 3D-1 of the unabridged version of Manual J are valid entries.
* For example:
Glass Type; Number of Panes; Type of Internal Shade; Rounded CTD | N | NE/NW | E/W | SE/SW | S
Double Pane; Clear; Horiz. Blinds @ 45 Deg; 15 | 13 | 30 | 43 | 37 | 21
5) Refer to Table 3C for cooling HTM values for skylights
* You can enter up to 5 different glass types for skylight heat gain
* HTM values from Table 3D-1 of the unabridged version of Manual J are valid entries.
* For example:
Glass Type; Number of Panes; Tilt Angle; Rounded CTD | N | NE/NW | E/W | SE/SW | S
Double Pane, Clear, 30 Deg; 15 | 142 | 156 | 167 | 162 | 150
Notes
Construction Attributes for Windows and Glass Doors
* Default glass type = clear (for all MJ8ae applications)
* Number of panes = single, double or triple
* Type of sash = fixed or operable
* Type of frame = Metal, no break; metal with break; wood (clad wood or vinyl = wood)
* Type of internal shade = None; Blinds @ 45 deg.; Drape or Roller Shade, half drawn
* Mandatory default for internal shade = Blinds @ 45 deg (no shade for day-light window).
Construction Attributes for Skylights
* Default glass type = flat clear (for all MJ8ae applications)
* Number of panes = single, double or triple
* Default glazing shape = flat (for all MJ8ae applications)
* Type of sash = Metal, no break; metal with break; wood (clad wood or vinyl = wood)
* Type of frame = Metal, no break; metal with break; wood (clad wood or vinyl = wood)
* Default curb attributes = Uninsulated wood 2x4 (for all MJ8ae applications)
* Default curb size = Small (for all MJ8ae applications -- see Table 2B-4)

## Walls
Table 4A -- Constructions 12, 13 & 15 -- Above Grade Walls | U-Value | Group | Shaded Wall | CLTD | Row | Col
Construction Number; Wall Type; Board R-Value; Cavity R-Value, Exterior Finish |  |  | Wall
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
|  |  | No | 0 | #N/A | #N/A | 0
Table 4A -- Constructions 12 & 13 -- Partitions | U-Value | PTDH | PTDC
Construction Number; Wall Type; Board R-Value; Cavity R-Value, Finish |  |  |  | H-HTM | C-HTM
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Table 4A -- Construction Number 15 -- Below Grade Walls | U-Value
Construction Number; Wall Type; Board R-Value; Cavity R-Value, Floor Depth
|  |  |  | #N/A | #N/A | #N/A
|  |  |  | #N/A | #N/A | #N/A
|  |  |  | #N/A | #N/A | #N/A
|  |  |  | #N/A | #N/A | #N/A
Population Instructions for Walls and Partitions
1) Input values are entered in the white cells (as requested by column headings; notes provide additional guidance).
2) Input values for above grade walls, partitions and below grade walls are extracted from Table 4A in the printed MJ8ae book.
* Construction attributes are extracted from plans or by site inspection.
* Input values for all constructions listed in Table 4A of the unabridged version of Manual J are valid entries.
3) You can enter up to 10 different above grade wall types (construction numbers 12, 13 and the above grade potion of number 15).
* The construction number, U-value and group number are extracted from Table 4A (leave group number blank for heating-only).
* Click on the Shaded Wall lookup value "Yes" if the wall is exposed to the outdoor air and shaded by a roof or overhang.
* For example:
Construction Number; Wall Type; Board R; Cavity R, Exterior Finish | U-Value | Group | Shaded Wall
12B-0bw, Frame, R0 board, R11 cavity, Brick | 0.097 | H | No
13C-2oc, OC Block, R2 Board, R13 Cavity, Any finish, Car port | 0.075 | I | Yes
15A-11-0ocw-6, OC Block + studs, R2 board, R11 cavity, Above grade area | 0.103 | H | No
4) You can enter up to 5 different partition walls (construction numbers 12 and 13).
* The construction number and U-value are extracted from Table 4A.
* Values for PTDH and PTDC are obtained from Table 4C or by personnel observations or experience (leave PTDC blank for heating-only).
* For example, partition wall for garage 1 (see Table 4C): 99% db = 20 ºF & room = 70 °F; 1% drybulb = 100 °F, high daily range & room = 75 °F
Construction Number; Wall Type; Board R; Cavity R, Finish | U-Value | PTDH | SE/SW
12B-0bw, Frame, R0 board, R11 cavity, Brick | 0.097 | 50 | 37
5) You can enter up to 5 different below grade walls (construction number 15).
* The construction number and U-value are extracted from Table 4A.
* For example:
Construction Number; Wall Type; Board R; Cavity R, Basement floor depth | U-Value
15A-11-0ocw-6, OC Block + studs, R2 board, R11 cavity, 6 feet | 0.046
Notes
Construction Attributes for Walls
* Wall type = Frame with wood studs or block with open cores (for MJ8ae applications)
* Board R = Insulation board R-value (thin plywood or particle board, etc. sheathing = R0)
* Cavity R = R-value of insulation in stud cavity
* Exterior finish = Brick or siding (stucco = siding; no finish for below grade wall)
Above Grade Walls
* Unshaded wall exposed to outdoor air (uses "Wall" CLTD, Table 4B).
* Wall always shaded and exposed to outdoor air (uses "Shaded Wall" CLTD, Table 4B).
* Garage partition: Classify as "Shaded Wall" if the overhead door is normally open.
* Applies to the above grade area of a basement wall.
* CLTD lookup is automatic, just enter group number (click check box for shaded wall).
Partition Wall (PTDH and PTDC)
* A wall that separates a conditioned space from an unconditioned space.
* A garage partition, providing the overhead door is normally closed.
* Use Table 4C to estimate PTDH and PTDC for selected scenarios.
* Values for PTDH and PTDC may be based on personal observations and experience.
* If the partition has plaster board on both sides, use the values for exterior finish = "Siding."
Below Grade Walls
* Walls that are not more than two feet below grade are classified as above grade.
* Applies to the below grade area of basement wall that is partially above grade.

## Ceilings
Table 4A -- Construction Numbers 16, 17 & 18 -- Ceilings | U-Value | CLTD
Construction Number; Type of Ceiling; R-Value; Roof Material and Roof Color
Construction Number; R-Value; Partition | U-Value | PTDH | PTDC
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Population Instructions for Ceilings and Partition Ceilings
1) Input values are entered in the white cells (as requested by column headings; notes provide additional guidance).
2) Input values for ceilings and partition ceilings are extracted from Table 4A in the printed MJ8ae book.
* Construction attributes are extracted from plans or by site inspection.
* Input values for ceiling constructions listed in Table 4A (#16A -> #16F, #17A -> #17C or #18A -> #18C) of the unabridged version of Manual J are valid entries.
3) You can enter up to 6 different ceiling types (construction numbers 16, 17 and 18).
* The construction number, U-value and CLTD are extracted from Table 4A (CLTD not required for heating-only).
* For example:
Construction Number; Type of Ceiling; R-Value; Roof Material and Roof Color | U-Value | CLTD
16B-19; FHA Vented Attic; R19; Asphalt Shingles; Dark | 0.049 | 55
4) You can enter up to 3 different partition ceilings (construction number 16B).
* The construction number and U-value are extracted from Table 4A, Construction 16B.
* Values for PTDH and PTDC are obtained from Table 4C or by personnel observations or experience (leave PTDC blank for heating-only).
* For example, conditioned space under encapsulated attic (see Table 4C): 99% db = 40 ºF & room = 70 °F; 1% drybulb = 90 °F, low daily range & room = 75 °F
Construction Number; Ceiling R-Value, Partition | U-Value | PTDH | PTDC
16B; R19; Partition | 0.097 | 4 | 3
Notes
Construction Attributes for Ceilings (for MJ8ae Applications)
* Ceiling below attic = #16B (FHA ventilated attic, no radiant barrier, R0 to R56, dark shingle roof).
* Ceiling below deck on exposed beams = #17A (R0 to R34, dark shingle roof).
* Ceiling below deck-joist-ceiling sandwich = #18A (R0 to R38, dark shingle roof).
Construction Attributes for Partition Ceilings
* Ceiling below an unconditioned room = #16B (use U-value for R0 to R56 insulation).
* Ceiling below an encapsulated attic = #16B (use U-value for R0 to R56 insulation).
* Use Table 4C to estimate PTDH and PTDC for ceiling under an encapsulated attic.
* Values for PTDH and PTDC may be based on personal observations and experience.
Attic Duct Systems
* Load factors for attic duct systems shall be compatible with the type of attic ceiling.
* For 16B ceilings, use MJ8ae Tables 7A-AE, 7B-AE or 7C-AE
* See unabridged Manual J tables 7A, 7C, 7D, 7E or 7F for duct systems above other types of attic ceilings.
* Use unabridged Manual J Table 7F for duct system in an encapsulated attic.

## Floors
Table 4A -- Floors | U-Value | PTDH | PTDC
Construction Number 19 -- Floor Over Enclosed Unconditioned Crawlspace or Basement |  | PTDH | PTDC
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Construction Number 20 -- Floor Over Open Crawlspace or Garage | U-Value
|  |  |  | #N/A | #N/A | #N/A
|  |  |  | #N/A | #N/A | #N/A
|  |  |  | #N/A | #N/A | #N/A
Construction Numbers 19 & 20, Partition Floors | U-Value | PTDH | PTDC
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
Construction Number 21, Basement Floor | U-Value
#N/A
#N/A
#N/A
Construction Number 22, Concrete Slab-On-Grade | F-Value
Population Instructions for Floors and Floor Partitions
1) Input values are entered in the white cells (as requested by column headings; notes provide additional guidance).
2) Input values for floors and partition floors are extracted from Table 4A in the printed MJ8ae book.
* Construction attributes are extracted from plans or by site inspection.
* Input values for floor constructions listed in Table 4A (#19A -> #19D, #20, #21A->21B or #22A -> #22D) of the unabridged version of Manual J are valid entries.
3) You can enter up to 3 different "over-crawlspace," "over-basement" floors.
* The construction number, U-value, PTDH and PTDC are extracted from Table 4A, Construction 19A.
* For example: Crawlspace floor; HTD =70; CTD = 20, Daily range = Medium
Construction Number; Floor Type; Insulation R-Value; Floor Cover | U-Value | PTDH | PTDC
19A-11p; Crawlspace floor; R11 floor: Any Cover | 0.073 | 49.5 | 14.1
4) You can enter up to 3 different exposed floors.
* The construction number, U-value and CLTD are extracted from Table 4A, Construction 20.
* For example:
Construction Number; Floor Type; Insulation R-Value; Floor Cover | U-Value
20p-30; Exposed floor; R30; Any cover | 0.035
5) You can enter up to 3 different partition floors.
* The construction number and U-value are extracted from Table 4A, Construction 19A.
* Values for PTDH and PTDC are obtained from Table 4C, or by observation and experience.
* For example, bonus room over garage number 2 (see Table 4C) 99% db = 10 ºF & room = 70 °F; 1% drybulb = 95 °F, medium daily range & room = 75 °F
Construction Number, Floor Type; Insulation R-Value; Floor Cover | U-Value | PTDH | PTDC
19A-11p; Partition floor; R11 floor; Any Cover | 0.073 | 65 | 26
6) You can enter up to 3 different basement floors.
* The construction number and U-value and CLTD are extracted from Table 4A, Construction 21.
* For example:
Construction Number, Floor Type; Insulation; R-Value; Slab Width | U-Value
21A-32; Basement floor; R0; 32 feet | 0.02
7) You can enter up to 3 different slab floors.
* The construction number and U-value is extracted from Table 4A, Construction 22.
* For example:
Construction Number, Floor Type; Insulation; R-Value; Soil Type | F-Value
22B-10ph; Slab floor; R10; heavy moist | 0.481
Notes
Construction Attributes for Floor Over a Closed Crawlspace (for MJ8ae Applications)
* A floor over a closed crawlspace or unconditioned basement is a partition floor.
* Use #19A (sealed or vented / leaky; no wall insulation, R0 to R38 floor insulation; carpet, tile or bare floor.
* Temperature difference (PTDH and PTDC) across floor provided by Table 4A, Construction 19A.
* Passive floor (no radiant heat).
Construction Attributes for Partition Floor (for MJ8ae Applications)
* A floor over closed, unconditioned room is a partition floor.
* Use #19A to determine U-Value.
* Use Table 4C to estimate PTDH and PTDC for floor over closed garage.
* Values for PTDH and PTDC may be based on personal observations and experience.
* Passive floor (no radiant heat).
Construction Attributes for Floor Exposed to Outdoor Air (for MJ8ae Applications)
* Floor over an open crawlspace, open garage, carport, wall overhang, etc. is an exposed floor.
* R0 to R38 insulation; tile, vinyl or hardwood floor cover.
* Passive floor (no radiant heat).
Construction Attributes for Basement Floor (for MJ8ae Applications)
* No insulation below floor, any floor cover.
* Passive floor (no radiant heat).
Construction Attributes for Slab Floor (for MJ8ae Applications)
* Uninsulated; or insulation (R5, R10 or R15 ) covers exposed edge and extends straight down (3 feet).
* Uninsulated; or insulation (R5, R10 or R15 ) covers exposed edge and extends straight down (3 feet).
* Three choices of soil conditions.
* Passive floor (no radiant heat).

## Help
Help Section
Microsoft Excel® version 2000 and later is recommended to take full advantage of display objects and color schemes.
A screen resolution of 1024 x 768 pixels is recommended to take full advantage of display screen formats.
This electronic workbook (template) provides automatic calculation of the MJ8ae procedures and supports all MJ8ae sensitivities and capabilities.
Scrutinize the Read Me tab before using the MJ8ae workbook.
Prepare One or More Workbook Templates for Local Use
Preserve the integrity of the original CD file. Make a folder on your hard drive named C:\MJ8. Copy the blank Microsoft Excel® workbook from the CD to the folder. Open the C:\MJ8 folder and open the blank workbook and "save as," using a unique filename (Nashville-Replacements, for example). Then click on the J1 Form tab and follow these instructions:
| 1) | The Header portion of the J1 Form tab (top left corner) must be populated with design conditions for your geographical region.
● Project: Leave blank for now (you are making a template for "Nashville-Replacements" work).
● Location: Enter the design city and state
● Indoor design heating default is 70 degrees dry bulb (mandatory default, unless code specifies different value)
● Indoor design cooling default is 75 degrees dry bulb (mandatory default, unless code specifies different value)
● Indoor design cooling default is 50% relative humidity
* Default value = 50% (applies to most climates that produce a latent gain).
* Dry climate option = 45% (Table 1A grains-difference value at 50% RH is zero or negative; or cooling coil is dry for most of the cooling season.)
* Humid-climate option = 55% (Climate has oppressive humidity; Manual S procedure shows the equipment does not have enough latent capacity for a 50% RH design value.)
Refer to Manual J8ae and enter the following information for the design location.
Enter values from Table 1A -- exactly -- unless code or regulation specifies a different value.
● Latitude
● Outdoor design 99% db
● Outdoor design 1% db
● Grains Difference (for the selected indoor RH value)
● Elevation
● Daily Range
Note: Create at least one template for each city in your local service area (design conditions and code requirements may differ).
| 2) | The Glass, Doors, Walls, Ceilings and Floors tabs (surface tabs) must be populated with information that applies to the typical construction practices
for the subject template (the "Nashville-Replacements" template, in this case).
● Detailed population instructions and helpful notes are provided with each surface tab (you may need to scroll down to see them).
Note: Ignore the Glass Sched tab for now.
● Tab input for construction detail should be "typical" for the application covered by the template.
For example, population choices for the "Nashville-Replacements" template would be representative of older Nashville homes.
● Create additional templates for other applications ("Nashville New Homes" or "Nashville E-Star Homes," for example).
Note: If the same construction applies to more than one city, populate the surface tabs first; then name and save the file; then populate the J1 Form design conditions for the
city; then rename (for the city and application) and save the file again.
● A template is your personal version of the MJ8ae tables and can be edited at any time (add items, delete items or correct input errors).
● Editing population input during any stage of an actual load calculation may change the heat loss and heat estimates for the problem at hand.
● Make sure that work in progress edits produce the desired result.
Using the Workbook to Calculate Loads for a Dwelling
Once the template is loaded (J1 Form header and the surface tabs are complete), the load estimate is performed with the Glass Schedule and J1 Form tabs. These tabs have color-coded cells. The white and yellow cells are used for input. The other cells contain information or provide output.
● Yellow cells are user lookup cells (click on the cell, then click on the the pull-down menu, then select an item).
● White cells require user input (type input values directly into the cell).
● Green cells contain text cells (row and column headings, etc.) that are locked (not accessible to user).
● Blue cells are output (formula) cells that are locked (not accessible to the user).
● Orange cells hold subtotals or totals for heat loss and heat gain (locked and not accessible to user).
| 1) | Obtain load area information (dimensions) from the plans or from site survey notes.
From this point, the load estimate is accomplished in about 10 minutes (for a block load) to about 20 minutes (for room-by-room loads).
| 2) | Use the yellow pull down menus on the Glass Sched tab to select the windows, glass doors and skylights for the dwelling.
| 3) | On the Glass Sched tab, enter values for the rough opening (W and H) and the overhang dimensions (X and Y) in the white cells.
Note: These choices and areas are automatically transcribed to the Form J1 tab.
| 3) | Move to the J1 Form tab; enter values in the white cells and select yellow-cell options.
● For a block load, enter block surface area values in the first room column and leave the other room columns blank.
● For room loads and the associated block load, use one column for each room and enter the appropriate surface area values in each room column.
● Use the "save as" command and a project name ("Jones Residence," for example).
Note: The blank version of the "Nashville-Replacement" template is preserved and ready for the next project.
Itemized Instructions for Populating the Form J1 Tab
| 1 | Enter the job name in the project cell (J1 Form tab), verify location and design conditions; then save the file with the project name.
| 2 | Use the pull down menus to select Doors ( J1 Form tab, line 7).
| 3 | Use the pull down menus to select Above Grade Walls and Partitions ( J1 Form tab, line 8).
1 | 4 | Use the pull down menus to select Below Grade Walls (J1 Form tab, line 9).
2 | 5 | Use the pull down menus to select Ceilings (J1 Form , line 10).
3 | 6 | Use the pull down menus to select Floors (J1 Form tab, line 11).
4 | 7 | Use the pull down menus and white cells for Infiltration (J1 Form tab, line 12).
5 | 8 | Use the pull down menus and white cells for Internal Gain (Form J1 tab, line 13).
6 | 9 | Use the pull down menus and white cells for Duct Loss and Duct Gain (J1 Form tab, line 15).
* Use the check boxes (in the blue cells) to activate a duct load for heating and/or a duct load for cooling (there is no duct load if the box is not checked).
* Enter the square feet of exposed (to unconditioned space) duct surface area for the supply- and return-sides of the duct system (or enter 1 for the default values).
Note: Failure to enter a surface area or a 1 results in a zero duct load for that side of the system (make sure the supply and return area inputs are correct).
7 | 10 | Use the pull down menus and white cells for Ventilation (J1 Form tab, line 16).
* Only click on the check boxes if the furnace and/or water heater draw combustion air from the conditioned space.
Note: Respond to the check boxes before using the yellow pull down menu to select a Table 8A Cfm option.
* Look at the value in the blue ventilation Cfm cell. This is the value for the suggested outdoor air Cfm (see Section 3-13 in the MJ8ae book).
* Use the yellow pull down menu to select the one of the four ventilation Cfm options.
8 | 11 | Use the pull down menu to toggle the Blower Heat Gain on or off (J1 Form tab, line 19).
9 | 12 | Use the white cells to account for the latent load produced by small, medium and large plants (J1 Form tab, line 21).
10 | 13 | Elect to do a room calculation (for equipment selection and duct system design) or a block calculation (for equipment selection only):
11 | 14 | Enter the rough opening areas for windows, glass doors and skylights (white cells, lines 6A and 6B).
Note: For block load only, copy the blue-cell values to the white cells in the room-1 column; or enter values for each room.
Note: Make sure the load area input line matches the correct construction detail line.
| 15 | Enter the load areas (net or gross) for surfaces (white cells, Lines 7 through 11).
Note: Make sure the load area input line matches the correct construction detail line.
| 16 | Enter internal gain (occupants & appliances) values for the room or zone (white cells, line 13).
* Assign occupants to selected rooms (total occupancy for all rooms shall not exceed number of bedrooms plus one).
* Assign appliance loads (Btuh) to the rooms (none to as much as 1,200 Btuh -- see MJ8ae Table 6A for distribution rules.).
| 17 | Use the Excel save option to save your work.
| 18 | Scrutinize the Summary Report (Page 2 of J1 Form tab) and make sure that the values are reasonable and plausible.
| 19 | Note: Example problem solutions in the MJ8ae book (for the Vatilo, Victor and Long problems) are slightly different than the solutions provided
by the book.
| 20 | CD solutions for infiltration loads and duct loads use exact interpolations (automatically performed by the MJ8ae spreadsheet).
Book solutions use ballpark interpolations.
| 21 | CD solutions for ventilation loads uses one of the ventilation Cfm options (selection item on From J1).
Book solutions may use a slightly different input for ventilation CFM.
♦ J1 Form Tab
All other design data cells are calculated automatically from the Design Tab
♦ Glass Schedule Tab
► Lookup construction type of glass heating from user populated Glass table
► Lookup construction type of glass cooling from user populated Glass table
► Lookup direction glass faces
Overhang Adjustment
● Enter width of the glass opening
● Enter overhang distance
● Enter distance from top of glass opening to overhang
● Enter height of the glass opening
► Lookup HTM adjustment (bay window, garden window or French door)
► Lookup cooling HTM adjustment (bug screen)
♦ J1 Form Tab (continued)
● Enter the room or zone name
♦ Windows, Glass Doors & Skylights
Windows & Glass Door construction types are automatic from the Glass Schedule Lookups
Skylight construction types are automatic from the Glass Schedule Lookups
Enter the net glass area for the construction type and direction
♦ Wood & Metal Doors
► Lookup construction type of doors from user populated Doors table
● Enter net square feet of exposed doors
♦ Above Grade Walls
► Lookup construction type of above grade walls from user populated Walls table
● Enter net square feet of exposed above grade walls
♦ Partition Walls
► Lookup construction type of partition walls from user populated Walls table
● Enter net square feet of partition walls
♦ Below Grade Walls
► Lookup construction type of below grade walls from user populated Walls table
● Enter net square feet of exposed below grade walls
♦ Ceilings
► Lookup construction type of exposed ceilings from user populated Ceilings table
● Enter net square feet of exposed ceilings
♦ Partition Ceilings
► Lookup construction type of partition ceilings from user populated Ceilings table
● Enter net square feet of partition ceilings
♦ Floors
► Lookup construction type of exposed floors from user populated Floors table
● Enter net square feet of exposed floors
♦ Slab On Grade Floors
► Lookup construction type of slab on grade floors from user populated Floors table
● Enter linear feet of exposed slab on grade
♦ Partition Floors
► Lookup construction type of partition floors from user populated Floors table
● Enter net square feet of partition floors
♦ Infiltration
► Lookup envelope leakage class
► Lookup number of fireplaces
● Enter the heated floor area (square feet) and above grade area (cubic feet)
● Enter the cooled floor area (square feet) and above grade area (cubic feet)
♦ Internal Gains
► Lookup number of occupants
► Lookup appliance class
♦ Duct Loss & Gain
► Lookup type of duct system / location
► Lookup duct insulation R-value
► Lookup duct leakage class
● Enter the installed Supply Duct Surface Area or Enter 1 for the Default
● Enter the installed Return Duct Surface Area or Enter 1 for the Default
♦ Ventilation
● Enter design CFM for mechanical ventilation
♦ Blower Heat Gain
► Lookup blower heat
♦ Latent Load for Plants
● Enter the quantity and size of plants

## What to do next
What To Do Next
1. | After obtaining a spreadsheet solution, scrutinize the load summary and make sure the solution and its component values are realistic (instructions for evaluating the out put of the MJ8AE procedure is provided by Section 10 of MJ8AE).
2. | Use Manual S and manufacturer’s applied performance data to size equipment.
3. | Use Manual T and manufacturer’s performance data to select and size air distribution devices.
4. | Use Manual D and the ACCA duct slide rule to design the duct system and to size airways.
5. | Refer to the ACCA website for a comprehensive discussion of testing and balancing procedures. www.acca.org
6. | Comply with applicable codes, standards and regulations.
7. | Use industry-certified methods and materials.

## Notes
Release Notes:
Version MJ8ae 1.00 14FEB05 | Initial Release
Version MJ8ae 1.01 28APR05 | Fixed Bug in Glass Schedule
Version MJ8ae 1.02 06JUL05 | Fixed Formatting Issues
Version MJ8ae 1.03 10SEP05 | Added Home Tab (Introduction and General Information
Added Print Option Buttons to J1 Form
Added Release Notes Tab
Version MJ8ae 1.04 05DEC05 | Fixed Bug in Glass Schedule
Version MJ8ae 1.05 17JAN06 | Fixed Bug in Ducts with Greater than 100 Degree Outdoor Design Temperatures
Fixed Bug for Cooling Design Temperature Difference Less Than 10 Degrees
Corrected Ceiling Example
Version MJ8ae 1.06 30JAN06 | Fixed Bug in Ducts with Sq. Ft. Greater than 3000
Version MJ8ae 1.07 27MAR06 | Fixed Bug in Daily Range Calculation Table
Revised Summary Report to New Tab
Added Room CFM Calculation to New Summary Report
Removed Macros
Version MJ8ae 1.08 24APR06 | Fixed Bug in Floors Over Open Areas
Version MJ8ae 1.09 16MAY06 | Fixed Partition Ceiling Drop Down Lookup
Fixed Bug in Infiltration
Version MJ8ae 1.10 19SEP06 | Fixed Cell Protection Errors in Glass Schedule
Version MJ8ae 1.11 17OCT06 | Fixed Error in Latent Load for Ducts with Design Grains Equal to or Greater than 60
Added Manual D CFM Column to Summary Tab
Added New Duct Scenario Table 7E
Version MJ8ae 1.12 31OCT06 | Fixed Error in Shaded Wall Calculation
Version MJ8ae 1.13 29NOV06 | Fixed Error in line 11C on J1 Form
Fixed Latent Calculations for Negative Design Grains
Version MJ8ae 1.14 30NOV06 | Fixed Calculations for Summer Design Conditions Less than 85 Degrees
Version MJ8ae 1.15 05MAR07 | Fixed errors and ommissions on Summary Tab
Version MJ8ae 1.16 02MAY07 | Changed Formula to Allow Zero Bedrooms
Corrected Adjustment Calculation for Projected Windows and French Doors
Eliminated Glass Width Entry for HTM Average Calculation
Added Support for Latitude of 50 Degrees
Cosmetic Changes
Version MJ8ae 1.17 11AUG08 | Added automated design conditions lookup from selected state & city.
Version MJ8ae 1.18 23MAY11 | Fixed rounding issue on design conditions

## Infil (hidden)
Envelope | Row | 3 | 3 |  | 1 | 2 | 3 | 4 | 5 |  | Worksheet E: Infiltration | [11 empty] | Worksheet H: Engineered Ventilation
Envelope | Col | #N/A | 1 |  | 900 | 1500 | 2000 | 3000 | 3001 | FP CFM | Design Values |  | Heating | Cooling |  | Occupants | Number | Burner | HTD | CTD | T1 Grains | ACF | Design Values |  |  | Heating | Cooling | HTD | CTD | T1 Grains | ACF
Fireplace | Row | 0 |  | 1 | 0.21 | 0.16 | 0.14 | 0.11 | 0.1 | 0 |  | Floor area | 0 | 0 |  | (# BR + 1) | Fireplaces | Btuh | #N/A | #N/A | #N/A | #N/A |  |  | Above grade volume | 0 | 0 | #N/A | #N/A | #N/A | #N/A
Fireplace | Col | 7 |  | 2 | 0.41 | 0.31 | 0.26 | 0.22 | 0.19 | 13 |  | Conditioned above grade volume | 0 | 0 |  | 4 | 0 | 0 | Note: Burner Btuh = 0 for direct-vent appliance
Tight | 1 |  |  | 3 | 0.61 | 0.45 | 0.38 | 0.32 | 0.28 | 20 | Table 8 Outdoor Air Requirement | [6 empty] | 0 |  |  | Heating | Cooling | Code Value for Outdoor Cfm
Semi-Tight | 2 |  |  | 4 | 0.95 | 0.7 | 0.59 | 0.49 | 0.43 | 27 | Outdoor air Cfm for 0.35 ACH requirement: | [6 empty] | 0 |  | 0.35 x above grade volume / 60 = | 0 | 0 |  |  | ACH per local code = | 0 |  |  | or Cfm required by local code = | 0
Average | 3 |  |  | 5 | 1.29 | 0.94 | 0.8 | 0.66 | 0.58 | 33 | Outdoor air Cfm for occupants: | [8 empty] | 20 x number of occupants = | 80 |  |  |  | Largest above grade volume = | 0
Semi-Loose | 4 |  |  | 1 | 0.11 | 0.08 | 0.07 | 0.06 | 0.05 | 0 | Outdoor air Cfm for burners that take combustion air from conditioned space: | [8 empty] | 0.50 x input capacity (Btuh) / 1000 = | 0 |  |  |  | Outdoor air Cfm for code ACH value = | 0 | < ACH (line 1) x volume (line 2) / 60
Loose | 5 |  |  | 2 | 0.22 | 0.16 | 0.14 | 0.11 | 0.1 | 0 | Suggest value for fresh air Cfm: | [8 empty] | Maximum value from lines 1, 2 or 3 = | 80 |  |  |  | Code value for outdoor air Cfm = | 0 | < Largest Cfm value from line 1 or 3
|  |  |  | 3 | 0.32 | 0.23 | 0.2 | 0.16 | 0.15 | 0 | Envelope Infiltration Rate | [12 empty] | Code Cfm can be provided by a combination of infiltration and engineered ventilation (yes/no)
0 | 0 |  |  | 4 | 0.5 | 0.36 | 0.31 | 0.25 | 0.23 | 0 | Tightness of construction: |  |  |  | Envelope = | Average |  | Cfm for 1 Fireplace = | 20 |  |  |  | y | Code Cfm shall be provided by engineered ventilation (yes/no)
1 | 1 |  |  | 5 | 0.67 | 0.49 | 0.42 | 0.34 | 0.3 | 0 | Table 5A ACH for heating |  |  |  | Envelope ACH (heating) = | 0.61 |  | Cfm for all fireplaces = | 0 |  |  |  | Smallest infiltration Cfm value (see lines 8 & 9 Worksheet E) = |  |  |  |  | 0
2 | 2 | [9 empty] | Table 5A ACH for cooling |  |  |  | Envelope ACH (cooling) = | 0.32 |  |  |  |  | Heating | Cooling | Code Cfm requirement |  | 0 | < If line 5 = yes; Cfm = line 4 - line 7) or if line 6 = yes (Cfm = line 4 value)
3+ | 3 | [9 empty] | Infiltration Cfm for heating: | [8 empty] | Line 6 ACH x above grade volume for heating / 60 + Line 6 fireplace Cfm x number of fireplaces = | 0
[11 empty] | Infiltration Cfm for cooling: | [8 empty] | Line 7 ACH x above grade volume for cooling / 60 = |  | 0 | Design Value for Engineered Ventilation Cfm
Sq. Ft. | Col | [9 empty] | Infiltration load for heating (Btuh): |  |  | To J1ae > | #N/A | < 1.1 x ACF x Line 8 Cfm x HTD | [9 empty] | Suggested ventilation Cfm (line 14 Worksheet E) = | 80
0 | 1 | [9 empty] | Sensible infiltration load for cooling (Btuh): |  |  | To J1ae > | #N/A | < 1.1 x ACF x Line 9 Cfm x CTD | [6 empty] | Design value for ventilation Cfm = |  |  | 0 | To J1ae | < See Section 3-13, Manual MJ8ae
901 | 2 | [9 empty] | Latent infiltration load for cooling (Btuh): |  |  | To J1ae> | #N/A | < 0.68 x ACF x Line 9 Cfm x Grains | [6 empty] | Note 1: Code Cfm value is a mandatory minimum. The system designer may chose to use a larger value.
1501 | 3 | [9 empty] | Suggested Value for Engineered Ventilation Cfm | [11 empty] | Note 2: Use the unabridged version of Manual J if the design Cfm value exceeds 50 Cfm.
2001 | 4 | [9 empty] | Compare infiltration rate with suggested fresh air rate: | [5 empty] | Line 4 Cfm - line 8 Cfm for heating = | 80 |  |  | Line 4 Cfm - line 9 Cfm for cooling = | 80 | Note 2: Use the unabridged version of Manual J if the design features heat recovery equipment.
3001 | 5 | [9 empty] | Suggest value for engineered ventilation Cfm: |  |  | 80 | < Largest positive value from line 13 (see line 11, Worksheet H)
Ventilation Loads
[13 empty] | None | 0 | [8 empty] | Ventilation load for heating (Btuh): |  |  |  | To J1ae > | 0 | < 1.1 x ACF x Line 10 Cfm x HTD
[13 empty] | Table 8A CFM | 80 | [8 empty] | Sensible ventilation load for cooling (Btuh): |  |  |  | To J1ae > | 0 | < 1.1 x ACF x Line 10 Cfm x CTD
[13 empty] | 25 CFM | 25 | [8 empty] | Latent ventilation load for cooling (Btuh): |  |  |  | To J1ae > | 0 | < 0.68 x ACF x Line 10 Cfm x Grains
[13 empty] | 50 Cfm (Max. for MJ8ae) | 50

## Ducts (hidden)
Duct System Type |  |  | Col | [6 empty] | LCF | LCF | LCF | [16 empty] | Worksheet G: Duct Runs in Unconditioned Space
7A-Radial or Spider SA & RA in Attic |  |  | 1 | Type | Htg | Clg | Lat | Ks | Kr | HTG | CLG | Latent | Ks | Kr | [14 empty] | 99% db | 1% db | Grains | Conditioned Floor Area (Sq. Ft.) | Heating | 0 | Base Case Heat Loss Factor (BHLF) | [5 empty] | Smaller Floor Area Value > |  |  |  |  | 1000
7B-Radial or Spider SA in Attic & RA Thru Closet Door |  |  | 2 | 1 | 1 | 1 | 1 | 0.771 | 0.229 | 1 | 1 | 1 | 0.829 | 0.171 | [14 empty] | #N/A | #N/A | #N/A |  | Cooling | 0 | 7E-T&B SA in Attic, RA Riser in Floor to Ceiling Chase, Perimeter Supply Outlets | [5 empty] | 1000 | 0 | 0 | 0 | 0
7C-T&B SA in Attic, RA Riser in Floor to Ceiling Chase, Center Supply outlets |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 0 | [19 empty] | 7E-T&B SA in Attic, RA Riser in Floor to Ceiling Chase, Perimeter Supply Outlets |  |  |  | Heat loss factor = | #N/A |  | Square Feet of Floor Area
7D-T&B SA, RA in Closed Crawlspace or Unconditioned Basement |  |  | 4 | 3 | 1 | 1 | 1 | 0.969 | 0.031 | [23 empty] | Sensible gain factor = | #N/A | OAT | 1000 | 1500 | 2000 | 2500 | 3000 | Smaller OAT Value > | [5 empty] | #N/A
7E-T&B SA in Attic, RA Riser in Floor to Ceiling Chase, Perimeter Supply Outlets |  |  | 5 | 4 | 1 | 1 | 1 | 0.79 | 0.21 | [23 empty] | Latent gain (Btuh) = | #N/A | -10 | 0.233 | 0.278 | 0.325 | 0.357 | 0.411
7F-Ducts in Conditioned Space |  |  | 6 | 5 | 1 | 1 | 1 | 0.829 | 0.171 | [19 empty] | R-Value = 6 |  |  |  | For heat loss = | 1 | 0 | 0.21 | 0.244 | 0.294 | 0.325 | 0.365
|  |  | 5 | [29 empty] | For sensible gain = | 1 | 10 | 0.197 | 0.224 | 0.262 | 0.294 | 0.318 | Look Up Engine # 1 |  |  | Interp | Look Up Engine # 2 |  |  | #N/A
R-Value Correction Factor | Htg | Sens | Col | Table |  |  | 1000 | 1500 | 2000 | 2500 | 3000 |  | RVC | Htg | Sens |  | R2 | R4 | R6 | R8 | Ks | Kr |  | 1000 | 1500 | 2000 | 2500 | 3000 | Adjusted heat loss factor = |  |  |  |  | #N/A | 20 | 0.182 | 0.203 | 0.231 | 0.251 | 0.285 | Area | Oat | Value | Value | Area | Oat | Value | 500
R-Value = 2 | 2.17 | 1.99 | 1 | 7A | -10 | 1 | 0.117 | 0.134 | 0.164 | 0.169 | 0.186 |  | R2 | 2.04 | 2.24 | Leakage Class .06/.06 | 0.88 | 0.82 | 0.76 | 0.74 | 0.811 | 0.189 | 10 | 77 | 126 | 172 | 217 | 261 | Adjusted sensible gain factor = |  |  |  |  | #N/A | 30 | 0.158 | 0.184 | 0.2 | 0.235 | 0.253 | 1000 | #N/A | #N/A | #N/A | 1500 | #N/A | #N/A | #N/A | #N/A
R-Value = 4 | 1.31 | 1.24 | 2 |  | 0 | 2 | 0.104 | 0.121 | 0.144 | 0.159 | 0.17 |  | R4 | 1.39 | 1.37 | Leakage Class .09/.15 | 0.94 | 0.91 | 0.87 | 0.88 | 0.788 | 0.212 | 20 | 113 | 185 | 251 | 317 | 382 | Leakage Class .12/.24 |  |  |  | For heat loss = | 1 | 40 | 0.135 | 0.161 | 0.188 | 0.207 | 0.223 | [7 empty] | #N/A | #N/A
R-Value = 6 | 1 | 1 | 3 |  | 10 | 3 | 0.092 | 0.111 | 0.122 | 0.13 | 0.149 |  | R6 | 1 | 1 | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 0.771 | 0.229 | 30 | 150 | 246 | 334 | 422 | 507 |  |  |  |  | For sensible gain = | 1 | [6 empty] | Look Up Engine # 3 |  |  | Interp | Look Up Engine # 4 |  |  | #N/A | #N/A
R-Value = 8 | 0.86 | 0.88 | 4 |  | 20 | 4 | 0.083 | 0.1 | 0.113 | 0.126 | 0.135 |  | R8 | 0.86 | 0.86 | Leakage Class .24/.47 | 1.26 | 1.37 | 1.43 | 1.53 | 0.752 | 0.248 | 40 | 189 | 309 | 419 | 530 | 637 |  |  |  |  | For latent gain = | 1 | [6 empty] | Area | Oat | Value | Value | Area | Oat | Value | 500 | #N/A
| 1 | 1 | 3 |  | 30 | 5 | 0.071 | 0.085 | 0.09 | 0.104 | 0.118 |  |  |  |  | Leakage Class .35/.70 | 1.65 | 1.8 | 1.97 | 2.19 | 0.743 | 0.257 | 50 | 229 | 374 | 507 | 641 | 772 |  |  |  |  | Adjusted heat loss factor = | #N/A | BHLF = | #N/A | SqFt = | 0 | OAT = | #N/A | 1000 | #N/A | #N/A | #N/A | 1500 | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40 | 6 | 0.069 | 0.07 | 0.082 | 0.09 | 0.099 | [9 empty] | LCF Latent |  | 60 | 270 | 441 | 599 | 757 | 911 |  |  |  |  | Adjusted sensible gain factor = | #N/A | [13 empty] | #N/A
[16 empty] | Leakage Class .06/.06 | 0.85 | 0.79 | 0.73 | 0.73 | 0.3 |  | 70 | 312 | 511 | 694 | 867 | 1055 |  |  |  |  | Adjusted latent gain (Btuh) = | #N/A | Base Case Heat Loss Factor (BSFG) | [5 empty] | Smaller Floor Area Value > |  |  |  |  | 1000
[5 empty] | 0 | 1 | 0.109 | 0.131 | 0.154 | 0.17 | 0.189 |  |  |  |  | Leakage Class .09/.15 | 0.94 | 0.89 | 0.86 | 0.85 | 0.64 | [11 empty] | Installed supply area (SqFt) = | 1 | 7E-T&B SA in Attic, RA Riser in Floor to Ceiling Chase, Perimeter Supply Outlets | [5 empty] | 1000 | 0 | 0 | 0 | 0
[5 empty] | 85 | 2 | 0.11 | 0.139 | 0.151 | 0.175 | 0.19 |  |  |  |  | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 1 |  | Default Duct Wall Surface Area | [9 empty] | Default supply area (SqFt) = | 1 |  | Square Feet of Floor Area
[5 empty] | 90 | 3 | 0.124 | 0.149 | 0.162 | 0.176 | 0.211 |  |  |  |  | Leakage Class .24/.47 | 1.29 | 1.39 | 1.58 | 1.67 | 2.58 |  | SA | 109 | 177 | 229 | 287 | 330 |  |  |  |  | Rs = Installed area / default area = | 1 | OAT | 1000 | 1500 | 2000 | 2500 | 3000 | Smaller OAT Value > | [5 empty] | #N/A
[5 empty] | 96 | 4 | 0.126 | 0.154 | 0.172 | 0.189 | 0.205 |  |  |  |  | Leakage Class .35/.70 | 1.6 | 1.83 | 2.11 | 2.34 | 4.42 |  | RA | 32 | 43 | 51 | 58 | 64 |  |  |  |  | Installed return area (SqFt) = | 1 | 85 | 0.211 | 0.262 | 0.314 | 0.333 | 0.366
[5 empty] | 100 | 5 | 0.136 | 0.159 | 0.175 | 0.211 | 0.241 | [21 empty] | Default return area (SqFt) = | 1 | 90 | 0.227 | 0.266 | 0.3 | 0.344 | 0.376
|  |  |  | Table |  |  | 1000 | 1500 | 2000 | 2500 | 3000 |  | RVC | Htg | Sens |  | R2 | R4 | R6 | R8 | Ks | Kr |  | 1000 | 1500 | 2000 | 2500 | 3000 |  |  |  |  | Rr = Installed area / default area = | 1 | 95 | 0.246 | 0.275 | 0.319 | 0.344 | 0.394 | Look Up Engine # 1 |  |  | Interp | Look Up Engine # 2
|  |  |  | 7B | -10 | 1 | 0.08 | 0.1 | 0.13 | 0.14 | 0.16 |  | R2 | 2.19 | 2.19 | Leakage Class .06/.06 | 0.92 | 0.84 | 0.84 | 0.84 | 1 | 0 | 10 | 51 | 89 | 136 | 186 | 231 |  |  |  |  | Kr = | 0.171 | 100 | 0.247 | 0.285 | 0.325 | 0.364 | 0.414 | Area | Oat | Value | Value | Area | Oat | Value
[5 empty] | 0 | 2 | 0.07 | 0.09 | 0.106 | 0.12 | 0.15 |  | R4 | 1.45 | 1.31 | Leakage Class .09/.15 | 0.94 | 0.93 | 0.89 | 0.9 | 1 | 0 | 20 | 68 | 119 | 183 | 250 | 310 |  |  |  |  | Ks = | 0.829 | 105 | 0.252 | 0.297 | 0.349 | 0.385 | 0.421 | 1000 | #N/A | #N/A | #N/A | 1500 | #N/A | #N/A
[5 empty] | 10 | 3 | 0.07 | 0.08 | 0.1 | 0.1 | 0.12 |  | R6 | 1 | 1 | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 1 | 0 | 30 | 86 | 151 | 231 | 316 | 392 |  |  |  |  | SAA (heating and sensible cooling) = | 1
[5 empty] | 20 | 4 | 0.06 | 0.08 | 0.09 | 0.1 | 0.11 |  | R8 | 0.84 | 0.83 | Leakage Class .24/.47 | 1.39 | 1.55 | 1.66 | 1.84 | 1 | 0 | 40 | 105 | 184 | 282 | 385 | 478 |  |  |  |  | LGA (latent cooling) = | 1 | [6 empty] | Look Up Engine # 3 |  |  | Interp | Look Up Engine # 4
[5 empty] | 30 | 5 | 0.06 | 0.07 | 0.07 | 0.08 | 0.1 |  |  |  |  | Leakage Class .35/.70 | 1.87 | 2.21 | 2.5 | 2.79 | 1 | 0 | 50 | 124 | 218 | 334 | 457 | 567 |  |  |  |  | Net heat loss factor = | #N/A | BSFG = | #N/A | SqFt = | 0 | OAT = | #N/A | Area | Oat | Value | Value | Area | Oat | Value
[5 empty] | 40 | 6 | 0.05 | 0.06 | 0.07 | 0.08 | 0.08 | [9 empty] | LCF Latent |  | 60 | 145 | 254 | 388 | 531 | 659 |  |  |  |  | Net sensible gain factor = | #N/A | [6 empty] | 1000 | #N/A | #N/A | #N/A | 1500 | #N/A | #N/A
[16 empty] | Leakage Class .06/.06 | 0.9 | 0.88 | 0.85 | 0.84 | 0.27 |  | 70 | 166 | 290 | 445 | 608 | 754 |  |  |  |  | Net latent gain (Btuh) = | #N/A
[5 empty] | 0 | 1 | 0.07 | 0.09 | 0.11 | 0.12 | 0.13 |  |  |  |  | Leakage Class .09/.15 | 0.96 | 0.93 | 0.91 | 0.91 | 0.57 | [13 empty] | Base Case Heat Loss Factor (BLG) | [5 empty] | Smaller Floor Area Value > |  |  |  |  | 1000
[5 empty] | 85 | 2 | 0.08 | 0.09 | 0.11 | 0.13 | 0.14 |  |  |  |  | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 1 |  | Default Duct Wall Surface Area | [11 empty] | 7E-T&B SA in Attic, RA Riser in Floor to Ceiling Chase, Perimeter Supply Outlets | [5 empty] | 1000 | 0 | 0 | 0 | 0
[5 empty] | 90 | 3 | 0.08 | 0.1 | 0.118 | 0.13 | 0.14 |  |  |  |  | Leakage Class .24/.47 | 1.21 | 1.35 | 1.51 | 1.47 | 3.42 |  | SA | 107 | 174 | 229 | 277 | 315 | [7 empty] | Square Feet of Floor Area
[5 empty] | 95 | 4 | 0.09 | 0.13 | 0.13 | 0.14 | 0.16 |  |  |  |  | Leakage Class .35/.70 | 1.51 | 1.8 | 1.96 | 2.09 | 6.35 |  | RA | 0 | 0 | 0 | 0 | 0 | [6 empty] | Grains | 1000 | 1500 | 2000 | 2500 | 3000 | Smaller Grains Value > | [6 empty] | #N/A
[5 empty] | 100 | 5 | 1 | 0.13 | 0.13 | 0.15 | 0.17 | [23 empty] | 10 | 188 | 286 | 384 | 478 | 544 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | Table |  |  | 1000 | 1500 | 2000 | 2500 | 3000 |  | RVC | Htg | Sens |  | R2 | R4 | R6 | R8 | Ks | Kr |  | 1000 | 1500 | 2000 | 2500 | 3000 | [6 empty] | 20 | 277 | 420 | 564 | 702 | 800
|  |  |  | 7C | -10 | 1 | 0.138 | 0.157 | 0.176 | 0.195 | 0.217 |  | R2 | 2.02 | 2.19 | Leakage Class .06/.06 | 0.87 | 0.83 | 0.78 | 0.75 | 0.975 | 0.025 | 10 | 111 | 166 | 214 | 264 | 297 | [6 empty] | 30 | 370 | 562 | 754 | 938 | 1069 | Look Up Engine # 1 |  |  | Interp | Look Up Engine # 2
[5 empty] | 0 | 2 | 0.131 | 0.145 | 0.164 | 0.184 | 0.199 |  | R4 | 1.28 | 1.3 | Leakage Class .09/.15 | 0.92 | 0.89 | 0.86 | 0.86 | 0.972 | 0.028 | 20 | 157 | 234 | 303 | 373 | 420 | [6 empty] | 40 | 468 | 711 | 954 | 1187 | 1353 | Area | Oat | Value | Value | Area | Oat | Value
[5 empty] | 10 | 3 | 0.118 | 0.133 | 0.148 | 0.166 | 0.188 |  | R6 | 1 | 1 | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 0.969 | 0.031 | 30 | 205 | 306 | 395 | 487 | 549 | [6 empty] | 50 | 571 | 867 | 1165 | 1448 | 1650 | 1000 | #N/A | #N/A | #N/A | 1500 | #N/A | #N/A
[5 empty] | 20 | 4 | 0.111 | 0.122 | 0.138 | 0.15 | 0.17 |  | R8 | 0.84 | 0.8 | Leakage Class .24/.47 | 1.4 | 1.56 | 1.68 | 1.81 | 0.965 | 0.035 | 40 | 255 | 380 | 492 | 606 | 683 | [6 empty] | 60 | 679 | 1031 | 1385 | 1723 | 1963
[5 empty] | 30 | 5 | 0.096 | 0.119 | 0.129 | 0.141 | 0.153 |  |  |  |  | Leakage Class .35/.70 | 1.84 | 2.21 | 2.47 | 2.76 | 0.962 | 0.038 | 50 | 307 | 458 | 592 | 730 | 823 | [6 empty] | 70 | 793 | 1204 | 1617 | 2011 | 2291 | Look Up Engine # 3 |  |  | Interp | Look Up Engine # 4
[5 empty] | 40 | 6 | 0.085 | 0.103 | 0.12 | 0.135 | 0.148 | [9 empty] | LCF Latent |  | 60 | 361 | 539 | 697 | 859 | 968 | [12 empty] | Area | Oat | Value | Value | Area | Oat | Value
[16 empty] | Leakage Class .06/.06 | 0.9 | 0.85 | 0.8 | 0.81 | 0.28 |  | 70 | 417 | 624 | 806 | 994 | 1119 | [12 empty] | 1000 | #N/A | #N/A | #N/A | 1500 | 30 | 562
[5 empty] | 0 | 1 | 0.137 | 0.17 | 0.2 | 0.22 | 0.24 |  |  |  |  | Leakage Class .09/.15 | 0.95 | 0.91 | 0.9 | 0.91 | 0.62 | [13 empty] | BLG = | #N/A | SqFt = | 0 | Grains | #N/A
[5 empty] | 85 | 2 | 0.146 | 0.161 | 0.203 | 0.22 | 0.24 |  |  |  |  | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 1 |  | Default Duct Wall Surface Area
[5 empty] | 90 | 3 | 0.157 | 0.175 | 0.203 | 0.22 | 0.24 |  |  |  |  | Leakage Class .24/.47 | 1.26 | 1.35 | 1.42 | 1.56 | 2.81 |  | SA | 189 | 276 | 361 | 431 | 481 | [6 empty] | Default Duct Wall Surface Area (SqFt) | [5 empty] | Smaller Floor Area Value > |  |  |  |  | 1000
[5 empty] | 95 | 4 | 0.158 | 0.18 | 0.203 | 0.22 | 0.247 |  |  |  |  | Leakage Class .35/.70 | 1.56 | 1.74 | 1.88 | 2.14 | 4.88 |  | RA | 5 | 7 | 9 | 11 | 12 | [6 empty] | 7E-T&B SA in Attic, RA Riser in Floor to Ceiling Chase, Perimeter Supply Outlets | [5 empty] | 1000 | 0 | 0 | 0 | 0
[5 empty] | 100 | 5 | 0.16 | 0.185 | 0.207 | 0.224 | 0.252 | [24 empty] | Square Feet of Floor Area
|  |  |  | Table |  |  | 1000 | 1500 | 2000 | 2500 | 3000 |  | RVC | Htg | Sens |  | R2 | R4 | R6 | R8 | Ks | Kr |  | 1000 | 1500 | 2000 | 2500 | 3000 | [6 empty] | Grains | 1000 | 1500 | 2000 | 2500 | 3000 | Look Up Engine # 1-SA |  |  | Interp | Look Up Engine # 2-SA
|  |  |  | 7D | -10 | 1 | 0.081 | 0.098 | 0.114 | 0.128 | 0.147 |  | R2 | 1.79 | 1.65 | Leakage Class .06/.06 | 0.76 | 0.71 | 0.66 | 0.6 | 0.846 | 0.154 | 10 | 182 | 270 | 345 | 418 | 466 | [6 empty] | Supply | 308 | 476 | 633 | 773 | 908 | Area |  | Value | Value | Area |  | Value
[5 empty] | 0 | 2 | 0.078 | 0.09 | 0.107 | 0.115 | 0.132 |  | R4 | 1.21 | 1.26 | Leakage Class .09/.15 | 0.86 | 0.84 | 0.82 | 0.79 | 0.81 | 0.19 | 20 | 275 | 408 | 521 | 631 | 703 | [6 empty] | Return | 55 | 82 | 105 | 128 | 147 | 1000 |  | 308 | -28 | 1500 |  | 476
[5 empty] | 10 | 3 | 0.075 | 0.087 | 0.1 | 0.109 | 0.125 |  | R6 | 1 | 1 | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 0.79 | 0.21 | 30 | 372 | 552 | 705 | 854 | 951
[5 empty] | 20 | 4 | 0.071 | 0.081 | 0.093 | 0.102 | 0.112 |  | R8 | 0.88 | 0.91 | Leakage Class .24/.47 | 1.65 | 1.94 | 2.07 | 2.19 | 0.772 | 0.228 | 40 | 473 | 702 | 897 | 1086 | 1210 | [6 empty] | SSA = | -28 |  |  |  |  | Look Up Engine # 1-RA |  |  | Interp | Look Up Engine # 1-RA
[5 empty] | 30 | 5 | 0.066 | 0.08 | 0.086 | 0.096 | 0.106 |  |  |  |  | Leakage Class .35/.70 | 2.52 | 2.99 | 3.31 | 3.57 | 0.764 | 0.236 | 50 | 579 | 859 | 1097 | 1329 | 1480 | [6 empty] | RSA = | 1 | SqFt = | 0 |  |  | Area |  | Value | Value | Area | Oat | Value
[5 empty] | 40 | 6 | 0.061 | 0.074 | 0.085 | 0.093 | 0.105 | [9 empty] | LCF Latent |  | 60 | 689 | 1022 | 1306 | 1581 | 1761 | [12 empty] | 1000 |  | 55 | 1 | 1500 | 30 | 82
[16 empty] | Leakage Class .06/.06 | 0.8 | 0.71 | 0.67 | 0.63 | 0.32 |  | 70 | 803 | 1191 | 1522 | 1843 | 2053
[5 empty] | 0 | 1 | 0.048 | 0.058 | 0.064 | 0.067 | 0.081 |  |  |  |  | Leakage Class .09/.15 | 0.89 | 0.86 | 0.82 | 0.8 | 0.65
[5 empty] | 85 | 2 | 0.049 | 0.059 | 0.067 | 0.068 | 0.081 |  |  |  |  | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 1 |  | Default Duct Wall Surface Area
[5 empty] | 90 | 3 | 0.05 | 0.059 | 0.067 | 0.069 | 0.081 |  |  |  |  | Leakage Class .24/.47 | 1.65 | 1.79 | 1.89 | 1.97 | 2.53 |  | SA | 251 | 374 | 493 | 585 | 649
[5 empty] | 95 | 4 | 0.052 | 0.059 | 0.068 | 0.072 | 0.084 |  |  |  |  | Leakage Class .35/.70 | 2.42 | 2.75 | 2.97 | 3.11 | 4.33 |  | RA | 49 | 69 | 86 | 100 | 111
[5 empty] | 100 | 5 | 0.054 | 0.059 | 0.069 | 0.075 | 0.087
|  |  |  | Table |  |  | 1000 | 1500 | 2000 | 2500 | 3000 |  | RVC | Htg | Sens |  | R2 | R4 | R6 | R8 | Ks | Kr |  | 1000 | 1500 | 2000 | 2500 | 3000
|  |  |  | 7E | -10 | 1 | 0.233 | 0.278 | 0.325 | 0.357 | 0.411 |  | R2 | 2.17 | 1.99 | Leakage Class .06/.06 | 0.81 | 0.75 | 0.72 | 0.69 | 0.855 | 0.145 | 10 | 188 | 286 | 384 | 478 | 544
[5 empty] | 0 | 2 | 0.21 | 0.244 | 0.294 | 0.325 | 0.365 |  | R4 | 1.31 | 1.24 | Leakage Class .09/.15 | 0.9 | 0.87 | 0.84 | 0.62 | 0.842 | 0.158 | 20 | 277 | 420 | 564 | 702 | 800
[5 empty] | 10 | 3 | 0.197 | 0.224 | 0.262 | 0.294 | 0.318 |  | R6 | 1 | 1 | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 0.829 | 0.171 | 30 | 370 | 562 | 754 | 938 | 1069
[5 empty] | 20 | 4 | 0.182 | 0.203 | 0.231 | 0.251 | 0.285 |  | R8 | 0.86 | 0.88 | Leakage Class .24/.47 | 1.53 | 1.66 | 1.82 | 1.91 | 0.818 | 0.182 | 40 | 468 | 711 | 954 | 1187 | 1353
[5 empty] | 30 | 5 | 0.158 | 0.184 | 0.2 | 0.235 | 0.253 |  |  |  |  | Leakage Class .35/.70 | 2.25 | 2.55 | 2.85 | 3.11 | 0.81 | 0.19 | 50 | 571 | 867 | 1165 | 1448 | 1650
[5 empty] | 40 | 6 | 0.135 | 0.161 | 0.188 | 0.207 | 0.223 | [9 empty] | LCF Latent |  | 60 | 679 | 1031 | 1385 | 1723 | 1963
[16 empty] | Leakage Class .06/.06 | 0.87 | 0.83 | 0.79 | 0.78 | 0.33 |  | 70 | 793 | 1204 | 1617 | 2011 | 2291
[5 empty] | 0 | 1 | 0.211 | 0.262 | 0.314 | 0.333 | 0.366 |  |  |  |  | Leakage Class .09/.15 | 0.92 | 0.92 | 0.89 | 0.87 | 0.65
[5 empty] | 85 | 2 | 0.227 | 0.266 | 0.3 | 0.344 | 0.376 |  |  |  |  | Leakage Class .12/.24 | 1 | 1 | 1 | 1 | 1 |  | Default Duct Wall Surface Area
[5 empty] | 90 | 3 | 0.246 | 0.275 | 0.319 | 0.344 | 0.394 |  |  |  |  | Leakage Class .24/.47 | 1.37 | 1.47 | 1.53 | 1.59 | 2.83 |  | SA | 308 | 476 | 633 | 773 | 908
[5 empty] | 95 | 4 | 0.247 | 0.285 | 0.325 | 0.364 | 0.414 |  |  |  |  | Leakage Class .35/.70 | 1.84 | 2.05 | 2.18 | 2.34 | 5.13 |  | RA | 55 | 82 | 105 | 128 | 147
[5 empty] | 100 | 5 | 0.252 | 0.297 | 0.349 | 0.385 | 0.421

## Group (hidden)
10Low | 2 | A | 2 | 95 | 7
10Medium | 3 | B | 3 | 105 | 6
15Low | 4 | C | 4 | 110 | 5
15Medium | 5 | D | 5 | 120 | 4
15High | 6 | E | 6 | 130 | 3
20Low | 7 | F | 7 | 150 | 2
20Medium | 8 | G | 8
20High | 9 | H | 9
25Medium | 10 | I | 10
25High | 11 | J | 11
30High | 12 | K | 12
35High | 13
Walls-Above Grade
| A | B | C | D | E | F | G | H | I | J | K
10Low | 25.5 | 23.1 | 20.5 | 18.5 | 16.4 | 14.3 | 12.3 | 11.7 | 11 | 10.4 | 9.6
10Medium | 21.5 | 19.1 | 16.5 | 14.5 | 12.4 | 10.3 | 8.3 | 7.7 | 7 | 6.4 | 5.6
15Low | 30.5 | 28.1 | 25.5 | 23.5 | 21.4 | 19.3 | 17.3 | 16.7 | 16 | 15.4 | 14.6
15Medium | 26.5 | 24.1 | 21.5 | 19.4 | 17.4 | 15.3 | 13.3 | 12.7 | 12 | 11.4 | 10.5
15High | 21.5 | 19.1 | 16.5 | 14.5 | 12.4 | 10.3 | 8.3 | 7.7 | 7 | 6.4 | 5.6
20Low | 35.5 | 33.1 | 30.5 | 28.5 | 26.4 | 24.3 | 22.3 | 21.7 | 21 | 20.4 | 19.6
20Medium | 31.5 | 29.1 | 26.5 | 24.5 | 22.4 | 20.3 | 18.3 | 17.7 | 17 | 16.4 | 15.6
20High | 26.5 | 24.1 | 21.5 | 19.5 | 17.4 | 15.3 | 13.3 | 12.7 | 12 | 11.4 | 10.6
25Medium | 36.5 | 34.1 | 31.5 | 29.5 | 27.4 | 25.3 | 23.3 | 22.7 | 22 | 21.4 | 20.6
25High | 31.5 | 29.1 | 26.5 | 24.5 | 22.4 | 20.3 | 18.3 | 17.7 | 17 | 16.4 | 15.6
30High | 36.5 | 34.1 | 31.5 | 29.5 | 27.4 | 25.3 | 23.3 | 22.7 | 22 | 21.4 | 20.6
35High | 41.5 | 39.1 | 36.5 | 34.5 | 32.4 | 30.3 | 28.3 | 27.7 | 27 | 26.4 | 25.6
Walls-Shaded
| A | B | C | D | E | F | G | H | I | J | K
10Low | 14.8 | 12.7 | 10.6 | 9.4 | 8 | 6.9 | 5.6 | 5.3 | 4.9 | 4.7 | 4.5
10Medium | 10.8 | 8.7 | 6.6 | 5.4 | 4 | 2.9 | 1.6 | 1.3 | 0.9 | 0.7 | 0.5
15Low | 19.8 | 17.7 | 15.6 | 14.4 | 13 | 11.9 | 10.6 | 10.3 | 9.9 | 9.7 | 9.5
15Medium | 15.8 | 13.7 | 11.6 | 10.4 | 9 | 7.9 | 6.6 | 6.3 | 5.9 | 5.7 | 5.5
15High | 10.8 | 8.7 | 6.6 | 5.4 | 4 | 2.9 | 1.6 | 1.3 | 0.9 | 0.7 | 0.5
20Low | 24.8 | 22.7 | 20.6 | 19.4 | 18 | 16.9 | 15.6 | 15.3 | 14.9 | 14.7 | 14.5
20Medium | 20.8 | 18.7 | 16.6 | 15.4 | 14 | 12.9 | 11.6 | 11.3 | 10.9 | 10.7 | 10.5
20High | 15.8 | 13.7 | 11.6 | 10.4 | 9 | 7.9 | 6.6 | 6.3 | 5.9 | 5.7 | 5.5
25Medium | 25.8 | 23.7 | 21.6 | 20.4 | 19 | 17.9 | 16.6 | 16.3 | 15.9 | 15.7 | 15.5
25High | 20.8 | 18.7 | 16.6 | 15.4 | 14 | 12.9 | 11.6 | 11.3 | 10.9 | 10.7 | 10.5
30High | 25.8 | 23.7 | 21.6 | 20.4 | 19 | 17.9 | 16.6 | 16.3 | 15.9 | 15.7 | 15.5
35High | 30.8 | 28.7 | 26.6 | 25.4 | 24 | 22.9 | 21.6 | 21.3 | 20.9 | 20.7 | 20.5

## Calc (hidden)
#N/A | #N/A | #N/A | #N/A |  | ACF | 0 | 1
[6 empty] | 250 | 0.9925
|  | Doors |  |  |  | 500 | 0.985
Calculated CLTD |  | #N/A |  |  |  | 750 | 0.9775
|  | Design | CLTD | Const 20 |  | 1000 | 0.97
10 | 10 | 10Low | 25 | 9 |  | 1250 | 0.96
11 | 10 | 10Medium | 21 | 5 |  | 1500 | 0.95
12 | 15 | 15Low | 30 | 14 |  | 1750 | 0.94
13 | 15 | 15Medium | 26 | 10 |  | 2000 | 0.93
14 | 15 | 15High | 21 | 5 |  | 2250 | 0.92
15 | 15 | 20Low | 35 | 19 |  | 2500 | 0.91
16 | 15 | 20Medium | 31 | 15 |  | 2750 | 0.9
17 | 20 | 20High | 26 | 10 |  | 3000 | 0.89
18 | 20 | 25Medium | 36 | 20 |  | 3250 | 0.885
19 | 20 | 25High | 31 | 15 |  | 3500 | 0.88
20 | 20 | 30High | 36 | 20 |  | 3750 | 0.875
21 | 20 | 35High | 41 | 25 |  | 4000 | 0.87
22 | 25 |  |  |  |  | 4250 | 0.8625
23 | 25 |  |  |  |  | 4500 | 0.855
24 | 25 |  |  |  |  | 4750 | 0.8475
25 | 25 |  |  |  |  | 5000 | 0.84
26 | 25 |  |  |  |  | 5250 | 0.83
27 | 30 |  |  |  |  | 5500 | 0.82
28 | 30 |  |  |  |  | 5750 | 0.81
29 | 30 |  |  |  |  | 6000 | 0.8
30 | 30 |  |  |  |  | 6250 | 0.7925
31 | 30 |  |  |  |  | 6500 | 0.785
32 | 35 |  |  |  |  | 6750 | 0.7775
33 | 35 |  |  |  |  | 7000 | 0.77
34 | 35 |  |  |  |  | 7250 | 0.765
35 | 35 |  |  |  |  | 7500 | 0.76
[6 empty] | 7750 | 0.755
[6 empty] | 8000 | 0.75
[6 empty] | 8250 | 0.7425
[6 empty] | 8500 | 0.735
[6 empty] | 8750 | 0.7275
[6 empty] | 9000 | 0.72
[6 empty] | 9250 | 0.7125
[6 empty] | 9500 | 0.705
[6 empty] | 9750 | 0.6975
[6 empty] | 10000 | 0.69
[6 empty] | 10250 | 0.6825
[6 empty] | 10500 | 0.675
[6 empty] | 10750 | 0.6675
[6 empty] | 11000 | 0.66
[6 empty] | 11250 | 0.6525
[6 empty] | 11500 | 0.645
[6 empty] | 11750 | 0.6375
[6 empty] | 12000 | 0.63