## Assessment (hidden)
Exhaust-Only Residential Ventilation Fan Measure Number: (Residential, Ventilation End Use)
| Algorithm Value name | Static Pressure (in. wc.) |  | Notes
0.1
CFM | CFMrated | 105 |  | Based upon typically installed qualifying products
Baseline CFM/W |  | 6.3 |  | Compare to Estar and Code
Efficient CFM/W |  | 12.6 |  | Based upon most typically installed qualifying products
Delta CFM/W |  | -6.3
Average delta CFM/W | deltaEfficiency | -6.3 |  | Field static pressures difficult to assess, but likely fall in the middle
Avg. delta W/CFM |  | -0.15873 |  | just the inverse of CFM/W
|  | 315 |  | implied max CFM per code 50W max. at avg SP |  | Sec 304.5 Fan Motor Requirements; Design Criteria for Residential Mechanical Ventilation Systems 2011 Vermont Residential Building Energy Standards
CFM/Day
Continuous |  | 69300 |  | 50% of Capacity for 22 hours/day | 1440
Peak |  | 12600 |  | 100% of Capacity for 2 hours/day
Avg CFM |  | 56.875
Capacity Factor | CF | 54.17% |  | Weighted for runtime | 50% | *CFM/Watt values qualifying fans use motors that operate at least 50% more efficiently
kWh savings | kWh | -79.0833 | kWh yr
| Hours | 8760
Note on E5: Note that energy star criteria are rather dated, focus on lighting savings with fan efficiencies of only 1.4 and 2.8 CFM/Watt for this size range. These baseline values exceed energy star significantly and would support code eligible compliant delivery of 250CFM. Baseline efficiency is 50% of Efficient product based upon review of product information sheets for qualifying and baseline equipment

## Summary
Measure Name |  | Residential Fan - Quiet, Exhaust-only, continuous ventilation
Measure Description |  | This market opportunity is defined by the need for continuous mechanical ventilation due to reduced air-infiltration from a tighter building shell. In retrofit projects, existing fans may be too loud, or insufficient in other ways, to be operated as required for proper ventilation. This measure assumes a fan capcity of 50 CFM rated at less then 2.0 sones at 0.1 inches of water column static pressure. This measure may be applied to larger capacity efficient fans with bi-level controls because the savings and incremental costs are similar.
Baseline Description |  | New standard efficiency (average CFM/Watt of 3.1 ) exhaust-only ventilation fan, quiet (< 2.0 sones ) operating in accordance with recommended ventilation rate indicated by ASHRAE 62.2
Efficient Description |  | New efficient (average FM/watt of 8.3 CFM/Watt) exhaust-only ventilation fan, quiet (< 2.0 sones) Continuous operation in accordance with recommended ventilation rate indicated by ASHRAE 62.2
Measure Limitations (target markets) |  | 50 to 150 CFM, In new or existing residential applications. Market opportunity is the need for new exhaust fan to be operated in accordance with ASHRAE 62.2
Cost
|  |  |  | Incremental | Base
Savings | Continuous | 87.632 | kWh | 43.5 | 136.5
| with bi-level controls | 83.955 | kWh | 31.2395 | 215.3421
| Average Demand Savings | 0.010004 | kW
| Measures | 150 | per year
| Gross MWH savings/yr | 13.1448 | MWh/yr

## Fan Info
Efficient Quiet Fan Measure Product Information | [6 empty] | CFM/Watt
Source of Price Data | Wholesale Online Vendor | [5 empty] | High Level (Spot) |  | Low Level
Source of Eq. Data | MFR Spec Submittal Sheets | [5 empty] | Rated CFM |  | 50 | CFM
|  |  |  | Nominal CFM |  | Sones | 0.1 | 0.25 | 0.1 | 0.25
Categorization | Name | Model # | Price | 0.1 | 0.25 |  | CFM/Watt |  |  |  | Features
Baseline | WhisperCeiling | FV-05VQ5 | 147 | 50 | 36 | 0.3 | 4.7 | 3.2
Baseline | WhisperFit | FV-05VFL2 | 177.75 | 50 | 35 | 0.3 | 3 | 3.1 |  |  | Light
Baseline | WhisperFit | FV-05VF2 | 129 | 50 | 35 | 0.4 | 3.3 | 2
Baseline | WhisperValue | FV-05VS1 | 92.25 | 50 | 37 | 0.8 | 3.2 | 2.4
|  | Average | 136.5 | 50 | 35.75 | 0.45 | 3.55 | 2.675
[6 empty] | Baseline | 3.1125
Baseline | WhisperValue | FV-08VS1 | 96.75 | 80 | 65 | 1.4 | 3.4 | 2.8
Baseline | WhisperFit | FV-08VF2 | 136.5 | 80 | 60 | 0.8 | 3.3 | 2.5
Baseline | Whisper Ceiling | FV-08VQ5 | 156.75 | 80 | 65 | 0.3 | 5.8 | 4.5
|  | Average | 130 | 80 | 63.3333 | 0.83333 | 4.1667 | 3.2667
3.7167
Baseline | WhisperValue | FV-10VSL1 | 168.75 | 100 | 90 | 1.5 | 2.9 | 2.7 |  |  | Light
Baseline | WhisperCeiling | FV-11VQ5 | 175.5 | 110 | 95 | 1 | 3.1 | 2.7
Baseline | WhisperFit | FV-11-VF2 | 153.75 | 110 | 94 | 1.5 | 3.3 | 2.8
Baseline | WhisperFit | FV-11-VFL2 | 225.75 | 110 | 96 | 1.3 | 3.3 | 2.9 |  |  | Light
|  | Average | 185 | 110 | 95 | 1.2667 | 3.2333 | 2.8
3.0167
Efficient | WhisperGreen | FV-05VK3 | 180 | 50 | 54 | 0.3 | 12.4 | 7.7
Efficient | WhisperGreen | FV-05VK1 | 180 | 50 | 49 | 0.3 | 8.5 | 4.4
|  |  | 180 | 50 | 51.5 | 0.3 | 10.45 | 6.05
[6 empty] | Efficient | 8.25
Efficient-Bi-level | WhisperGreen | FV-13VKS3 | 244.5 | 130 | 126 | 0.5 | 7.5 | 4.8 | 9.8 | 5 | Continuous and spot ventilation and Motion sensor
Efficient-Bi-level | WhisperGreen | FV-08VKM2 | 139.99 | 80 | 82 | 0.3 | 7.8 | 5 | 9 | 4.9 | Continuous and spot ventilation and Motion sensor
Efficient-Bi-level | WhisperGreen | FV-08VKML3 | 309.75 | 80 | 79 | 0.3 | 11.2 | 6.6 | 12.5 | 7 | Continuous and spot ventilation and Motion sensor and light
Efficient-Bi-level | WhisperGreen | FV-13VKM3 | 266.25 | 130 | 126 | 0.5 | 7.5 | 4.8 | 9.8 | 5 | Continuous and spot ventilation and Motion sensor
Efficient-Bi-level | WhisperGreen | FV-08VKM3 | 231 | 80 | 79 | 0.3 | 12.1 | 7.6 | 12.4 | 7.7 | Continuous and spot ventilation and Motion sensor
Efficient-Bi-level | WhisperGreen | FV-08VKSL3 | 288 | 80 | 79 | 0.3 | 11.2 | 6.6 | 12.5 | 7 | Continuous and spot ventilation and and light
[6 empty] | Efficient w/Controls | (See Bi-Level Efficient Sheet For Caclulated Weighted average)

## Continuous
Continuous Operation
ASHRAE 62.2 Mechanical Ventilation Requirement
Bedrooms | 3
Square footage | 1800
Mech Vent air-requirement* | 48 | Calculated according to "=0.01*Square_Footage+7.5*(Bedrooms+1)
*note that this does not account for the infiltration credit or airflow deficits caused by other fans.
From Fan Info worksheet |  | --> | CFM/Watt
|  |  | Baseline | Efficient
|  |  | 3.1125 | 8.25
Watts
|  | CFM | Baseline | Efficient | Delta W | Annual kWh | BaseCost | EffCost | Incr. Cost
Fan Capacity Selection | --> | 50 | 16.0643 | 6.0606 | 10.0037 | 87.632 | 136.5 | 180 | 43.5
|  | 80 | 25.7028 | 9.697 | 16.0058 | 140.2112
|  | 110 | 35.3414 | 13.3333 | 22.008 | 192.7904
|  | 130 | 41.7671 | 15.7576 | 26.0095 | 227.8432

## Bi-level Baseline
Baseline Quiet Fans | [5 empty] | Cycled On
|  | Web Price |  |  |  | Rated |  | *all of the below are continuous ventilation only
|  |  | CFM |  | Sones | CFM/Watt
|  |  | 0.1 | 0.25 |  | 0.1 | 0.25
WhisperCeiling | FV-11VQ5 | 175.5 | 110 | 95 | 1 | 3.1 | 2.7
WhisperValue | FV-08VS1 | 96.75 | 80 | 65 | 1.4 | 3.4 | 2.8
WhisperFit | FV-08VF2 | 136.5 | 80 | 60 | 0.8 | 3.3 | 2.5
Whisper Ceiling | FV-08VQ5 | 156.75 | 80 | 65 | 0.3 | 5.8 | 4.5
WhisperFit | FV-11-VF2 | 153.75 | 110 | 94 | 1.5 | 3.3 | 2.8
WhisperFit | FV-11-VFL2 | 225.75 | 110 | 96 | 1.3 | 3.3 | 2.9 | Light
WhisperValue | FV-10VSL1 | 168.75 | 100 | 90 | 1.5 | 2.9 | 2.7 | Light
| Fan Average | 159.1071 | 95.7143 | 80.7143 | 1.1143 | 3.5857 | 2.9857
| AirCycler Controls | 56.235 |  |  |  | 3.2857 |  | average
| Baseline Average | 215.3421
Static Pressure | 0.1 | 0.25
Cu. Ft per Day | 77600 | 77420 | Equivalent to Efficient level of ventilation
Hours on/day | 13.5124 | 15.9864 | Runtime req'd to deliver ft^3/day
avg CFM/day | 53.8889 | 53.7639
kWh per year | 131.6521 | 157.7417
average | 144.6969
WhisperCeiling | FV-05VQ5 | 147 | 50 | 36 | 0.3 | 4.7 | 3.2
WhisperFit | FV-05VFL2 | 177.75 | 50 | 35 | 0.3 | 3 | 3.1 | Light
WhisperValue | FV-05VS1 | 92.25 | 50 | 37 | 0.8 | 3.2 | 2.4
| Controls | [5 empty] | 1000
0.11416
55.51
56.96
[7 empty] | 1 | kw
[6 empty] | annual | 730 | kWh
5000
6.8493
0.38052

## Bi-Level Efficient
Efficient Quiet Fan Measure Re-Re-Assessment | [5 empty] | CFM/Watt
Source of Price Data | Wholesale Online Vendor |  |  |  | Ventilation Level | Spot |  | Continuous |  | *all of the below are continuous and spot ventilation
Source of Eq. Data | MFR Spec Submittal Sheets |  |  |  | hours/day | 2 |  | 22
[6 empty] | Rated CFM |  | 50 | CFM
|  |  | Nominal CFM |  |  | 0.1 | 0.25 | 0.1 | 0.25
|  |  | 0.1 | 0.25 | Sones | CFM/Watt
WhisperGreen | FV-13VKS3 | 244.5 | 130 | 126 | 0.5 | 7.5 | 4.8 | 9.8 | 5 | Continuous and spot ventilation and Motion sensor
WhisperGreen | FV-08VKM2 | 139.99 | 80 | 82 | 0.3 | 7.8 | 5 | 9 | 4.9 | Continuous and spot ventilation and Motion sensor
WhisperGreen | FV-08VKML3 | 309.75 | 80 | 79 | 0.3 | 11.2 | 6.6 | 12.5 | 7 | Continuous and spot ventilation and Motion sensor and light
WhisperGreen | FV-13VKM3 | 266.25 | 130 | 126 | 0.5 | 7.5 | 4.8 | 9.8 | 5 | Continuous and spot ventilation and Motion sensor
WhisperGreen | FV-08VKM3 | 231 | 80 | 79 | 0.3 | 12.1 | 7.6 | 12.4 | 7.7 | Continuous and spot ventilation and Motion sensor
WhisperGreen | FV-08VKSL3 | 288 | 80 | 79 | 0.3 | 11.2 | 6.6 | 12.5 | 7 | Continuous and spot ventilation and and light
| Average | 246.5817 | 96.6667 | 95.1667 | 0.36667 | 9.55 | 5.9 | 11 | 6.1
| Incremental Cost | 31.2395 |  |  | sp avg. | 7.725 |  | 8.55
Avg. Savings
Static Pressure | 0.1 | 0.25 |  | Spot hrs/day | 0.1 | 0.25
Daily Ventilation (ft^3) | 77600 | 77420 |  | 0.1 | 82.6047 | 75.1579
Daily Ventilation (CFM) | 53.8889 | 53.7639 |  | 0.25 | 83.0119 | 75.5518
Efficient kWh/yr | 43.8892 | 77.5945 |  | 0.5 | 83.6906 | 76.2083
Baseline kWh/yr | 131.6521 | 157.7417 |  | 1 | 85.048 | 77.5212
Savings per year | 87.7629 | 80.1472 |  | 4 | 93.1925 | 85.3991
Average | 83.955 |  |  | 24 | 147.4892 | 137.918
81.28
89.3

## Sheet3 (hidden)
Application
When the decision is to install a new ventilation fan you can do either.
Also Residential Retrofit
Multi-family
screening | measure
no new cost of the fan
Baseline
Issue list
static pressure
Baseline Wattage |  | ? | 50W 2.6CFM/watt uses max of 130 seems to high
|  | ? | Is there any data or information on actual fan wattage (or efficiency), other than Energy Star fans? What does the Energy Star website say
|  | ? | 110 vs 130 as the upper bound of typical installs
|  | ? | The analysis seems to suggest that the efficient fans have BLPM motors, but this is not included in the description. Is this a given if it’s a multi-speed fan?
|  | ? | clean up note about baseline wattage
|  | ? | Logic for bi-level operation assumption split? ? Are these typically controlled as low speed continuous with a button to bump to 100%? That should be explained, as well as the basis of the low speed assumption you made (40 or 50 CFM)
|  | ? | Static Pressure of 0.1 realistic? Recalculate at higher static Pressures (what is the impact on partially shaded motors
| 130 | DONE | Size limit for this measure

## Sample Product Specs and Calcs
80 | CFM | CFM/Watt
Run time |  | 0.1 | static pressure
8.333% | 80 | 12.1
| 70 | 13.3
| 60 | 13.6
| 50 | 12.4
91.67% | 40 | 12.8
| 30 | 11.4
Weighted Average |  | 12.7417
130 | CFM | CFM/Watt
Runtime |  | 0.1 | static pressure
8.333% | 130 | 11
| 110 | 12
| 90 | 15
| 70 | 18
91.67% | 50 | 23
15.8
Weighted Average |  | 22
Avg. of wtd. Avg |  | 17.3708
Efficient CFM/Watt |  | 17.3708
Baseline |  | 5.775 | 50% of Efficient fan efficiency at 100% rated capacity
Sample Calculation
kW | 0.092308
0.031034
0.061273
6.4337
| 0.0064337 | kW
kWh | 56.3591 | kWh
| 150 | units per year
8453.8647