## Sheet1
S fuel CHP = F grid + F thermal CHP – F total CHP
F grid = E CHP X H grid
H CHP = (F total CHP – F thermal CHP) / E CHP
S CHP Elec = S fuel CHP / H CHP
S CHP gas = S fuel CHP / 100,000 Btu/therm
Units | Assumptions
kW | CHP Capacity (kW) | 850
yrs | Measure Life (years) | 20
Hrs | Operating Hours (Hrs) | 6002.401
kWh | E CHP (kWh) | 5102040.85
2% | Parasitic Loads (kWh) | 102040.817
| Total E CHP (kWh) | 5000000.033
kBtu/kWh | Grid heat rate (kBtu/kWh) (Hgrid) | 10
kBtu/yr | F grid (Fg) (kBtu/yr) | 50000000.33
kBtu/hr | Usable Waste heat from CHP (kBtu/hr) | 3733.0174
| Thermal Utilization | 81.5%
| Displaced thermal Eff | 70.24%
| Electric Efficiency % (HHV) | 34.82%
kBtu/yr | F thermal CHP (Ft) (kBtu/yr) | 25999999.5169
| Total CHP efficiency | 70.64%
kBtu/hr | Fuel Use by CHP (kBtu/hr) | 8329.9999
kBtu/yr | F total CHP (Fc) (kBtu/yr) | 49999999.6559
kBtu/yr | S fuel CHP [ Fg+Ft-Fc ] | 26000000.191
Key Assumptions
|  | Site |  |  | Source
Changes in Energy Consumption (kBtu) |  | Increase | Reduction | Net Impact | Increase | Reduction | Net Impact |  | Heat Rate | Grid CO2/kWh
| Electricity | 0 | 17065000.1126 | -17065000.1126 | 0 | 50000000.33 | -50000000.33 |  | 10000 | 1800
| Gas | 49999999.6559 | 25999999.5169 | 24000000.139 | 49999999.6559 | 25999999.5169 | 24000000.139 |  | affects scenario 3 | affects scenario 4
| Total | 49999999.6559 | 43064999.6296 | 6935000.0264 | 49999999.6559 | 75999999.8469 | -26000000.191
Savings claim calcs
Scenario |  | Electric Utility Only - kWh Savings |  |  | Joint Program - kWh Savings |  |  | Joint Program - therm Savings
|  | Electric kWh Output | Penalty for Increased Gas Use | Total | Electric kWh Output | Penalty for Increased Gas Use (vs. 65% CHP) | Total | Baseline Therms (65% CHP Effic) | Efficient CHP | Savings
1 | No adjustment for increased gas use | 5000000.033 | 0 | 5000000.033 | 5000000.033 | 0 | 5000000.033 | 543411.691 | 499999.9966 | 43411.6944
2 | Gas to kWh - site BTU conversion (3412 Btu/kWh) | 5000000.033 | 7031936.7533 | -2031936.7203 | 5000000.033 | 8303887.9521 | -3303887.9191 | 543411.691 | 499999.9966 | 43411.6944
3 | Gas to kWh - source BTU conversion (heat rate) | 5000000.033 | 2400000.0139 | 2600000.0191 | 5000000.033 | 2834116.958 | 2165883.075 | 543411.691 | 499999.9966 | 43411.6944
4 | Gas to kWh - CO2 equivalency conversion (C02/grid kWh) | 5000000.033 | 1417904.7015 | 3582095.3315 | 5000000.033 | 1674378.2234 | 3325621.8096 | 543411.691 | 499999.9966 | 43411.6944 | analogous to current TRM, except that current TRM has simplified calcs based on CHP efficiency (based on these kind of detailed calcs for different types of CHPs)
5 | Current TRM formula (based on CO2 equivalency) |  |  | 3782176.0406 |  |  | 3500000.0231 |  |  | 36682.8814
CO2 Equivalency Assumptions and Calcs
| fossil gas CO2 emissions rate | 53.06 | kg/MMBtu | From both EPA (http://www.epa.gov/climateleadership/documents/emission-factors.pdf) and EIA (http://www.eia.gov/oiaf/1605/coefficients.html#tbl1)
|  | 2.2046 | kg to lb. conversion
| electric grid CO2 emissions rate | 1800 | lbs CO2/kWh |  |  | 2019 Egrid
[6 empty] | Con Ed (RFCW) | Ameren (SRMW) | Statewide Wtd Avg
[5 empty] | non-baseload | 1832 | 1961 | 1870.7
| CO2 tons/MMBtu from gas on-site | 0.058489 |  |  | all fossil | 1068 | 1584 | 1222.8
| Avg electric T&D marginal losses | 10% |  |  |  | 70% | 30%
| CO2 tons/MWh from electricity | 0.99
| CO2 tons/yr from on-site fuel | 2924.4284
| CO2 tons/yr displaced thermal | 1520.7028
| CO2 tons/yr displaced electric | 4950
| CO2 tons/yr net impact | -3546.2744
| Equivalent electricity impact (kWh) | -3582095.3315
| equiv elec CO2 impact as % of CHP elec output | 71.64%
Note on B17: raikar: From ICF draft paper, Table 3, Total Heat Recovered
Note on B20: raikar: From ICF draft paper, Table 3, Electrical Efficiency