## Sheet1
S fuel CHP = F grid + F thermal CHP – F total CHP
F grid = E CHP X H grid
H CHP = (F total CHP – F thermal CHP) / E CHP
S CHP Elec = S fuel CHP / H CHP
S CHP gas = S fuel CHP / 100,000 Btu/therm
Units | Assumptions
kW | CHP Capacity (kW) | 850
yrs | Measure Life (years) | 20
Hrs | Operating Hours (Hrs) | 6002.401
kWh | E CHP (kWh) | 5102040.85
2% | Parasitic Loads (kWh) | 102040.817
| Total E CHP (kWh) | 5000000.033
kBtu/kWh | Grid heat rate (kBtu/kWh) (Hgrid) | 10
kBtu/yr | F grid (Fg) (kBtu/yr) | 50000000.33
kBtu/hr | Usable Waste heat from CHP (kBtu/hr) | 3733.0174
| Thermal Utilization | 81.5%
| Displaced thermal Eff | 70.24%
| Electric Efficiency % (HHV) | 34.82%
kBtu/yr | F thermal CHP (Ft) (kBtu/yr) | 25999999.5169
| Total CHP efficiency | 70.64%
kBtu/hr | Fuel Use by CHP (kBtu/hr) | 8329.9999
kBtu/yr | F total CHP (Fc) (kBtu/yr) | 49999999.6559 | [6 empty] | Key Assumptions
kBtu/yr | S fuel CHP [ Fg+Ft-Fc ] | 26000000.191
[9 empty] | Heat Rate | Grid CO2 lbs/MWh
|  | Site |  |  | Source |  |  |  | 10000 | 1800
Changes in Energy Consumption (kBtu) |  | Increase | Reduction | Net Impact | Increase | Reduction | Net Impact |  | affects scenario 3 | affects scenario 4
| Electricity | 0 | 17065000.1126 | -17065000.1126 | 0 | 55000000.363 | -55000000.363
| Gas | 51749999.6439 | 26909999.5 | 24840000.1438 | 51749999.6439 | 26909999.5 | 24840000.1438
| Total | 51749999.6439 | 43974999.6127 | 7775000.0312 | 51749999.6439 | 81909999.863 | -30160000.2192
Savings claim calcs
Scenario |  | Electric Utility Only - kWh Savings |  |  | Joint Program - kWh Savings |  |  | Joint Program - therm Savings |  |  | Gas Only Program - therm Savings
|  | Electric kWh Output | Penalty for Increased Gas Use | Total | Electric kWh Output | Penalty for Increased Gas Use (vs. 65% CHP) | Total | Baseline Therms (65% CHP Effic) | Efficient CHP | Savings | Baseline Therms (vs. 60% CHP or no CHP) | CHP | Savings
1 | No adjustment for increased gas use | 5000000.033 | 0 | 5000000.033 | 5000000.033 | 0 | 5000000.033 | 543411.691 | 499999.9966 | 43411.6944 | 588695.9986 | 499999.9966 | 88696.002 | gas only baseline is 60% CHP; CHP savings are purely efficiency gains vs. baseline
2 | Gas to kWh - site BTU conversion (3412 Btu/kWh) | 5000000.033 | 7278054.5397 | -2278054.5067 | 5000000.033 | 8594524.0304 | -3594523.9974 | 543411.691 | 499999.9966 | 43411.6944 | 259999.9952 | 329349.9954 | -69350.0003 | gas only baseline is thermal therms displaced; CHP savings = [increased on-site therms - (decreased site electric BTUs / 100,000)]
3 | Gas to kWh - source BTU conversion (heat rate) | 5000000.033 | 2258181.8313 | 2741818.2017 | 5000000.033 | 2666646.4105 | 2333353.6225 | 543411.691 | 499999.9966 | 43411.6944 | 259999.9952 | -50000.0071 | 310000.0022 | gas only baseline is thermal therms displaced, CHP savings = [increased on-site gas therms - (decreased grid BTUs / 100,000)]
4 | Gas to kWh - CO2 equivalency conversion (C02/grid kWh) | 5000000.033 | 3005957.9673 | 1994042.0657 | 5000000.033 | 3549681.8337 | 1450318.1993 | 543411.691 | 499999.9966 | 43411.6944 | n.a. | n.a. | 337519.2268 | CHP savings = CO2e emission reductions / CO2e emissions per therm of gas
5 | Current TRM formula (based on CO2 equivalency) |  |  | 3782176.0406 |  |  | 3500000.0231 |  |  | 36682.8814 |  |  | 69182.8807 | current TRM formulae
CO2 Equivalency Assumptions and Calcs
| fossil gas CO2 emissions rate | 53.06 | kg/MMBtu | From both EPA (http://www.epa.gov/climateleadership/documents/emission-factors.pdf) and EIA (http://www.eia.gov/oiaf/1605/coefficients.html#tbl1)
|  | 2.2046 | kg to lb. conversion
| electric grid CO2 emissions rate | 1800 | lbs CO2/MWh |  |  | 2019 Egrid
[6 empty] | Con Ed (RFCW) | Ameren (SRMW) | Statewide Wtd Avg
[5 empty] | non-baseload | 1832 | 1961 | 1870.7
[5 empty] | all fossil | 1068 | 1584 | 1222.8
| CO2 tons/MMBtu from gas on-site | 0.058489 |  |  |  | 70% | 30%
| Avg electric T&D marginal losses | 10%
| Gas T&D losses | 3.5% | national avg LAUG - excludes losses upstream of city gate which could also be added
| Methane to CO2 multiplier | 32 | EPA says 28 to 36 over 100 years (https://www.epa.gov/ghgemissions/understanding-global-warming-potentials#:~:text=Methane%20(CH4)%20is%20estimated,uses%20a%20different%20value.).&text=Nitrous%20Oxide%20(N2O,for%20a%20100%2Dyear%20timescale)
| CO2 tons/MWh from electricity | 0.99
| CO2 tons/yr from on-site fuel | 6199.7882
| CO2 tons/yr displaced thermal | 3223.8898
| CO2 tons/yr displaced electric | 4950
| CO2 tons/yr net impact | -1974.1016
| Equivalent electricity impact (kWh) | -1994042.0657
| equiv elec CO2 impact as % of CHP elec output | 39.88%
| Equivalent gas impact (therms) | -337519.2268
Note on B17: raikar: From ICF draft paper, Table 3, Total Heat Recovered
Note on B20: raikar: From ICF draft paper, Table 3, Electrical Efficiency