## HVAC End Use

Many of the commercial HVAC measures use equivalent full load hours (EFLH) to calculate heating and cooling savings.  The tables with these values are included in this section and referenced in each measure.

To estimate the EFLHs by building type and climate zone provided below, OpenStudio models have been developed using the most appropriate DOE prototypical models, as described in NREL’s “U.S. Department of Energy Commercial Reference Building Models of the National Building Stock”, as the initial base. Adjustments to these models were discussed and approved through a TRM Working Group and then calibrated to align the energy use intensity (kBtu/sq ft) from the models to within 30% of ComStock/ResStock models where possible, or CBECS/RECS data when not available. Calibration adjustments included updates to Lighting Power Density (LPD), exterior lighting, Equipment Power Density (EPD), HVAC setpoints, occupancy schedules, space type assignments, and other system configurations to better reflect actual building operations.

The key building characteristics of the OpenStudio models and a description of the calibration adjustments made is provided in “XXX”. These documents and all the models are available on the SharePoint site.

Note, for greenhouse boiler control measures, like Modulating Boiler Controls and/or Boiler Oxygen Trim Controls, it is recommended to use the methodology detailed in 4.4.21 Linkageless Boiler Controls for Space Heating and 4.4.22 Oxygen Trim Controls for Space Heating Boilers, respectively.

Note that where a measure installation is within a building or application that does not fit with any of the defined building types below, the user should apply custom assumptions where it is reasonable to estimate them, else the building of best fit should be utilized.

Equivalent Full Load Hours for Heating (EFLHHeating) for Existing Buildings:

| Building Type | Heating EFLH Existing Buildings |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Assembly | 1,007 | 1,024 | 894 | 804 | 786 | OpenStudio |
| Assisted Living | 2,210 | 2,127 | 2,114 | 2,164 | 2,150 | OpenStudio |
| Auto Dealership | 1,016 | 1,053 | 942 | 852 | 817 | OpenStudio |
| Childcare/Pre-School | 1,855 | 1,831 | 1,682 | 1,505 | 1,476 | OpenStudio |
| College | 1,558 | 1,677 | 1,433 | 1,318 | 1,330 | OpenStudio |
| Convenience Store | 2,338 | 2,412 | 2,240 | 2,201 | 2,211 | OpenStudio |
| Drug Store | 974 | 990 | 889 | 712 | 622 | OpenStudio |
| Elementary School | 1,279 | 1,257 | 1,179 | 1,052 | 986 | OpenStudio |
| Emergency Services | 1,056 | 1,079 | 977 | 848 | 323 | OpenStudio |
| Garage | 914 | 889 | 794 | 619 | 642 | eQuest |
| Greenhouse – w/ Curtains | 4,009 | 3,726 | 3,255 | 2,728 | 2,504 | Virtual Grower 3.1 |
| Greenhouse – w/o Curtains | 4,032 | 3,746 | 3,274 | 2,742 | 2,518 | Virtual Grower 3.1 |
| Grocery | 2,683 | 2,725 | 2,561 | 2,559 | 2,590 | OpenStudio |
| Healthcare Clinic | 1,294 | 1,298 | 1,224 | 1,251 | 1,664 | OpenStudio |
| High School | 1,682 | 1,633 | 1,679 | 1,745 | 1,697 | OpenStudio |
| Hospital - CAV no econ | 1,360 | 1,373 | 1,255 | 1,166 | 1,158 | OpenStudio |
| Hospital - CAV econ | 1,386 | 1,409 | 1,286 | 1,196 | 1,182 | OpenStudio |
| Hospital - VAV econ | 823 | 812 | 717 | 621 | 640 | OpenStudio |
| Hospital - FCU | 1,539 | 1,549 | 1,400 | 1,244 | 1,186 | OpenStudio |
| Hotel/Motel | 1,643 | 1,644 | 1,511 | 1,386 | 1,417 | OpenStudio |
| Hotel/Motel - Common | 1,721 | 1,726 | 1,601 | 1,495 | 1,508 | OpenStudio |
| Hotel/Motel - Guest | 1,606 | 1,615 | 1,489 | 1,336 | 1,383 | OpenStudio |
| Manufacturing Facility | 1,153 | 1,156 | 1,027 | 974 | 968 | OpenStudio |
| MF - High Rise | 933 | 913 | 795 | 567 | 587 | OpenStudio |
| MF - High Rise - Common | 1,040 | 957 | 836 | 661 | 659 | OpenStudio |
| MF - High Rise - Residential | 977 | 957 | 840 | 646 | 683 | OpenStudio |
| MF - Mid Rise | 1,483 | 1,492 | 1,364 | 1,233 | 1,163 | OpenStudio |
| Movie Theater | 1,305 | 1,311 | 1,180 | 1,117 | 1,079 | OpenStudio |
| Office - High Rise - CAV no econ | 1,111 | 1,156 | 1,014 | 925 | 810 | OpenStudio |
| Office - High Rise - CAV econ | 1,120 | 1,162 | 1,032 | 948 | 834 | OpenStudio |
| Office - High Rise - VAV econ | 1,475 | 1,423 | 1,268 | 1,080 | 1,052 | OpenStudio |
| Office - High Rise - FCU | 608 | 533 | 510 | 466 | 379 | OpenStudio |
| Office - Low Rise | 1,240 | 1,426 | 1,187 | 1,154 | 1,037 | OpenStudio |
| Office - Mid Rise | 1,395 | 1,367 | 1,246 | 1,073 | 831 | OpenStudio |
| Religious Building | 1,398 | 1,390 | 1,245 | 1,099 | 1,057 | OpenStudio |
| Restaurant | 1,487 | 1,459 | 1,382 | 1,272 | 1,240 | OpenStudio |
| Retail - Department Store | 889 | 878 | 795 | 683 | 629 | OpenStudio |
| Retail - Strip Mall | 1,333 | 1,389 | 1,247 | 1,092 | 1,040 | OpenStudio |
| Warehouse | 1,245 | 1,274 | 1,126 | 1,067 | 1,057 | OpenStudio |
| Unknown | 1,319 | 1,345 | 1,219 | 1,134 | 1,082 | n/a |

Equivalent Full Load Hours for Heating (EFLHHeating) for New Construction:

| Building Type | Heating EFLH New Construction |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Assembly | 877 | 862 | 804 | 772 | 857 | OpenStudio |
| Assisted Living | 2,606 | 2,527 | 2,556 | 2,612 | 2,693 | OpenStudio |
| Auto Dealership | 650 | 646 | 595 | 468 | 423 | OpenStudio |
| Childcare/Pre-School | 536 | 508 | 487 | 377 | 346 | OpenStudio |
| College | 1,040 | 1,023 | 958 | 952 | 1,115 | OpenStudio |
| Convenience Store | 2,174 | 2,258 | 2,063 | 2,035 | 1,969 | OpenStudio |
| Drug Store | 467 | 430 | 375 | 290 | 219 | OpenStudio |
| Elementary School | 669 | 647 | 582 | 503 | 491 | OpenStudio |
| Emergency Services | 1,068 | 1,038 | 934 | 801 | 714 | OpenStudio |
| Grocery | 3,312 | 3,401 | 3,179 | 3,239 | 3,238 | OpenStudio |
| Healthcare Clinic | 643 | 621 | 546 | 494 | 482 | OpenStudio |
| High School | 1,901 | 1,764 | 1,855 | 2,163 | 1,987 | OpenStudio |
| Hospital - CAV no econ | 984 | 1,002 | 899 | 756 | 696 | OpenStudio |
| Hospital - CAV econ | 1,128 | 1,149 | 1,055 | 912 | 852 | OpenStudio |
| Hospital - VAV econ | 885 | 896 | 789 | 626 | 716 | OpenStudio |
| Hospital - FCU | 1,801 | 1,893 | 1,745 | 1,717 | 1,666 | OpenStudio |
| Hotel/Motel | 835 | 855 | 752 | 596 | 674 | OpenStudio |
| Hotel_Motel_Common | 1,382 | 1,407 | 1,320 | 1,180 | 1,162 | OpenStudio |
| Hotel_Motel_Guest | 976 | 1,009 | 883 | 722 | 793 | OpenStudio |
| Manufacturing Facility | 841 | 811 | 752 | 499 | 502 | OpenStudio |
| MF - High Rise | 634 | 617 | 506 | 322 | 307 | OpenStudio |
| MF - High Rise - Common | 904 | 823 | 732 | 563 | 524 | OpenStudio |
| MF - High Rise - Residential | 691 | 694 | 584 | 435 | 436 | OpenStudio |
| MF - Mid Rise | 914 | 913 | 777 | 599 | 484 | OpenStudio |
| Movie Theater | 939 | 930 | 851 | 769 | 757 | OpenStudio |
| Office - High Rise - CAV no econ | 807 | 809 | 685 | 513 | 468 | OpenStudio |
| Office - High Rise - CAV econ | 865 | 871 | 752 | 577 | 554 | OpenStudio |
| Office - High Rise - VAV econ | 921 | 921 | 835 | 730 | 703 | OpenStudio |
| Office - High Rise - FCU | 780 | 827 | 711 | 638 | 701 | OpenStudio |
| Office Low Rise | 606 | 578 | 532 | 462 | 452 | OpenStudio |
| Office - Mid Rise | 965 | 981 | 858 | 703 | 648 | OpenStudio |
| Religious Building | 639 | 639 | 578 | 491 | 460 | OpenStudio |
| Restaurant | 1,352 | 1,322 | 1,202 | 1,093 | 1,058 | OpenStudio |
| Retail - Department Store | 686 | 675 | 593 | 471 | 420 | OpenStudio |
| Retail - Strip Mall | 786 | 795 | 712 | 612 | 626 | OpenStudio |
| Warehouse | 1,247 | 1,261 | 1,208 | 1,100 | 1,119 | OpenStudio |
| Unknown | 986 | 972 | 914 | 857 | 853 | n/a |

Equivalent Full Load Hours for Cooling (EFLHcooling) for Existing Buildings:

| Building Type | Cooling EFLH Existing Buildings |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Assembly | 573 | 519 | 704 | 763 | 754 | OpenStudio |
| Assisted Living | 577 | 531 | 766 | 847 | 858 | OpenStudio |
| Auto Dealership | 575 | 503 | 670 | 732 | 739 | OpenStudio |
| Childcare/Pre-School | 799 | 625 | 883 | 957 | 1,158 | OpenStudio |
| College | 849 | 877 | 1,047 | 1,155 | 1,150 | OpenStudio |
| Convenience Store | 219 | 147 | 288 | 342 | 347 | OpenStudio |
| Drug Store | 913 | 882 | 1,047 | 1,124 | 1,042 | OpenStudio |
| Elementary School | 516 | 497 | 717 | 743 | 670 | OpenStudio |
| Emergency Services | 1,419 | 1,503 | 1,867 | 2,085 | 2,040 | OpenStudio |
| Garage | 846 | 843 | 1,097 | 1,369 | 1,260 | eQuest |
| Grocery | 451 | 400 | 607 | 663 | 619 | OpenStudio |
| Healthcare Clinic | 1,730 | 1,761 | 2,047 | 2,189 | 1,730 | OpenStudio |
| High School | 524 | 475 | 738 | 831 | 763 | OpenStudio |
| Hospital - CAV no econ | 2,005 | 1,999 | 2,244 | 2,470 | 2,447 | OpenStudio |
| Hospital - CAV econ | 1,278 | 1,316 | 1,621 | 1,771 | 1,770 | OpenStudio |
| Hospital - VAV econ | 1,627 | 1,661 | 1,842 | 1,984 | 2,079 | OpenStudio |
| Hospital - FCU | 3,297 | 3,180 | 3,340 | 3,514 | 3,463 | OpenStudio |
| Hotel/Motel | 1,180 | 1,111 | 1,403 | 1,585 | 1,642 | OpenStudio |
| Hotel/Motel - Common | 1,212 | 1,176 | 1,435 | 1,596 | 1,631 | OpenStudio |
| Hotel/Motel - Guest | 1,108 | 1,086 | 1,389 | 1,519 | 1,559 | OpenStudio |
| Manufacturing Facility | 18 | 27 | 58 | 52 | 61 | OpenStudio |
| MF - High Rise | 1,451 | 1,341 | 1,890 | 2,001 | 1,353 | OpenStudio |
| MF - High Rise - Common | 924 | 900 | 1,183 | 1,178 | 837 | OpenStudio |
| MF - High Rise - Residential | 1,404 | 1,288 | 1,843 | 1,962 | 1,326 | OpenStudio |
| MF - Mid Rise | 1,065 | 1,142 | 1,444 | 1,599 | 1,369 | OpenStudio |
| Movie Theater | 584 | 528 | 671 | 752 | 716 | OpenStudio |
| Office - High Rise - CAV no econ | 1,382 | 1,342 | 1,444 | 1,700 | 1,620 | OpenStudio |
| Office - High Rise - CAV econ | 928 | 916 | 1,102 | 1,250 | 1,218 | OpenStudio |
| Office - High Rise - VAV econ | 984 | 890 | 993 | 1,232 | 1,018 | OpenStudio |
| Office - High Rise - FCU | 1,274 | 1,522 | 1,293 | 1,437 | 1,489 | OpenStudio |
| Office - Low Rise | 935 | 956 | 1,197 | 1,150 | 1,197 | OpenStudio |
| Office - Mid Rise | 900 | 906 | 1,042 | 1,136 | 1,014 | OpenStudio |
| Religious Building | 161 | 163 | 219 | 236 | 238 | OpenStudio |
| Restaurant | 999 | 1,011 | 1,295 | 1,387 | 1,382 | OpenStudio |
| Retail - Department Store | 712 | 645 | 845 | 942 | 966 | OpenStudio |
| Retail - Strip Mall | 793 | 797 | 1,076 | 1,096 | 1,084 | OpenStudio |
| Warehouse | 226 | 246 | 351 | 380 | 396 | OpenStudio |
| Unknown | 708 | 700 | 890 | 947 | 923 | n/a |

Equivalent Full Load Hours for Cooling (EFLHcooling) for New Construction:

| Building Type | Cooling EFLH New Construction |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Assembly | 674 | 667 | 837 | 890 | 808 | OpenStudio |
| Assisted Living | 865 | 868 | 1,169 | 1,214 | 1,059 | OpenStudio |
| Auto Dealership | 724 | 654 | 849 | 934 | 962 | OpenStudio |
| Childcare/Pre-School | 620 | 577 | 756 | 768 | 646 | OpenStudio |
| College | 713 | 717 | 897 | 1,040 | 910 | OpenStudio |
| Convenience Store | 121 | 103 | 209 | 246 | 249 | OpenStudio |
| Drug Store | 1,015 | 1,007 | 1,165 | 1,229 | 1,250 | OpenStudio |
| Elementary School | 632 | 634 | 841 | 838 | 769 | OpenStudio |
| Emergency Services | 955 | 1,057 | 1,349 | 1,236 | 1,200 | OpenStudio |
| Grocery | 36 | 45 |  | 76 |  | 64 |  | 77 |  | OpenStudio |  |
| Healthcare Clinic | 1,237 | 1,243 | 1,421 | 1,582 | 1,571 | OpenStudio |
| High School | 557 | 578 |  | 792 |  | 887 |  | 905 |  | OpenStudio |  |
| Hospital - CAV no econ | 2,206 | 2,201 | 2,430 | 2,644 | 2,634 | OpenStudio |
| Hospital - CAV econ | 1,188 | 1,230 | 1,530 | 1,647 | 1,757 | OpenStudio |
| Hospital - VAV econ | 778 | 846 | 939 | 1,011 | 1,471 | OpenStudio |
| Hospital - FCU | 2,264 | 2,227 | 2,281 | 2,344 | 2,546 | OpenStudio |
| Hotel/Motel | 1,517 | 1,529 | 1,583 | 1,641 | 1,470 | OpenStudio |
| Hotel_Motel_Common | 1,085 | 1,185 | 1,329 | 1,364 | 1,464 | OpenStudio |
| Hotel_Motel_Guest | 811 | 825 | 931 | 927 | 797 | OpenStudio |
| Manufacturing Facility | 13 | 17 | 40 | 23 | 35 | OpenStudio |
| MF - High Rise | 1,982 | 1,906 | 2,258 | 2,359 | 1,681 | OpenStudio |
| MF - High Rise - Common | 948 | 949 | 1,208 | 1,247 | 898 | OpenStudio |
| MF - High Rise - Residential | 1,962 | 1,894 | 2,271 | 2,374 | 1,676 | OpenStudio |
| MF - Mid Rise | 1,716 | 1,791 | 2,077 | 2,129 | 1,811 | OpenStudio |
| Movie Theater | 297 | 266 | 396 | 424 | 434 | OpenStudio |
| Office - High Rise - CAV no econ | 1,225 | 1,195 | 1,402 | 1,538 | 1,490 | OpenStudio |
| Office - High Rise - CAV econ | 928 | 925 | 1,162 | 1,224 | 1,182 | OpenStudio |
| Office - High Rise - VAV econ | 518 | 549 | 690 | 715 | 572 | OpenStudio |
| Office - High Rise - FCU | 1,129 | 1,098 |  | 1,172 |  | 1,240 |  | 1,168 |  | OpenStudio |  |
| Office - Low Rise | 625 | 642 | 793 | 779 | 623 | OpenStudio |
| Office - Mid Rise | 699 | 757 |  | 885 |  | 916 |  | 750 |  | OpenStudio |  |
| Religious Building | 188 | 179 |  | 218 |  | 248 |  | 269 |  | OpenStudio |  |
| Restaurant | 980 | 970 |  | 1,234 |  | 1,313 |  | 1,311 |  | OpenStudio |  |
| Retail - Department Store | 732 | 661 | 848 | 931 | 954 | OpenStudio |
| Retail - Strip Mall | 554 | 521 | 745 | 721 | 716 | OpenStudio |
| Warehouse | 172 | 192 | 275 | 235 | 287 | OpenStudio |
| Unknown | 608 | 617 | 772 | 797 | 754 | n/a |

### Variable Speed Drives for HVAC Pumps and Cooling Tower Fans

###### Description

This measure is applied to variable speed drives (VSD) which are installed on the following HVAC system applications: chilled water pump, hot water pumps and cooling tower fans.  There is a separate measure for HVAC supply and return fans. All other VSD applications require custom analysis by the program administrator. The VSD will modulate the speed of the motor when it does not need to run at full load. Since the power of the motor is proportional to the cube of the speed for these types of applications, significant energy savings will result.

This measure is not applicable for:

- Cooling towers, chilled or hot water pumps with any process load.

- VSD installation in existing cooling towers with 2-speed motors. (current code requires 2-speed motors for cooling towers with motors greater than 7.5 HP)

- VSD installation in new cooling towers with motors greater than 7.5 HP

This measure was developed to be applicable to the following program types: TOS, RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The VSD is applied to a motor which does not have a VSD. This measure is not applicable for replacing failed VSDs. The application must have a variable load and installation is to include the necessary controls.  Savings are based on application of VSDs to a range of baseline load conditions including no control, inlet guide vanes, outlet guide vanes and throttling valves.

###### Definition of Baseline Equipment

The time of sale baseline is a new motor installed without a VSD or other methods of control.  Retrofit baseline is an existing motor operating as is. Retrofit baselines may or may not include guide vanes, throttling valves or other methods of control.  This information shall be collected from the customer.

Installations of new equipment with VSDs which are required by IECC, state energy code as adopted by the State of Illinois are not eligible for incentives. As code requirements and adoption can differ from municipality to municipality, the user should verify which version of code is applicable given these constraints.

Note, IECC 2021 became effective statewide as of 1/1/2024. IECC 2018 is the requisite code for any projects with permitting dates spanning July 1, 2019 to the 12/31/2023. Prior to July 1, 2019, IECC 2015 is the applicable code.

###### Deemed Lifetime of Efficient Equipment

The expected measure life for HVAC application is 15 years;  measure life for process is 15 years.

###### Deemed Measure Cost

Customer provided costs will be used when available.  Default measure costs are noted below for up to 75 hp motors.  Custom costs must be gathered from the customer for motor sizes not listed below.

| HP | Cost |
| --- | --- |
| 5 HP | $2,250 |
| 7.5 HP | $2,517 |
| 10 HP | $2,784 |
| 15 HP | $3,318 |
| 20 HP | $3,852 |
| 25 HP | $4,386 |
| 50 HP | $6,573 |
| 75 HP | $8,532 |

###### Loadshape

Loadshape C42 - VFD - Boiler feedwater pumps <10 HP

Loadshape C43 - VFD - Chilled water pumps <10 HP

Loadshape C44 - VFD Boiler circulation pumps <10 HP

Loadshape C48 - VFD Boiler draft fans <10 HP

Loadshape C49 - VFD Cooling Tower Fans <10 HP

###### Coincidence Factor

The demand savings factor (DSF) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh  = BHP /EFFi * Hours * ESF

Where:

BHP 	= System Brake Horsepower

(Nominal motor HP * Motor load factor)

Motors are assumed to have a load factor of 65% for calculating kW if actual values cannot be determined.  Custom load factor may be applied if known.

EFFi 	= Motor efficiency, installed. Actual motor efficiency shall be used to calculate kW.  If not known, default motor is a NEMA Premium Efficiency, ODP, 4-pole/1800 RPM fan motor, as detailed in the table below.

NEMA Premium Efficiency Motors Default Efficiencies

| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | # of Poles |  |  | # of Poles |  |  |
|  | 6 | 4 | 2 | 6 | 4 | 2 |
|  | Speed (RPM) |  |  | Speed (RPM) |  |  |
|  | 1200 | 1800 Default | 3600 | 1200 | 1800 | 3600 |
| 1 | 0.825 | 0.855 | 0.770 | 0.825 | 0.855 | 0.770 |
| 1.5 | 0.865 | 0.865 | 0.840 | 0.875 | 0.865 | 0.840 |
| 2 | 0.875 | 0.865 | 0.855 | 0.885 | 0.865 | 0.855 |
| 3 | 0.885 | 0.895 | 0.855 | 0.895 | 0.895 | 0.865 |
| 5 | 0.895 | 0.895 | 0.865 | 0.895 | 0.895 | 0.885 |
| 7.5 | 0.902 | 0.910 | 0.885 | 0.910 | 0.917 | 0.895 |
| 10 | 0.917 | 0.917 | 0.895 | 0.910 | 0.917 | 0.902 |
| 15 | 0.917 | 0.930 | 0.902 | 0.917 | 0.924 | 0.910 |
| 20 | 0.924 | 0.930 | 0.910 | 0.917 | 0.930 | 0.910 |
| 25 | 0.930 | 0.936 | 0.917 | 0.930 | 0.936 | 0.917 |
| 30 | 0.936 | 0.941 | 0.917 | 0.930 | 0.936 | 0.917 |
| 40 | 0.941 | 0.941 | 0.924 | 0.941 | 0.941 | 0.924 |
| 50 | 0.941 | 0.945 | 0.930 | 0.941 | 0.945 | 0.930 |
| 60 | 0.945 | 0.950 | 0.936 | 0.945 | 0.950 | 0.936 |
| 75 | 0.945 | 0.950 | 0.936 | 0.945 | 0.954 | 0.936 |
| 100 | 0.950 | 0.954 | 0.936 | 0.950 | 0.954 | 0.941 |
| 125 | 0.950 | 0.954 | 0.941 | 0.950 | 0.954 | 0.950 |
| 150 | 0.954 | 0.958 | 0.941 | 0.958 | 0.958 | 0.950 |
| 200 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.954 |
| 250 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.958 |
| 300 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 350 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 400 | 0.958 | 0.958 | 0.958 | 0.958 | 0.962 | 0.958 |
| 450 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |
| 500 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |

Hours	= Default hours are provided for HVAC applications which vary by HVAC application and building type. When available (provided via Energy Management Software or metered), actual hours should be used.

| Building Type | Heating Run Hours | Cooling Run Hours | Model Source |
| --- | --- | --- | --- |
| Assembly |  | 5149 |  | 3945 |  | OpenStudio |  |
| Assisted Living |  | 8760 |  | 4731 |  | OpenStudio |  |
| Auto Dealership | 4215 | 2776 | OpenStudio |
| Childcare/Pre-School | 5632 | 3041 | OpenStudio |
| College | 6391 | 4332 | OpenStudio |
| Convenience Store |  | 8184 |  | 3497 |  | OpenStudio |  |
| Drug Store | 3084 | 3130 | OpenStudio |
| Elementary School | 6031 | 2809 | OpenStudio |
| Emergency Services |  | 4511 |  | 4513 |  | OpenStudio |  |
| Garage | 4849 | 2102 | eQuest |
| Grocery | 8760 | 4076 | OpenStudio |
| Healthcare Clinic | 7908 | 4564 | OpenStudio |
| High School |  | 4629 |  | 3104 |  | OpenStudio |  |
| Hospital - VAV econ | 8271 | 8709 | OpenStudio |
| Hospital - CAV econ | 2456 | 7006 | OpenStudio |
| Hospital - CAV no econ | 2456 | 8670 | OpenStudio |
| Hospital - FCU | 4292 | 8760 | OpenStudio |
| Manufacturing Facility |  | 4770 |  | 1973 |  | OpenStudio |  |
| MF - High Rise | 7443 | 7942 | OpenStudio |
| MF - Mid Rise | 6717 | 7834 | OpenStudio |
| Hotel/Motel - Guest | 8282 | 8675 | OpenStudio |
| Hotel/Motel - Common | 7975 | 8508 | OpenStudio |
| Movie Theater |  | 6902 |  | 2891 |  | OpenStudio |  |
| Office - High Rise - VAV econ | 5585 | 3343 | OpenStudio |
| Office - High Rise - CAV econ |  | 2605 |  | 6041 |  | OpenStudio |  |
| Office - High Rise - CAV no econ | 2605 | 8405 | OpenStudio |
| Office - High Rise - FCU | 4498 | 8158 | OpenStudio |
| Office - Low Rise | 6123 | 7118 | OpenStudio |
| Office - Mid Rise | 6099 | 4372 | OpenStudio |
| Religious Building |  | 5890 |  | 2554 |  | OpenStudio |  |
| Restaurant | 3256 | 4448 | OpenStudio |
| Retail - Department Store |  | 4352 |  | 2882 |  | OpenStudio |  |
| Retail - Strip Mall |  | 5705 |  | 3245 |  | OpenStudio |  |
| Warehouse |  | 6296 |  | 3262 |  | OpenStudio |  |
| Unknown | 5778 | 4377 | n/a |

The type of hours to apply depends on the VFD application, according to the table below.

| Application | Hours Type |
| --- | --- |
| Hot Water Pump | Heating |
| Chilled Water Pump | Cooling |
| Cooling Tower Fan | Cooling |

ESF	= Energy savings factor varies by VFD application.  Units are kW/HP.

| Application | ESF |
| --- | --- |
| Hot Water Pump | 0.249 |
| Chilled Water Pump | 0.081 |
| Cooling Tower Fan | 0.502 |

###### Summer Coincident Peak Demand Savings

ΔkW  =BHP/EFFi * DSF

Where:

DSF 	= Demand Savings Factor varies by VFD application. Units are kW/HP. Values listed below are based on typical peak load for the listed application.

| Application | DSF |
| --- | --- |
| Hot Water Pump | 0 |
| Chilled Water Pump | 0 |
| Cooling Tower Fan | 0.407 |

###### Fossil Fuel Impact Descriptions and Calculation

There are no expected fossil fuel impacts for this measure.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-VSDHP-V11-250101

###### Review Deadline: 1/1/2028

### Variable Speed Drives for HVAC Supply and Return Fans

###### Description

This measure is applied to variable speed drives (VSD) which are installed on HVAC supply fans and return fans. The VSD will modulate the speed of the motor when it does not need to run at full load. Since the power of the motor is proportional to the cube of the speed for these types of applications, significant energy savings will result.

Note this measure should be used for evaluating control system modifications. If combined with the evaluation of a more efficient over a baseline fan, measure ‘4.4.53 HVAC Supply, Return and Exhaust Fans – Fan Energy Index’ should be utilized. The FEPnew value from measure 4.4.53 should be used to replace the 0.746×HP×LFηmotor term in this measure.

This measure was developed to be applicable to the following program types: TOS, RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The VSD is applied to a motor which does not have a VSD. The application must have a variable load and installation is to include the necessary controls.  Savings are based on application of VSDs to a range of baseline load conditions including no control, inlet guide vanes, outlet guide vanes and throttling valves.

###### Definition of Baseline Equipment

The time of sale baseline is a new motor installed without a VSD or other methods of control.  Retrofit baseline is an existing motor operating as is.  Retrofit baselines may or may not include guide vanes, throttling valves or other methods of control.  This information shall be collected from the customer.

Installations of new equipment with VSDs which are required by IECC, state energy code as adopted by the State of Illinois are not eligible for incentives. As code requirements and adoption can differ from municipality to municipality, the user should verify which version of code is applicable given these constraints.

Note, IECC 2021 became effective statewide on 1/1/2024. IECC 2018 is the requisite code for any projects with permitting dates spanning July 1, 2019 to 12/31/2023. Prior to July 1, 2019, IECC 2015 is the applicable code.

###### Deemed Lifetime of Efficient Equipment

The expected measure life for all VSDs is 15 years.

###### Deemed Measure Cost

Customer-provided costs will be used when available.  Default measure costs are noted below for up to 75 hp motors. Custom costs must be gathered from the customer for motor sizes not listed below.

| HP | Cost |
| --- | --- |
| 5 HP | $2,585 |
| 15 HP | $4,483 |
| 25 HP | $6,524 |
| 50 HP | $11,239 |
| 75 HP | $15,834 |

###### Loadshape

Loadshape C39 - VFD - Supply fans <10 HP

Loadshape C40 - VFD - Return fans <10 HP

Loadshape C41 - VFD - Exhaust fans <10 HP

###### Coincidence Factor

The demand savings factor (DSF) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

0.746×HP×LFηmotor

| kWhBase = | 0.746×HP×LFηmotor×RHRSBase×0%100%%FF×PLRBase |
| --- | --- |
| kWhRetrofit = | 0.746×HP×LFηmotor×RHRSbase×0%100%(%FF×PLRRetrofit) |
| ∆kWhfan = | kWhBase-kWhRetrofit |
| ∆kWhtotal = | ∆kWhfan×(1+IEenergy) |

Where:

kWhBase 	= Baseline annual energy consumption (kWh/yr)

kWhRetrofit 	= Retrofit annual energy consumption (kWh/yr)

∆kWhfan 	= Fan-only annual energy savings

∆kWhtotal 	= Total project annual energy savings

0.746 		= Conversion factor for HP to kWh

HP		= Nominal horsepower of controlled motor

LF 		= Load Factor; Motor Load at Fan Design CFM (Default = 65%)

ηmotor		= Installed nominal/nameplate motor efficiency

Default motor is a NEMA Premium Efficiency, ODP, 4-pole/1800 RPM fan motor

NEMA Premium Efficiency Motors Default Efficiencies

| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | # of Poles |  |  | # of Poles |  |  |
|  | 6 | 4 | 2 | 6 | 4 | 2 |
|  | Speed (RPM) |  |  | Speed (RPM) |  |  |
|  | 1200 | 1800 Default | 3600 | 1200 | 1800 | 3600 |
| 1 | 0.825 | 0.855 | 0.770 | 0.825 | 0.855 | 0.770 |
| 1.5 | 0.865 | 0.865 | 0.840 | 0.875 | 0.865 | 0.840 |
| 2 | 0.875 | 0.865 | 0.855 | 0.885 | 0.865 | 0.855 |
| 3 | 0.885 | 0.895 | 0.855 | 0.895 | 0.895 | 0.865 |
| 5 | 0.895 | 0.895 | 0.865 | 0.895 | 0.895 | 0.885 |
| 7.5 | 0.902 | 0.910 | 0.885 | 0.910 | 0.917 | 0.895 |
| 10 | 0.917 | 0.917 | 0.895 | 0.910 | 0.917 | 0.902 |
| 15 | 0.917 | 0.930 | 0.902 | 0.917 | 0.924 | 0.910 |
| 20 | 0.924 | 0.930 | 0.910 | 0.917 | 0.930 | 0.910 |
| 25 | 0.930 | 0.936 | 0.917 | 0.930 | 0.936 | 0.917 |
| 30 | 0.936 | 0.941 | 0.917 | 0.930 | 0.936 | 0.917 |
| 40 | 0.941 | 0.941 | 0.924 | 0.941 | 0.941 | 0.924 |
| 50 | 0.941 | 0.945 | 0.930 | 0.941 | 0.945 | 0.930 |
| 60 | 0.945 | 0.950 | 0.936 | 0.945 | 0.950 | 0.936 |
| 75 | 0.945 | 0.950 | 0.936 | 0.945 | 0.954 | 0.936 |
| 100 | 0.950 | 0.954 | 0.936 | 0.950 | 0.954 | 0.941 |
| 125 | 0.950 | 0.954 | 0.941 | 0.950 | 0.954 | 0.950 |
| 150 | 0.954 | 0.958 | 0.941 | 0.958 | 0.958 | 0.950 |
| 200 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.954 |
| 250 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.958 |
| 300 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 350 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 400 | 0.958 | 0.958 | 0.958 | 0.958 | 0.962 | 0.958 |
| 450 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |
| 500 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |

RHRSBase	= Annual operating hours for fan motor based on building type

Default hours are provided for HVAC applications which vary by HVAC application and building type. When available (provided via Energy Management Software or metered),  actual hours should be used.

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly |  | 8760 |  | OpenStudio |  |
| Assisted Living |  | 8760 |  | OpenStudio |  |
| Auto Dealership | 6050 | OpenStudio |
| Childcare/Pre-School | 6884 | OpenStudio |
| College | 8760 | OpenStudio |
| Convenience Store |  | 8184 |  | OpenStudio |  |
| Drug Store | 0 | OpenStudio |
| Elementary School | 8760 | OpenStudio |
| Emergency Services |  | 0 |  | OpenStudio |  |
| Garage |  | 7357 |  | eQuest |  |
| Grocery | 8760 | OpenStudio |
| Healthcare Clinic | 8760 | OpenStudio |
| High School |  | 8760 |  | OpenStudio |  |
| Hospital - VAV econ | 8760 | OpenStudio |
| Hospital - CAV econ | 8760 | OpenStudio |
| Hospital - CAV no econ | 8760 | OpenStudio |
| Hospital - FCU | 8760 | OpenStudio |
| Manufacturing Facility |  | 6118 |  | OpenStudio |  |
| MF - High Rise | 8760 | OpenStudio |
| MF - Mid Rise | 8760 | OpenStudio |
| Hotel/Motel - Guest | 8760 | OpenStudio |
| Hotel/Motel - Common | 8760 | OpenStudio |
| Movie Theater |  | 7206 |  | OpenStudio |  |
| Office - High Rise - VAV econ | 7066 | OpenStudio |
| Office - High Rise - CAV econ |  | 8628 |  | OpenStudio |  |
| Office - High Rise - CAV no econ | 8628 | OpenStudio |
| Office - High Rise - FCU | 8752 | OpenStudio |
| Office - Low Rise | 8116 | OpenStudio |
| Office - Mid Rise |  | 8535 |  | OpenStudio |  |
| Religious Building |  | 6663 |  | OpenStudio |  |
| Restaurant | 8222 | OpenStudio |
| Retail - Department Store |  | 6225 |  | OpenStudio |  |
| Retail - Strip Mall |  | 6977 |  | OpenStudio |  |
| Warehouse |  | 6801 |  | OpenStudio |  |
| Unknown |  | 8057 |  | n/a |  |

%FF		= Percentage of run-time spent within a given flow fraction range

Default Fan Duty Cycle Based on 2012 ASHRAE Handbook; HVAC Systems and Equipment, page 45.11, Figure 12.

| Flow Fraction (% of design cfm) | Percent of Time at Flow Fraction |
| --- | --- |
| 0% to 10% | 0.0% |
| 10% to 20% | 1.0% |
| 20% to 30% | 5.5% |
| 30% to 40% | 15.5% |
| 40% to 50% | 22.0% |
| 50% to 60% | 25.0% |
| 60% to 70% | 19.0% |
| 70% to 80% | 8.5% |
| 80% to 90% | 3.0% |
| 90% to 100% | 0.5% |

PLRBase	= Part load ratio for a given flow fraction range based on the baseline flow control type

PLRRetrofit	= Part load ratio for a given flow fraction range based on the retrofit flow control type

| Control Type | Flow Fraction |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% |
| No Control or Bypass Damper | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Discharge Dampers | 0.46 | 0.55 | 0.63 | 0.70 | 0.77 | 0.83 | 0.88 | 0.93 | 0.97 | 1.00 |
| Outlet Damper, BI & Airfoil Fans | 0.53 | 0.53 | 0.57 | 0.64 | 0.72 | 0.80 | 0.89 | 0.96 | 1.02 | 1.05 |
| Inlet Damper Box | 0.56 | 0.60 | 0.62 | 0.64 | 0.66 | 0.69 | 0.74 | 0.81 | 0.92 | 1.07 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.53 | 0.56 | 0.57 | 0.59 | 0.60 | 0.62 | 0.67 | 0.74 | 0.85 | 1.00 |
| Inlet Vane Dampers | 0.38 | 0.40 | 0.42 | 0.44 | 0.48 | 0.53 | 0.60 | 0.70 | 0.83 | 0.99 |
| Outlet Damper, FC Fans | 0.22 | 0.26 | 0.30 | 0.37 | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06 |
| Eddy Current Drives | 0.17 | 0.20 | 0.25 | 0.32 | 0.41 | 0.51 | 0.63 | 0.76 | 0.90 | 1.04 |
| Inlet Guide Vane, FC Fans | 0.21 | 0.22 | 0.23 | 0.26 | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04 |
| VFD with duct static pressure controls | 0.09 | 0.10 | 0.11 | 0.15 | 0.20 | 0.29 | 0.41 | 0.57 | 0.76 | 1.01 |
| VFD with low/no duct static pressure | 0.05 | 0.06 | 0.09 | 0.12 | 0.18 | 0.27 | 0.39 | 0.55 | 0.75 | 1.00 |

Provided below is the resultant values based upon the defaults provided above:

| Control Type | 0%100%%FF×PLRBase |
| --- | --- |
| No Control or Bypass Damper | 1.00 |
| Discharge Dampers | 0.80 |
| Outlet Damper, BI & Airfoil Fans | 0.78 |
| Inlet Damper Box | 0.69 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.63 |
| Inlet Vane Dampers | 0.53 |
| Outlet Damper, FC Fans | 0.53 |
| Eddy Current Drives | 0.49 |
| Inlet Guide Vane, FC Fans | 0.39 |
| VFD with duct static pressure controls | 0.30 |
| VFD with low/no duct static pressure | 0.27 |

IEenergy		= HVAC interactive effects factor for energy (default = 15.7%)

###### Summer Coincident Peak Demand Savings

| kWBase = | 0.746×HP×LFηmotor×PLRBase, FFpeak |
| --- | --- |
| kWRetrofit = | 0.746×HP×LFηmotor× PLRRetrofit, FFpeak |
| ∆kWfan = | kWBase-kWRetrofit |
| ∆kWtotal = | ∆kWfan×(1+IEdemand) |

Where:

kWBase 		= Baseline summer coincident peak demand (kW)

kWRetrofit 		= Retrofit summer coincident peak demand (kW)

∆kWfan 		= Fan-only summer coincident peak demand impact

∆kWtotal 		= Total project summer coincident peak demand impact

PLRBase,FFpeak	= The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the baseline flow control type (default average flow fraction during peak period = 90%)

PLRRetrofit,FFpeak	= The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the retrofit flow control type (default average flow fraction during peak period = 90%)

IEdemand	= HVAC interactive effects factor for summer coincident peak demand
 (default = 15.7%)

###### Fossil Fuel Impact Descriptions and Calculation

There are no expected fossil fuel impacts for this measure.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-VSDF-V11-260101

###### Review Deadline: 1/1/2029

### Notched V Belts for HVAC Systems

###### Measure Description

This measure is for replacement of smooth v-belts in non-residential package and split HVAC systems with notched v-belts or for installing new equipment with synchronous belts instead of smooth v-belts.  Typically there is a v-belt between the motor and the supply air fan and/or return air fan in larger package and split HVAC systems (RTU).

In general there are two styles of grooved v-belts, notched and synchronous.  The DOE defines each as follows;

Notched V-Belts - A notched belt has grooves or notches that run perpendicular to the belt’s length, which reduces the bending resistance of the belt. Notched belts can use the same pulleys as cross-section standard V-belts. They run cooler, last longer, and are about 2% more efficient than standard V-belts.

Synchronous Belts - Synchronous belts (also called cogged, timing, positive-drive, or high-torque drive belts) are toothed and require the installation of mating grooved sprockets. These belts operate with a consistent efficiency of 98% and maintain their efficiency over a wide load range.

- Smooth v-belts are usually referred to in five basic groups:

- “L” belts are low end belts that are for small, fractional horsepower motors and these are not used in RTUs.

- “A” and “B” belts are the two types typically used in RTUs.  The “A” belt is a ½ inch width by 5/16 inch thickness and the “B” belt is larger, 21/32 inch wide and 12/32 inch thick so it can carry more power.  V-belts come in a wide variety of lengths where 20 to 100 inches is typical.

- “C” and “D” belts are primarily for industrial applications with high power transmission requirements.

- V-belts are provided by various vendors.  The notched version of these belts typically have an “X” added to the designation.  For this HVAC fans notched v-belt Replacement measure, only the “A” and “B” v-belts are considered.  A typical “A” v-belt is replaced by a notched “AX” v-belt and a “B” is replaced by a “BX.”  In general, smooth v-belts have an efficiency of 90% to 98% while notched v-belts have an efficiency of 95% to 98%.  Because notched v-belts are more flexible they work with smaller diameter pulleys and they have less resistance to bending.  Lower bending resistance increases the power transmission efficiency, lowers the waste heat, and allows the belt to last longer than a smooth belt.

Three research papers   show that the notched v-belt efficiency is 2% to 5% better than a typical smooth v-belt.  A fourth paper by USDOE’s Energy Efficiency and Renewable Energy  group reviewed most of the earlier literature and recommended using a conservative 2% efficiency improvement for energy savings for calculations.

For this measure it is assumed that upgrading a standard smooth v-belt with a new notched v-belt will result in a fan energy reduction of 2%.

###### Definition of Efficient Equipment

For the Notched V-Belt characterization to apply, the Efficient Equipment is HVAC RTUs that have notched v-belts installed on the supply and/or return air fans.  This can be done as a retrofit, TOS, or NC project.

For the Synchronous Belt characterization to apply, the Efficient Equipment is HVAC RTUs that have synchronous belts installed on the supply and/or return air fans. This can be done as a TOS or NC project. Retrofit projects can also claim savings, but costs should be verified independently (typically the cost of installing synchronous belts as a retrofit is not economically viable).

###### Definition of Baseline Equipment

The Baseline Equipment is HVAC RTUs that have smooth v-belts installed on the supply and/or return air fans (i.e., RTU does not already have a notched v-belt installed).

###### Deemed Lifetime of Efficient Equipment

A v-belt has a life based on fan run hours which varies by building type based primarily on occupancy schedule because the fans are required by code to operate continuously during occupied hours.  The supply and return fans will also run a few hours during unoccupied hours for heating and cooling as needed.  For the notched v-belt EUL calculation, the default hours in the following table are used for a variety of building types and HVAC applications.

EUL 	= Belt Life / Occupancy Hours per year

Where:

Belt Life 				= 24,000 hours

Occupancy Hours per year 	= values from Table below

The notched v-belt measure EUL is summarized by building type in the following table.

Notched v-belt Effective Useful Life (EUL)

| Building Type | Total Fan Run Hours | EUL (Years) | Model Source |
| --- | --- | --- | --- |
| Assembly |  | 8760 |  | 2.7 |  |  |  | OpenStudio |
| Assisted Living |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Auto Dealership |  | 6050 |  | 4.0 |  | OpenStudio |  |  |
| Childcare/Pre-School |  | 6884 |  | 3.5 |  | OpenStudio |  |  |
| College |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Convenience Store |  | 8184 |  | 2.9 |  | OpenStudio |  |  |
| Drug Store | 7156 | 3.4 | OpenStudio |
| Elementary School | 8760 | 2.7 | OpenStudio |
| Emergency Services | 8760 | 2.7 | OpenStudio |
| Garage | 7357 | 3.3 | eQuest |
| Grocery |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Healthcare Clinic |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| High School |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Hospital - VAV econ |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Hospital - CAV econ |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Hospital - CAV no econ |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Hospital - FCU |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Manufacturing Facility |  | 6118 |  | 3.9 |  | OpenStudio |  |  |
| MF - High Rise | 8760 | 2.7 | OpenStudio |
| MF - Mid Rise | 8760 | 2.7 | OpenStudio |
| Hotel/Motel - Guest |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Hotel/Motel - Common |  | 8760 |  | 2.7 |  | OpenStudio |  |  |
| Movie Theater |  | 7206 |  | 3.3 |  | OpenStudio |  |  |
| Office - High Rise - VAV econ |  | 7066 |  | 3.4 |  | OpenStudio |  |  |
| Office - High Rise - CAV econ |  | 8628 |  | 2.8 |  | OpenStudio |  |  |
| Office - High Rise - CAV no econ |  | 8628 |  | 2.8 |  | OpenStudio |  |  |
| Office - High Rise - FCU |  | 8752 |  | 2.7 |  | OpenStudio |  |  |
| Office - Low Rise |  | 8116 |  | 3.0 |  | OpenStudio |  |  |
| Office - Mid Rise |  | 8535 |  | 2.8 |  | OpenStudio |  |  |
| Religious Building |  | 6663 |  | 3.6 |  | OpenStudio |  |  |
| Restaurant |  | 8222 |  | 2.9 |  | OpenStudio |  |  |
| Retail - Department Store |  | 6225 |  | 3.9 |  | OpenStudio |  |  |
| Retail - Strip Mall |  | 6977 |  | 3.4 |  | OpenStudio |  |  |
| Warehouse | 6801 | 3.5 | OpenStudio |
| Unknown |  | 8057 |  | 3.0 |  | n/a |  |  |

The lifetime of a synchronous belt system is the same as the lifetime of the equipment it is installed on because it is a permanent upgrade, involving the installation of toothed pulleys. Typical HVAC RTU lifetime is 15 years, which applies to synchronous belts as well. This is not to suggest that the actual belt component has an equivalent lifetime because they do require replacement. However, their O&M cost savings (derived from not having to tension, etc.) are assumed to offset the replacement cost of the belt, resulting in a net cost of zero. As a result, neither a separate lifetime nor O&M savings are quantified for synchronous belts and lifetime can therefore be considered as the lifetime of the equipment they’re installed on because it would not be possible to install a traditional or notched belt on the synchronous pulleys.

###### Deemed Measure Cost

Costs of belts and pulleys are known to vary substantially based on belt length and pulley diameter. Two cost estimations are provided below; a fully deemed approach for applications such as an upstream program where limited information is known, and a semi-custom approach that is useful when more accurate cost estimates are desired.

Fully Deemed:

A review of the Grainger online pricing for “A,” “B,” “AX,” and “BX” v-belts revealed the incremental costs to upgrade to notched v-belts as summarized in the table below:

Notched V-belt Incremental Cost Summary

| Smooth V-Belt Industry Number | Outside Length (Inches) | Dayton Smooth V-Belt* | Notched V-belt Industry Number | Dayton Notched v-belt* | Price Increase | % Increase |
| --- | --- | --- | --- | --- | --- | --- |
| A30 (Item # 1A095) | 32 | $10.38 | AX30 (Item # 3GWU4) | $14.64 | $4.26 | 41% |
| B29 (Item # 6L208) | 32 | $14.38 | BX29 (Item # 5TXL4) | $20.80 | $6.42 | 45% |
| * Pricing based on Dayton Belts as found on Grainger Website 10/30/14 |  |  |  |  |  |  |

Note that the incremental cost for notched V-Belts assumes that the notched belt is purchased and installed instead of a smooth v-belt. There is no difference in the cost of installation, only the material.

Synchronous Belt Incremental Cost Summary

| Smooth V-Belt Industry Number | Smooth belt system Price* | Synchronous Belt Industry Number | Synchronous System Price* | Price Difference |
| --- | --- | --- | --- | --- |
| Belt A30 (Item # 1A095) | $10.38 | Belt 1DHL5 (Item # 322L050) | $15.37 | $4.99 |
| Gearbelt pulley BK47 (Item #5UHD5) | $47.98 | Gearbelt sprocket GTR-36G-8M-12 (Item # 2UWH6) | $113.91 | $65.93 |
| * Costs based on Grainger pricing. |  |  |  |  |

Incremental cost for a NC or TOS project is $136.85. This is the price of synchronous equipment (belt, two sprockets) subtract v-belt equipment (belt, two pulleys). Labor cost is assumed to be equal in the baseline and efficient cases.

Incremental cost for a RF project is $380.49. This is the price of synchronous equipment and labor to install it (not including a trip charge), less the cost of the v-belt (but not the pulleys).

Semi-Custom

Use the following relationships along with NC, TOS and RF assumptions outlined above to estimate semi-custom costs.

| Component | Type | Cost Function (per inch) | Inch Measurement |
| --- | --- | --- | --- |
| Standard V-Belt | A | $0.28/in + $0.96 | Outside Length |
| Standard V-Belt | B | $0.29/in + $9.15 | Outside Length |
| Standard Pulley | A, B, AX, BX | $11.85/in - $9.47 | Outside Diameter |
| Notched Belt | AX | $0.36/in + $1.07 | Outside Length |
| Notched Belt | BX | $0.49/in + $2.33 | Outside Length |
| Synchronous Belt | 1/2 inch | $0.58/in + $8.90 | Pitch Length |
| Synchronous Belt | 1 inch | $0.26/in + $5.67 | Pitch Length |
| Synchronous Pulley | for use with 1/2 inch belt | $27.20/in - $21.19 | Pitch Diameter |
| Synchronous Pulley | for use with 1 inch belt | $25.04/in - $27.23 | Pitch Diameter |

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

Loadshape C05 - Commercial Electric Heating and Cooling

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh  = kWconnectedkWconnected* Hours * ESF

Where:

kWConnected 	=kW of equipment is calculated using motor efficiency

= (HP * 0.746 kW/HP* Load Factor)/Motor Efficiency

Load Factor 	=Motors are assumed to have a load factor of 80% for calculating KW if actual values cannot be determined.  Custom load factor may be applied if known.

Motor Efficiency 	= Actual motor efficiency shall be used to calculate KW.  If not known a value from the motor efficiency refrence tables below should be used.  Default motor is a NEMA Premium Efficiency, ODP, 4-pole/1800 RPM fan motor.

| Baseline Motor Efficiencies (EPACT) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
|  | # of Poles |  |  |  |  |  |
|  | 6 | 4 | 2 | 6 | 4 | 2 |
|  | Speed (RPM) |  |  |  |  |  |
|  | 1200 | 1800 | 3600 | 1200 | 1800 | 3600 |
| 1/8 | - | 44.00% | - | - | - | - |
| 1/6 | 57.50% | 62.00% | - | - | - | - |
| 1/4 | 68.00% | 68.00% | - | 68.00% | 64.00% | - |
| 1/3 | 70.00% | 70.00% | 72.00% | 70.00% | 68.00% | 72.00% |
| 1/2 | 78.50% | 80.00% | 68.00% | 72.00% | 74.00% | 68.00% |
| 3/4 | 77.00% | 78.50% | 74.00% | 77.00% | 75.50% | 74.00% |
| 1 | 80.00% | 82.50% | 75.50% | 80.00% | 82.50% | 75.50% |
| 1.5 | 84.00% | 84.00% | 82.50% | 85.50% | 84.00% | 82.50% |
| 2 | 85.50% | 84.00% | 84.00% | 86.50% | 84.00% | 84.00% |
| 3 | 86.50% | 86.50% | 84.00% | 87.50% | 87.50% | 85.50% |
| 5 | 87.50% | 87.50% | 85.50% | 87.50% | 87.50% | 87.50% |
| 7.5 | 88.50% | 88.50% | 87.50% | 89.50% | 89.50% | 88.50% |
| 10 | 90.20% | 89.50% | 88.50% | 89.50% | 89.50% | 89.50% |
| 15 | 90.20% | 91.00% | 89.50% | 90.20% | 91.00% | 90.20% |
| 20 | 91.00% | 91.00% | 90.20% | 90.20% | 91.00% | 90.20% |
| 25 | 91.70% | 91.70% | 91.00% | 91.70% | 92.40% | 91.00% |

| Efficient Motor Efficiencies (NEMA Premium) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
|  | # of Poles |  |  | # of Poles |  |  |
|  | 2 | 4 | 6 | 2 | 4 | 6 |
|  | Speed (RPM) |  |  | Speed (RPM) |  |  |
|  | 1200 | 1800 (Default) | 3600 | 1200 | 1800 | 3600 |
| 0.125 * | - | 44.00% | - | - | - | - |
| 1/6 | 57.50% | 62.00% | - | - | - | - |
| 1/4 | 68.00% | 68.00% | - | 68.00% | 64.00% | - |
| 1/3 | 70.00% | 70.00% | 72.00% | 70.00% | 68.00% | 72.00% |
| 1/2 | 78.50% | 80.00% | 68.00% | 72.00% | 74.00% | 68.00% |
| 3/4 | 77.00% | 78.50% | 74.00% | 77.00% | 75.50% | 74.00% |
| 1 | 82.50% | 85.50% | 77.00% | 82.50% | 85.50% | 77.00% |
| 1.5 | 86.50% | 86.50% | 84.00% | 87.50% | 86.50% | 84.00% |
| 2 | 87.50% | 86.50% | 85.50% | 88.50% | 86.50% | 85.50% |
| 3 | 88.50% | 89.50% | 85.50% | 89.50% | 89.50% | 86.50% |
| 5 | 89.50% | 89.50% | 86.50% | 89.50% | 89.50% | 88.50% |
| 7.5 | 90.20% | 91.00% | 88.50% | 91.00% | 91.70% | 89.50% |
| 10 | 91.70% | 91.70% | 89.50% | 91.00% | 91.70% | 90.20% |
| 15 | 91.70% | 93.00% | 90.20% | 91.70% | 92.40% | 91.00% |
| 20 | 92.40% | 93.00% | 91.00% | 91.70% | 93.00% | 91.00% |
| 25 | 93.00% | 93.60% | 91.70% | 93.00% | 93.60% | 91.70% |

Hours 	= When available, actual hours should be used. If actual hours are not available, default hours are provided in table below for HVAC fan operation, which varies by building type:

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly |  | 8760 |  | OpenStudio |  |
| Assisted Living |  | 8760 |  | OpenStudio |  |
| Auto Dealership | 6050 | OpenStudio |
| Childcare/Pre-School | 6884 | OpenStudio |
| College | 8760 | OpenStudio |
| Convenience Store |  | 8184 |  | OpenStudio |  |
| Drug Store | 0 | OpenStudio |
| Elementary School | 8760 | OpenStudio |
| Emergency Services | 0 | OpenStudio |
| Garage | 7357 | eQuest |
| Grocery | 8760 | OpenStudio |
| Healthcare Clinic | 8760 | OpenStudio |
| High School |  | 8760 |  | OpenStudio |  |
| Hospital - VAV econ | 8760 | OpenStudio |
| Hospital - CAV econ | 8760 | OpenStudio |
| Hospital - CAV no econ | 8760 | OpenStudio |
| Hospital - FCU | 8760 | OpenStudio |
| Manufacturing Facility |  | 6118 |  | OpenStudio |  |
| MF - High Rise | 8760 | OpenStudio |
| MF - Mid Rise | 8760 | OpenStudio |
| Hotel/Motel - Guest | 8760 | OpenStudio |
| Hotel/Motel - Common | 8760 | OpenStudio |
| Movie Theater |  | 7206 |  | OpenStudio |  |
| Office - High Rise - VAV econ | 7066 | OpenStudio |
| Office - High Rise - CAV econ |  | 8628 |  | OpenStudio |  |
| Office - High Rise - CAV no econ | 8628 | OpenStudio |
| Office - High Rise - FCU | 8752 | OpenStudio |
| Office - Low Rise | 8116 | OpenStudio |
| Office - Mid Rise |  | 8535 |  | OpenStudio |  |
| Religious Building |  | 6663 |  | OpenStudio |  |
| Restaurant | 8222 | OpenStudio |
| Retail - Department Store |  | 6225 |  | OpenStudio |  |
| Retail - Strip Mall |  | 6977 |  | OpenStudio |  |
| Warehouse |  | 6801 |  | OpenStudio |  |
| Unknown |  | 8057 |  | n/a |  |

ESF 		= Energy Savings Factor, the ESF for notched v-belt Installation is assumed to be 2%

= the ESF for notched Synchronous Belt Installation is assumed to be 3.1%

For example, a notched v-belt installation in an low rise office building RTU with a 5 HP NEMA premium efficiency motor  using the default hours of operation, motor load and 89.5% motor efficiency;

ΔkWh	= kWconnected* Hours * ESF

= ((HP * 0.746 kW/HP* Load Factor)/Motor Efficiency) * Hours * ESF

= ((5 HP * 0.746 kW/HP* 80%) / 89.5%) * 6288 * 2%

= 419 kWh Savings

Summer Coincident Peak Demand Savings

ΔkW  = kWconnectedkWconnected* ESF * CF

Where:

kWConnected  	= kW of equipment is calculated using motor efficiency.

= (HP *0 .746 kW/HP* Load Factor)/Motor Efficiency

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Variables as provided above

For example, an office building RTU with a 5 HP NEMA premium efficiency motor using the default motor load and 89.5% motor efficiency;

ΔkWSSP	= kWconnected* ESF * CF

= ((HP * 0.746 kW/HP* Load Factor)/Motor Efficiency) * ESF * CF

= ((5 HP * 0.746 kW/HP* 80%) / 89.5%) * 2% * 0.913

= 0.0609 kW Savings

###### Fossil Fuel Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-NVBE-V06-210101

###### Review Deadline: 1/1/2027

### HVAC Supply, Return and Exhaust Fans – Fan Energy Index

###### Description

The Fan Energy Index (FEI) is a new fan efficiency metric that allows for the comparison of different fans at application specific operating conditions. This is a significant improvement over the current Fan Efficiency Grade metric, which is defined at a rated condition. FEI is incorporated in ASHRAE 90.1-2019 and IECC-2021. These codes set the baseline FEI as 1.0 for constant speed fan operation and 0.95 for variable speed fan operation. More efficient fans will have FEI greater than these values. It is only applicable to stand-alone fans, and not for fans embedded in packaged equipment. This measure results in fan energy savings compared to a baseline scenario of an existing fan’s FEI or code minimum FEI for a new fan.

Note this measure should be used for evaluating more efficient over baseline fans with the same control system. Measure 4.4.26 should be utilized to evaluate control system modifications. When combining the two measures, the FEPNew value should be used to replace the 0.746×HP×LFηmotor term in Measure 4.4.26 Variable Speed Drive for HVAC Supply and Return Fans.

This measure serves the market for commercial and industrial buildings.

This measure was developed to be applicable to the following program types: TOS, NC, and EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to exceed the efficiency requirements defined by the program.

###### Definition of Baseline Equipment

For Time of Sale (TOS):  The baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit or sale (if unknown assume IECC 2021).

For New Construction (NC): The baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit (if unknown assume IECC 2021). As code requirements and adoption can differ from municipality to municipality, the user should verify which version of code is applicable given these constraints.

For Early Replacement (EREP): The baseline equipment is assumed to be the existing fan.

###### Deemed Lifetime of Efficient Equipment

For variable speed fans, the expected measure life is 15 years.

For constant speed fans, the expected measure life is 18 years for centrifugal housed and unhoused fans. The expected measure life is 25 years for all other fan types.

###### Deemed Measure Cost

Actual measure costs should be used if available. Default measure costs are noted below for fans with FEI greater than 1.0. These costs are established at an FEI of 1.2. To calculate the cost for a fan with different FEI, prorate the default cost with the actual FEI (see example).

TOS and NC

| Fan Type | Cost ($/hp) |  |
| --- | --- | --- |
|  | Small (< 10 hp) | Large (>= 10 hp) |
| Axial Cylindrical Housed | $264 | $87 |
| Panel | $29 | $10 |
| Centrifugal Housed | $199 | $55 |
| Centrifugal Unhoused | $76 | $18 |
| Inline and Mixed Flow | $297 | $97 |
| Radial | $119 | $33 |
| Power Roof Ventilator | $140 | $42 |

EREP

| Fan Type | Cost ($/hp) |  |
| --- | --- | --- |
|  | Small (< 10 hp) | Large (>= 10 hp) |
| Axial Cylindrical Housed | $3,218 | $1,068 |
| Panel | $319 | $104 |
| Centrifugal Housed | $1,381 | $382 |
| Centrifugal Unhoused | $827 | $195 |
| Inline and Mixed Flow | $2,301 | $751 |
| Radial | $1,570 | $434 |
| Power Roof Ventilator | $1,536 | $460 |

For example, the default deemed measure cost of installing a new construction, centrifugal housed, 5 hp fan with FEI = 1.3 is:

Deemed Measure Costs ($) = $199 per hp *5 hp * (1.3 / 1.2) = $1,078

###### Loadshape

Loadshape C39 – VFD – Supply fans <10 HP

Loadshape C40 – VFD – Return fans <10 HP

Loadshape C41 – VFD – Exhaust fans <10 HP

###### Coincidence Factor

The demand savings factor (DSF) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Note this measure should be used for evaluating more efficient over baseline fans with the same control system. Measure 4.4.26 Variable Speed Drives for HVAC Supply and Return Fans should be utilized to evaluate control system modifications. When combining the two measures, the FEPNew value should be used to replace the 0.746×HP×LFηmotor term in Measure 4.4.26.

| ∆kWhfan = | FEPNew*(FEINewFEIBase-1)*RHRS*0%100%%FF*PLR |
| --- | --- |
| ∆kWhtotal = | ∆kWhfan*(1+IEenergy) |

Where:

∆kWhfan	= Fan-only annual energy savings (kWh)

FEPNew		= Fan Electrical Power of new fan at 100% flow fraction (kW)

FEINew		= Fan Energy Index of new fan at 100% flow fraction (-)

FEIBase 		= Fan Energy Index of baseline fan at 100% flow fraction (-)

TOS and NC: 	FEIbase is defined per IECC.

= 0.95 for Variable Speed Fan

= 1.0 for Constant Speed Fan

EREP: 		FEIbase is defined as existing fan efficiency. If unknown, use:

| Fan Type | Drive Type |  |  |
| --- | --- | --- | --- |
|  | Variable Speed – Belt | Constant Speed – Belt | Constant Speed – Direct |
| Axial Cylindrical Housed | 0.88 | 0.88 | 0.97 |
| Panel | 0.95 | 0.95 | 0.88 |
| Centrifugal Housed | 0.92 | 0.92 | 0.92 |
| Centrifugal Unhoused | 0.94 | 0.94 | 1.03 |
| Inline and Mixed Flow | 0.79 | 0.79 | 0.77 |
| Radial | 0.81 | 0.81 | 0.94 |
| Power Roof Ventilator | 0.82 | 0.82 | 0.76 |

RHRS		= Annual operating hours for fan based on building type

Default hours are provided for HVAC applications which vary by HVAC application and building type. When available (provided via Energy Management Software or metered), actual hours should be used.

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly |  | 8760 |  | OpenStudio |  |
| Assisted Living |  | 8760 |  | OpenStudio |  |
| Auto Dealership | 6050 | OpenStudio |
| Childcare/Pre-School | 6884 | OpenStudio |
| College | 8760 | OpenStudio |
| Convenience Store |  | 8184 |  | OpenStudio |  |
| Drug Store | 0 | OpenStudio |
| Elementary School | 8760 | OpenStudio |
| Emergency Services |  | 0 |  | OpenStudio |  |
| Garage | 7357 | eQuest |
| Grocery | 8760 | OpenStudio |
| Healthcare Clinic | 8760 | OpenStudio |
| High School |  | 8760 |  | OpenStudio |  |
| Hospital – VAV econ | 8760 | OpenStudio |
| Hospital – CAV econ | 8760 | OpenStudio |
| Hospital – CAV no econ | 8760 | OpenStudio |
| Hospital – FCU | 8760 | OpenStudio |
| Manufacturing Facility |  | 6118 |  | OpenStudio |  |
| MF – High Rise | 8760 | OpenStudio |
| MF – Mid Rise | 8760 | OpenStudio |
| Hotel/Motel – Guest | 8760 | OpenStudio |
| Hotel/Motel – Common | 8760 | OpenStudio |
| Movie Theater |  | 7206 |  | OpenStudio |  |
| Office – High Rise – VAV econ | 7066 | OpenStudio |
| Office – High Rise – CAV econ |  | 8628 |  | OpenStudio |  |
| Office – High Rise – CAV no econ | 8628 | OpenStudio |
| Office – High Rise – FCU | 8752 | OpenStudio |
| Office – Low Rise | 8116 | OpenStudio |
| Office – Mid Rise |  | 8535 |  | OpenStudio |  |
| Religious Building |  | 6663 |  | v |  |
| Restaurant | 8222 | OpenStudio |
| Retail – Department Store |  | 6225 |  | OpenStudio |  |
| Retail – Strip Mall |  | 6977 |  | OpenStudio |  |
| Warehouse |  | 6801 |  | OpenStudio |  |
| Unknown |  | 8057 |  | n/a |  |

%FF 		= Percentage of run-time spent within a given flow fraction range

| Flow Fraction (% of design cfm) | Percent of Time at Flow Fraction |
| --- | --- |
| 0% to 10% | 0.0% |
| 10% to 20% | 1.0% |
| 20% to 30% | 5.5% |
| 30% to 40% | 15.5% |
| 40% to 50% | 22.0% |
| 50% to 60% | 25.0% |
| 60% to 70% | 19.0% |
| 70% to 80% | 8.5% |
| 80% to 90% | 3.0% |
| 90% to 100% | 0.5% |

PLR		= Part load ratio for a given flow fraction range

| Control Type | Flow Fraction |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% |
| No Control or Bypass Damper | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Discharge Dampers | 0.46 | 0.55 | 0.63 | 0.70 | 0.77 | 0.83 | 0.88 | 0.93 | 0.97 | 1.00 |
| Outlet Damper, BI & Airfoil Fans | 0.53 | 0.53 | 0.57 | 0.64 | 0.72 | 0.80 | 0.89 | 0.96 | 1.02 | 1.05 |
| Inlet Damper Box | 0.56 | 0.60 | 0.62 | 0.64 | 0.66 | 0.69 | 0.74 | 0.81 | 0.92 | 1.07 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.53 | 0.56 | 0.57 | 0.59 | 0.60 | 0.62 | 0.67 | 0.74 | 0.85 | 1.00 |
| Inlet Vane Dampers | 0.38 | 0.40 | 0.42 | 0.44 | 0.48 | 0.53 | 0.60 | 0.70 | 0.83 | 0.99 |
| Outlet Damper, FC Fans | 0.22 | 0.26 | 0.30 | 0.37 | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06 |
| Eddy Current Drives | 0.17 | 0.20 | 0.25 | 0.32 | 0.41 | 0.51 | 0.63 | 0.76 | 0.90 | 1.04 |
| Inlet Guide Vane, FC Fans | 0.21 | 0.22 | 0.23 | 0.26 | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04 |
| VFD with duct static pressure controls | 0.09 | 0.10 | 0.11 | 0.15 | 0.20 | 0.29 | 0.41 | 0.57 | 0.76 | 1.01 |
| VFD with low/no duct static pressure | 0.05 | 0.06 | 0.09 | 0.12 | 0.18 | 0.27 | 0.39 | 0.55 | 0.75 | 1.00 |

Provided below are the resultant values based upon the defaults provided above:

| Control Type | 0%100%%FF×PLR |
| --- | --- |
| No Control or Bypass Damper | 1.00 |
| Discharge Dampers | 0.80 |
| Outlet Damper, BI & Airfoil Fans | 0.78 |
| Inlet Damper Box | 0.69 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.63 |
| Inlet Vane Dampers | 0.53 |
| Outlet Damper, FC Fans | 0.53 |
| Eddy Current Drives | 0.49 |
| Inlet Guide Vane, FC Fans | 0.39 |
| VFD with duct static pressure controls | 0.30 |
| VFD with low/no duct static pressure | 0.27 |

∆kWhtotal	= Total project annual energy savings (kWh)

IEenergy		= HVAC interactive effects factor for energy (default = 15.7%)

###### Summer Coincident Peak Demand Savings

| ∆kWfan = | FEPNew*FEINewFEIBase-1*PLRFFpeak |
| --- | --- |
| ∆kWtotal = | ∆kWfan*(1+IEdemand) |

Where:

∆kWfan		= Fan-only summer coincident peak demand impact (kW)

PLRFfpeak	= The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the baseline flow control type (default average flow fraction during peak period = 90%)

∆kWtotal		= Total project summer coincident peak demand impact (kW)

IEdemand		= HVAC interactive effects factor summer coincident peak demand (default = 15.7%)

###### Fossil Fuel Savings

There are no expected fossil fuel impacts for this measure.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-FFEI-V04-250101

###### Review Deadline: 1/1/2028

###### Waterless HVAC Condensate Trap

###### Description

Traditional, waterfilled P-traps are commonly installed on commercial HVAC condensate drainpipes to prevent air from leaking into or out of the HVAC system, but they rely on water remaining present in the curve of the trap at all times to prevent air infiltration. When traditional P-traps dry out in the winter or shoulder seasons due to the lack of condensate production, they allow air to enter or leave the HVAC system, resulting in energy loss as the replacement air must be conditioned. In commercial HVAC systems, this energy loss can become significant and lead to increased energy bills for building operators. A cost-effective means of reducing this energy loss is by replacing traditional P-traps with waterless HVAC condensate traps that seal using the HVAC system’s air pressure instead of water, eliminating the concern of dried out P-traps.

Waterless HVAC condensate traps installed on commercial HVAC systems minimize air leakage from condensate drainpipes, while also minimizing the space needed for installation when compared to traditional P-traps. Laboratory testing of waterless HVAC condensate traps demonstrated that, across all tested models, pressure levels, and pipe diameters, air leakage rates consistently remained below 1 SCFM. Notably, 90% of the tests recorded leakage rates under 0.5 SCFM. These findings support that waterless HVAC condensate traps provide a highly effective alternative to traditional P-traps, significantly reducing air leakage in dry condensate drainpipes. These waterless condensate traps can function in both positive and negative pressure environments, and are adaptable to different system configurations, pressure ranges, and drainpipe connection types. When condensate forms, buoyancy lifts the float valve from the valve seat, allowing the condensate to drain properly

A variety of commercial packaged rooftop units (RTUs) HVAC units may qualify for this measure, including packaged rooftop units (RTUs), makeup air units (MAUs), and outdoor air handling units (AHUs).. The measure applies to commercial HVAC applications for retrofitting P-trap condensate traps with a properly sized waterless condensate trap with the exception of HVAC systems with a condensing gas-fired heating systems owing to condensate management in the heating season. It is assumed that the same HVAC system serves the building cooling and heating loads.

This measure was developed to be applicable to the following program types: TOS, RF, EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is a waterless HVAC condensate trap designed for installation on a commercial HVAC system’s condensate drainpipe.

###### Definition of Baseline Equipment

The baseline equipment consists of a traditional, waterfilled P-trap, which is used as a condensate trap in commercial HVAC condensate drainpipes to prevent air leakage. This measure does not apply to existing P-traps that are sufficiently tall to hold condensate for several months.

###### Deemed Lifetime of Efficient Equipment

Specific data on the lifespan of HVAC condensate traps is limited, as their durability can be influenced by factors such as maintenance practices, water quality, and environmental conditions. The estimated useful life is assumed to be 5 years.

###### Deemed Measure Cost

Actual measure costs should be used if available. If actual costs are not available, the deemed measure costs listed below may be used.

| Waterless Condensate Trap Type | Cost per Trap (Material Only) | Per-Unit Labor Cost (Trap Replacement) |
| --- | --- | --- |
| Negative Pressure Trap | $81.6 | $25 |
| Positive Pressure Trap | $96.5 | $25 |

###### Loadshape

Loadshape C04 – Commercial Electric Heating

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

Any conditioned air leaked to the environment through a condensate drainpipe will need to be replaced by outdoor air that is conditioned, and the magnitude of the energy loss is driven by the temperature difference between the leaked air temperature and the outdoor air temperature. The leaked air temperature depends on the orientation of the cooling coil (with condensate drain) relative to the gas furnace heat exchanger and the HVAC supply fan. For systems where the cooling coil is upstream of the fan and the gas furnace, the leaked air temperature is estimated to be the same as the indoor air temperature at 75°F for all times the fan is running (heat and fan modes). For systems where the cooling coil and gas furnace are downstream of the fan, the leaked air temperature is estimated to be 120°F during heating mode and 75°F during fan only mode.

A leak would occur during the heating season if the depth of the standing water in the p-trap is not sufficient to withstand the pressure difference between the air handler and outdoors, which is more likely to occur during heating season due to evaporation of water in the trap and the lack of production of condensate during winter. The impact of a condensate drain leak during cooling season is unlikely during the summer when condensate is bring produced.

###### Electric Energy Savings

Electric Energy Savings are only applicable if the heating system is electric. For gas-fired heating systems, please refer to the FOSSIL FUEL SAVINGS section for energy savings.

∆kWh = (kWhheating + kWhfan)

Where:

∆kWhheating = heating energy saved in kWh during heating operation

∆kWhfan       = heating energy saved in kWh during ventilation operation during heating season

| kWhheating=v×*60 ×* EFLHheat ×* ρ ×* cp ×*∆Theat ×*tons 3,412*ηHeat |  |
| --- | --- |
| kWhfan=v×*60 ×*EFLHfanheat ×* ρ ×* cp ×*∆Tfan ×*tons 3,412*ηHeat |  |

v                       = estimated leak rate for the HVAC system in CFM/ton. Use actual if known.

| System Tonnage | External Static Pressure (in WC) | Leak Rate (cfm/ton) |
| --- | --- | --- |
| Under20 tons | 1” | 0.6 |
|  | 2” | 0.9 |
|  | 3” | 1.0 |
| 20 - 50 tons | 1” | 0.6 |
|  | 2” | 0.8 |
|  | 3” | 1.0 |

60                    = conversion from minutes to hour

EFLHheat          =  Equivalent Full Load Hours for heating in Existing Buildings are provided in section 4.4 HVAC

End Use

ηHeat		=  Efficiency of electric heating system, as deemed from table below

| System Type | Cooling Capacity of Equipment | Age of Equipment | HSPF Estimate | η (Effective COP Estimate) (HSPF/3.413) |
| --- | --- | --- | --- | --- |
| Heat Pump | All | Before 2009 | 6.8 | 2.0 |
|  | < 65,000 Btu/h | 2009 - 2017 | 7.7 | 2.3 |
|  |  | 2017 on | 8.2 | 2.40 |
|  | ≥ 65,000 Btu/h and < 135,000 Btu/h | 2010 on | 11.3 | 3.3 |
|  | ≥ 135,000 Btu/h and < 240,000 Btu/h | 2010 on | 10.9 | 3.2 |
|  | ≥ 240,000 Btu/h and < 760,000 Btu/h | 2010 on | 10.9 | 3.2 |
| Resistance | N/A | N/A | N/A | 1 |

EFLHfanheat     = Total Fan Run hours during heating season in fan mode when burner is off

= 0.5 * Total Fan Run Hours- EFLHheat

= Assuming the heating season is from October to March

Total Fan Run Hours = Default hours are provided for HVAC applications which vary by HVAC application and building type in the following table. When available, actual hours should be used

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly |  | 8760 |  | OpenStudio |  |
| Assisted Living |  | 8760 |  | OpenStudio |  |
| Auto Dealership | 6050 | OpenStudio |
| Childcare/Pre-School | 6884 | OpenStudio |
| College | 8760 | OpenStudio |
| Convenience Store |  | 8184 |  | OpenStudio |  |
| Drug Store | 0 | OpenStudio |
| Elementary School | 8760 | OpenStudio |
| Emergency Services |  | 0 |  | OpenStudio |  |
| Garage |  | 7357 |  | eQuest |  |
| Grocery | 8760 | OpenStudio |
| Healthcare Clinic | 8760 | OpenStudio |
| High School |  | 8760 |  | OpenStudio |  |
| Hospital - VAV econ | 8760 | OpenStudio |
| Hospital - CAV econ | 8760 | OpenStudio |
| Hospital - CAV no econ | 8760 | OpenStudio |
| Hospital - FCU | 8760 | OpenStudio |
| Manufacturing Facility |  | 6118 |  | OpenStudio |  |
| MF - High Rise | 8760 | OpenStudio |
| MF - Mid Rise | 8760 | OpenStudio |
| Hotel/Motel - Guest | 8760 | OpenStudio |
| Hotel/Motel - Common | 8760 | OpenStudio |
| Movie Theater |  | 7206 |  | OpenStudio |  |
| Office - High Rise - VAV econ | 7066 | OpenStudio |
| Office - High Rise - CAV econ |  | 8628 |  | OpenStudio |  |
| Office - High Rise - CAV no econ | 8628 | OpenStudio |
| Office - High Rise - FCU | 8752 | OpenStudio |
| Office - Low Rise | 8116 | OpenStudio |
| Office - Mid Rise |  | 8535 |  | OpenStudio |  |
| Religious Building |  | 6663 |  | OpenStudio |  |
| Restaurant | 8222 | OpenStudio |
| Retail - Department Store |  | 6225 |  | OpenStudio |  |
| Retail - Strip Mall |  | 6977 |  | OpenStudio |  |
| Warehouse |  | 6801 |  | OpenStudio |  |
| Unknown |  | 8057 |  | n/a |  |

ρ                    = density of the leaked air in lb/ft3

= 0.08 (lb/ft3) at 1 atmosphere pressure and approximately 30-40°F

cp                  = specific heat in BTU/(lb °F)

= 0.24 (BTU/lb) at 1 atmosphere pressure and 32°F

∆Theat        = Theat - T Avg_Htg_OAT

=  average difference between the leaked air temperature and the outside air temperature

in °F for the hours in which fan and heating operates during the heating season

Theat                = Supply Air Temperature of the gas heating system.

= Use 120°F when cooling coil and furnace are downstream of fan. Use 75°F when cooling coil

is upstream of fan and furnace. Use actual if known.

TAvg_Htg_OAT       = Deemed average ambient air temperature over the heating season based on climate zone

| Climate Zone | Heating Season Avg OA DBT |
| --- | --- |
| 1 - Rockford | 29.4 degF |
| 2 - Chicago | 34.2 degF |
| 3 - Springfield | 27.4 degF |
| 4 - Belleville | 38.4 degF |
| 5 - Marion | 31.4 degF |

∆Tfan          = Tfan - T Avg_Htg_OAT

Tfan                 = Return Air Temperature in the Air Handler. Use the indoor air temperature setpoint.

= 75°F or actual if known.

tons               = Nominal rated tonnage of HVAC system. Use actual.

3,412             = conversion from Btu to kWh

###### Summer Coincident Peak Demand Savings

N/A

###### Fossil Fuel Savings

The annual gas heating energy saved per year is:

ΔTherms = (ΔThermsheating + ΔThermsfan)

| ΔThermsheating=v×*60* EFLHheat ×* ρ ×* cp ×*∆Theat ×*tons 100,000*ηHeat |  |
| --- | --- |
| ΔThermsfan=v×*60*EFLHfan ×* ρ ×* cp ×*∆Tfan ×*tons 100,000*ηHeat |  |

Where:

ΔThermsheating = heating energy saved in therms during heating operation

ΔThermsfan         = heating energy saved in therms during ventilation operation in heating season

100,000           = conversion from Btu to therms

ηHeat	 =  heating system efficiency

= custom, if unknown:

80% for hot water boilers, except multifamily

79% for steam boilers, except multifamily

83.2% for furnaces (including roof-top units), except multifamily use 80.2%

Please see the previous section for a definition of parameters and guidance on default values to be used.

For example, a 30-ton RTU with the cooling coil and gas furnace downstream of the fan, rated for 3” WC external static pressure and with gas-fired heating in an elementary school in Chicago has a waterless condensate trap retrofitted in place of a p-trap:

Δtherms		= ((1.1*60*1,603*0.08*0.24*(120-34.2)*30) + (1.1*60*279.5*0.08*0.24*(75-34.2)*30))/100,000*0.8

= (5,228,621.8 + 433,519.3)/(100,000 * 0.8)

= 70.8 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-WCNDT-V01-260101

###### Review Deadline: 1/1/2028

###### Review Deadline: 1/1/2028

## Lighting End Use

The commercial lighting measures use a standard set of variables for hours of use, waste heat factors, coincident factors and HVAC interaction effects.  For ease of review, the table is included here and referenced in each measure.

OpenStudio models have been developed using the most appropriate DOE protypical models, as described in NREL’s “U.S. Department of Energy Commercial Reference Building Models of the National Building Stock”, as the initial base, and calibrated align with ComStock/ResStock or CBECS/RECS energy use intensity. These models are used to estimate the fixture operating hours (except where noted), waste heat and coincidence factors.

The key building characteristics of the OpenStudio models and a description of the calibration adjustments is provided in “OS Model Details and Adjustments.xls”.  Documents and all models are available on the SharePoint site.

Note where a measure installation is within a building or application that does not fit with any of the defined building types below, the user should apply custom assumptions where it is reasonable to estimate them, else the building of best fit should be utilized.

In addition, deemed baseline fixture wattages (extracted from the 2026 Pennsylvania Technical Reference Manual, Appendix C, ‘Lighting Audit & Design Tool for Commercial and Industrial Projects’, accessed 07/2025) is provided in “Lighting Deemed Fixture Wattage.xls” within the 4.5 Lighting folder in the Reference Documents section of the Illinois TRM Sharepoint site.

| Building/Space Type |  | Fixture Annual Operating Hours |  | Screw based bulb Annual Operating hours |  |  |  | Waste Heat Cooling Energy WHFe |  | Waste Heat Cooling DemandWHFd |  |  |  | Coinci-dence Factor CF | Waste Heat Gas Heating IFTherms |  | Waste Heat Electric Resistance Heating IFkWh |  | Waste Heat Electric Heat Pump Heating IFkWh |  | Model Source |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Agriculture – Chicken Broilers |  | 3,251 |  | 3,251 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.76 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Agriculture – Chicken Breeders |  | 4,606 |  | 4,606 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.95 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Agriculture – Chicken Layers |  | 4,914 |  | 4,914 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.95 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Agriculture – Turkey Hens |  | 2,231 |  | 2,231 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.76 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Agriculture – Turkey Toms |  | 5,351 |  | 5,351 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.95 | 0.000 |  | 0.000 |  | 0.000 |  | na |  |  |
| Agriculture – Turkey Breeder Hens |  | 4,396 |  | 4,396 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.95 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Agriculture – Turkey Breeder Toms |  | 5,446 |  | 5,446 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.95 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Agriculture – Dairy Long Day Lighting |  | 6,205 |  | 6,205 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.95 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Assisted Living |  | 4,652 |  | 5,950 |  |  |  | 1.07 |  | 1.13 |  |  |  | 0.54 | 0.029 |  | 0.672 |  | 0.292 |  | OpenStudio |  |  |
| Auto Dealership |  | 3,474 |  | 2,935 |  |  |  | 1.30 |  | 1.83 |  |  |  | 0.67 | 0.015 |  | 0.349 |  | 0.152 |  | OpenStudio |  |  |
| Childcare/Pre-School |  | 3,233 |  | 2,860 |  |  |  | 1.08 |  | 1.77 |  |  |  | 0.59 | 0.020 |  | 0.472 |  | 0.205 |  | OpenStudio |  |  |
| College |  | 3,395 |  | 2,588 |  |  |  | 1.28 |  | 1.26 |  |  |  | 0.61 | 0.010 |  | 0.226 |  | 0.098 |  | OpenStudio |  |  |
| Convenience Store |  | 3,750 |  | 3,650 |  |  |  | 1.02 |  | 1.22 |  |  |  | 0.66 | 0.018 |  | 0.416 |  | 0.181 |  | OpenStudio |  |  |
| Drug Store |  | 5,116 |  | 2,935 |  |  |  | 1.23 |  | 1.92 |  |  |  | 0.65 | 0.016 |  | 0.379 |  | 0.165 |  | OpenStudio |  |  |
| Elementary School |  | 3,038 |  | 2,118 |  |  |  | 1.19 |  | 1.80 |  |  |  | 0.61 | 0.030 |  | 0.701 |  | 0.305 |  | OpenStudio |  |  |
| Emergency Services |  | 5,274 |  | 3,088 |  |  |  | 1.07 |  | 1.19 |  |  |  | 0.47 | 0.004 |  | 0.094 |  | 0.041 |  | OpenStudio |  |  |
| Garage |  | 3,401 |  | 3,540 |  |  |  | 1.08 |  | 1.16 |  |  |  | 0.82 | 0.000 |  | 0.000 |  | 0.000 |  | eQuest |  |  |
| Garage, 24/7 lighting |  | 8,766 |  | 8,766 |  |  |  | 1.08 |  | 1.16 |  |  |  | 1.00 | 0.000 |  | 0.000 |  | 0.000 |  | eQuest |  |  |
| Grocery |  | 5,468 |  | 3,650 |  |  |  | 1.02 |  | 1.22 |  |  |  | 0.65 | 0.019 |  | 0.449 |  | 0.195 |  | OpenStudio |  |  |
| Healthcare Clinic |  | 3,890 |  | 4,207 |  |  |  | 0.97 |  |  | 1.72 |  |  | 0.63 | 0.003 |  | 0.080 |  | 0.035 |  |  | OpenStudio |  |  |
| High School |  | 3,038 |  | 2,327 |  |  |  | 1.05 |  | 2.00 |  |  |  | 0.66 | 0.021 |  | 0.494 |  | 0.215 |  | OpenStudio |  |  |
| Hospital - CAV no econ |  | 7,616 |  | 4,207 |  |  |  | 1.42 |  | 1.66 |  |  |  | 0.52 | 0.011 |  | 0.248 |  | 0.108 |  | OpenStudio |  |  |
| Hospital - CAV econ |  | 7,616 |  | 4,207 |  |  |  | 1.31 |  | 1.66 |  |  |  | 0.52 | 0.010 |  | 0.245 |  | 0.107 |  | OpenStudio |  |  |
| Hospital - VAV econ |  | 7,616 |  | 4,207 |  |  |  | 1.22 |  | 1.32 |  |  |  | 0.52 | 0.008 |  | 0.179 |  | 0.078 |  | OpenStudio |  |  |
| Hospital - FCU |  | 7,616 |  | 4,207 |  |  |  | 1.25 |  | 1.49 |  |  |  | 0.52 | 0.000 |  | 0.002 |  | 0.001 |  | OpenStudio |  |  |
| Manufacturing Facility |  | 4,618 |  | 2,629 |  |  |  | 1.00 |  | 1.09 |  |  |  | 0.68 | 0.008 |  | 0.178 |  | 0.077 |  | OpenStudio |  |  |
| MF - High Rise - Common |  | 4,824 |  | 5,950 |  |  |  | 1.01 |  | 1.00 |  |  |  | 0.43 | 0.001 |  | 0.028 |  | 0.012 |  | OpenStudio |  |  |
| MF - Mid Rise - Common |  | 4,263 |  | 5,950 |  |  |  | 1.11 |  | 0.97 |  |  |  | 0.50 | 0.019 |  | 0.443 |  | 0.193 |  | OpenStudio |  |  |
| Hotel/Motel - Guest |  | 2,390 |  | 777 |  |  |  | 1.22 |  | 1.35 |  |  |  | 0.49 | 0.023 |  | 0.535 |  | 0.232 |  | OpenStudio |  |  |
| Hotel/Motel - Common |  | 6,138 |  | 4,542 |  |  |  | 1.19 |  | 1.47 |  |  |  | 0.47 | 0.019 |  | 0.454 |  | 0.197 |  | OpenStudio |  |  |
| Movie Theater |  | 2,592 |  | 5,475 |  |  |  | 1.16 |  | 1.66 |  |  |  | 0.62 | 0.000 |  | 0.009 |  | 0.004 |  | OpenStudio |  |  |
| Office - High Rise - CAV no econ |  | 3,216 |  | 3,088 |  |  |  | 1.43 |  | 1.48 |  |  |  | 0.73 | 0.007 |  | 0.172 |  | 0.075 |  | OpenStudio |  |  |
| Office - High Rise - CAV econ |  | 3,216 |  | 3,088 |  |  |  | 1.31 |  | 1.48 |  |  |  | 0.73 | 0.007 |  | 0.167 |  | 0.072 |  | OpenStudio |  |  |
| Office - High Rise - VAV econ |  | 3,216 |  | 3,088 |  |  |  | 1.21 |  | 1.59 |  |  |  | 0.74 | 0.008 |  | 0.190 |  | 0.083 |  | OpenStudio |  |  |
| Office - High Rise - FCU |  | 3,216 |  | 3,088 |  |  |  | 1.38 |  | 1.19 |  |  |  | 0.49 | 0.003 |  | 0.078 |  | 0.034 |  | OpenStudio |  |  |
| Office - Low Rise |  | 2,698 |  | 3,088 |  |  |  | 1.12 |  | 1.13 |  |  |  | 0.73 | 0.014 |  | 0.318 |  | 0.138 |  | OpenStudio |  |  |
| Office - Mid Rise |  | 3,266 |  | 3,088 |  |  |  | 1.19 |  | 1.48 |  |  |  | 0.48 | 0.008 |  | 0.187 |  | 0.081 |  | OpenStudio |  |  |
| Religious Building |  | 2,124 |  | 1,664 |  |  |  | 1.01 |  | 1.20 |  |  |  | 0.59 | 0.012 |  | 0.285 |  | 0.124 |  | OpenStudio |  |  |
| Restaurant |  | 5,069 |  | 4,784 |  |  |  | 1.25 |  | 1.75 |  |  |  | 0.60 | 0.015 |  | 0.354 |  | 0.154 |  | OpenStudio |  |  |
| Retail - Department Store |  | 4,099 |  | 2,935 |  |  |  | 1.30 |  | 1.69 |  |  |  | 0.67 | 0.015 |  | 0.347 |  | 0.151 |  | OpenStudio |  |  |
| Retail - Strip Mall |  | 3,677 |  | 2,935 |  |  |  | 1.09 |  | 1.12 |  |  |  | 0.67 | 0.013 |  | 0.315 |  | 0.137 |  | OpenStudio |  |  |
| Warehouse |  | 3,135 |  | 4,293 |  |  |  | 1.02 |  | 1.17 |  |  |  | 0.68 | 0.013 |  | 0.313 |  | 0.136 |  | OpenStudio |  |  |
| Unknown |  | 3,473 |  | 3,612 |  |  |  | 1.13 |  | 1.40 |  |  |  | 0.64 | 0.015 |  | 0.361 |  | 0.157 |  | n/a |  |  |
| Exterior – dusk to dawn |  | 4,303 |  | 4,303 |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.00 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Exterior – dusk to business close |  | See calculation below |  |  |  | 1.00 |  |  | 1.00 |  |  |  |  | 0.00 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Low-Use Small Business |  | 2,954 |  | 2,954 |  |  |  | 1.31 |  | 1.53 |  |  |  | 0.66 | 0.023 |  | 0.524 |  | 0.262 |  | n/a |  |  |
| Uncooled Building |  | Varies |  | Varies |  |  |  | 1.00 |  | 1.00 |  |  |  | 0.66 | 0.014 |  | 0.320 |  | 0.160 |  | n/a |  |  |
| Refrigerated Cases |  | 5,802 |  | n/a |  |  |  | 1.29 |  | 1.29 |  |  |  | 1.00 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |
| Freezer Cases |  | 5,802 |  | n/a |  |  |  | 1.50 |  | 1.5 |  |  |  | 1.00 | 0.000 |  | 0.000 |  | 0.000 |  | n/a |  |  |

Based on model with single duct reheat system with a fixed outdoor air volume.

Based on model with single duct reheat system with airside economizer controls, with constant volume zone reheat boxes and single speed fan motors.

Based on model with single duct reheat system with airside economizer controls, zone VAV reheat boxes and VFD fan motors.

ComEd Effective Useful Life Research Report (2018), Navigant, May 14, 2018

California Public Utilities Commission (CPUC), Energy Division. 2014. “DEER2014-EUL-table-update_2014-02-05.xlsx”

NEEP Incremental Cost Study Phase Two Final Report dated January 13, 2013 (pg. 32; Table 15). Equipment and labor costs were extrapolated or interpolated as necessary for motor sizes not covered in the incremental cost study.

Del Balso, Ryan J. “Investigation into the Reliability of Energy Efficiency/Demand Side Management Savings Estimates for Variable Frequency Drives in Commercial Applications”, University of Colorado, Department of Civil, Environmental and Architectural Engineering, 2013.

Douglass, J. (2005). Induction Motor Efficiency Standards. Washington State University and the Northwest Energy Efficiency Alliance, Extension Energy Program, Olympia, WA, October 2005.

Hours per year are estimated using the eQuest or OpenStudio models as the total number of hours the heating or cooling system is operating for each building type. “Heating and Cooling Run Hours” are estimated as the total number of hours fans are operating for heating, cooling and ventilation for each building type. This may overclaim certain applications (e.g. pumps) and so where possible actual hours should be used for these applications.

Based on OpenStudio Large Office model, finding difference in energy use for each VSD application. See ‘VSD ESF Calculation.xls’.

Based on OpenStudio Large Office model, finding difference in maximum demand for each VSD application. See ‘VSD ESF Calculation.xls’.

Efficiency Vermont TRM 10/26/11 for HVAC VSD motors.

RS Means, 2023. Equipment and labor costs for new VSD installation in Springfield, IL .

Methodology developed and tested in Del Balso, Ryan Joseph. “Investigation into the Reliability of Energy Efficiency/Demand Side Management Savings Estimates for Variable Frequency Drives in Commercial Applications”. A project report submitted to the Faculty of the Graduate School of the University of Colorado, 2013.

Lawrence Berkeley National Laboratory, and Resource Dynamics Corporation. (2008). “Improving Motor and Drive System Performance; A Sourcebook for Industry”. U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy. Golden, CO: National Renewable Energy Laboratory.

Douglass, J. (2005). Induction Motor Efficiency Standards. Washington State University and the Northwest Energy Efficiency Alliance, Extension Energy Program, Olympia, WA, October 2005.

Hours per year are estimated using the eQuest or OpenStudio models as the total number of hours the fans are operating for heating, cooling and ventilation for each building type.

”Gates Corporation Announces New EPDM Molded Notch V-Belts,” The Gates Rubber Co., June 2010 (Assumed 3% efficiency improvement).

“Synchronous Belt Drives Offer Low Cost Energy Savings,” Baldor. February 2009. (attached in Reference Documents).

"Energy Savings from Synchronous Belts," The Gates Rubber Co., February 2014. (Assumed 5% efficiency improvement).

“Motor System Tip Sheet #5, Replace V-Belts with Cogged or Synchronous Belt Drives,” USDOE-EERE, September 2005. (Assumed 2% efficiency improvement).

ComEd Trm June 1, 2010 page 139. The Office hours is based upon occupancy from the eQuest model developed for EFLH, since it was agreed the ComEd value was too low.

“DEER2014-EUL-table-update_2014-02-05.xlsx,” Database for Energy Efficiency Resources (DEER), DEER2014 EUL Table. (attached in Reference Documents).

Grainger catalog on-line web-site for Dayton v-belt pricing.

Assumed to be $150 based on mechanical contractor estimate.

Based on review and trend fitting cost data from Grainger online. See reference document “Notched V Belts costs.xlsx” for derivation.

Note that kWConnected may be determined using various methodologies. The examples provided use rated HP and assumed load factor. Other methodologies include rated voltage and full load current with assumed load factor, or actual measured voltage and current.

Com Ed TRM June 1, 2010.

Efficiency values for motors less than one HP taken from Baldor Electric Catalog 501, standard motor product catalog.

Hours per year are estimated using the eQuest models as the total number of hours the fans are operating for heating, cooling and ventilation for each building type.

Based on information found in Advanced Manufacturing Office, US DOE, “Replace V-Belts with Notched or Synchronous Drives”, (US Department of Energy Motor Systems Tip Sheet #5, DOE/GO-102012-3740,  November 2012). V-belt drives can have a peak efficiency of 95% and synchronous belts operate at 98%, therefore ESF is (1-95%/98%) = 3.1%.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

“NEEP Incremental Cost Study – Phase II Final Report, Navigant, 2013.”

U.S. Department of Energy Fans and Blowers Working Group, Energy Conservation Program: Final Determination of Fans and Blowers as Covered Equipment

Costs are based on the U.S. Department of Energy Fans and Blowers Working Group spreadsheet: EERE-2013-BT-STD-0006-0189_attachment_1.xlsx.

“Fan Energy Index Market Research: Final Report”, prepared for ComEd by Slipstream, May 2021.

Hours per year are estimated using the eQuest or OpenStudio models as the total number of hours the fans are operating for heating, cooling and ventilation for each building type.

Default Fan Duty Cycle Based on 2012 ASHRAE Handbook; HVAC Systems and Equipment (pg. 45.11, Figure 12)

Methodology developed and tested in Del Balso, Ryan Joseph. “Investigation into the Reliability of Energy Efficiency/Demand Side Management Savings Estimates for Variable Frequency Drives in Commercial Applications”. A project report submitted to the Faculty of the Graduate School of the University of Colorado, 2013.

Rachael Collins, Theresa Pistochini, and Robert McMurry, “Laboratory Testing and Energy Saving Potential of Des Champs HVAC Air-Trap,” UC Davis Western Cooling Efficiency Center, September 9, 2021

Ibid

Nicholas H. Des Champs, “It’s Time to Reconsider the Use of P-Traps for HVAC Condensate Removal,” (Whitepaper, February 2023).

The average material costs are based on an evaluation of commercial waterless HVAC condensate traps designed for positive/negative pressure systems with standard drainpipe diameters of 1.25", 1.5", and 2.0". Labor cost estimates are derived from 2025 RS Means data for PVC P-trap replacement in Springfield, IL.

Rachael Collins, Theresa Pistochini, and Robert McMurry, “Laboratory Testing and Energy Saving Potential of Des Champs HVAC Air-Trap,” UC Davis Western Cooling Efficiency Center, September 9, 2021

Minimum heating efficiency standards for heat pumps are sourced from the Code of Federal Standards for Small and Large Commercial Package Air Conditioning and Heating Equipment (Air Cooled), 10 CFR 431.97 with compliance dates of June 16, 2008; January 1, 2010; January 1, 2017; and January 1, 2018. As the first federal appliance standards for heating efficiency for commercial heat pumps went into effect in June 2008, assuming efficiency standards equivalent to residential heat pumps prior to that date.

Hours per year are estimated using the eQuest or OpenStudio models developed by VEIC, as the total number of hours the fans are operating for heating, cooling and ventilation for each building type. Assumes total fan run hours are divided equally between the heating and cooling seasons and that a traditional P-trap is fully dry during the heating season.

Ibid

Engineering ToolBox, (2003). Air - Density, Specific Weight and Thermal Expansion Coefficient at Varying Temperature and

Constant Pressures. [online] Available at: https://www.engineeringtoolbox.com/air-density-specific-weight-d_600.html

[Accessed April 2025].

Engineering ToolBox, (2004). Air - Specific Heat at Constant Pressure and Varying Temperature. [online] Available at:

https://www.engineeringtoolbox.com/air-specific-heat-capacity-d_705.html [Accessed April 2025]

BinMaker Pro weather data, based on average outdoor air temperatures over the hottest 5 calendar months.  Outdoor average temperatures are assumed to be equivalent to the average temperatures of typical duct locations in: attics, basements, crawl spaces and outdoors. Additional research is recommended to verify actual average ambient temperatures in these areas; additional inputs may be recommended to identify the actual space type of the duct and create a lookup table based on space type and climate zone.

Federal Register, volume 74, Number 139, July 22, 2009 for boilers >300,000 Btu/hr

Ibid

GDS Associates Inc., “2023-2024 Illinois Baseline Study: Nonresidential Baseline Study Results”, Oct 31 2024.

Fixtures hours of use are based upon schedule assumptions used in the OpenStudio models, except for those building types where Illinois based metering results provide a statistically valid estimate (currently: College, Elementary School, High School, Manufacturing, Low and Mid rise Office, Retail Department Store and Warehouse) or Grocery which is based on logging survey at 28 grocery stores in a Massachusetts DNV-GL “Lighting Hours of Use Study” report, April 12,2019. Miscellaneous is a weighted average of indoor spaces using the relative area of each building type in the region (CBECS).

Hours of use for screw based bulbs are derived from DEER 2008 by building type for cfls.  Garage, exterior and multi-family common area values are from the Hours of Use Table in this document.  Miscellaneous is an average of interior space values. Some building types are averaged when DEER has two values: these include office, restaurant and retail. Healthcare clinic uses the hospital value.

The Waste Heat Factor for Energy and is developed using EQuest models for various building types base on Chicago Illinois (closest to statewide average HDD and CDD). Exterior and garage values are 1, unknown is a weighted average of the other building types.

Coincident diversity factors are based on either combined IL evaluation results (College, Elementary School, High School, Manufacturing, Low and Mid rise Office, Retail Department Store and Warehouse), case lighting projects performed over several years by Michaels Energy in Illinois and other jurisdictions (Refrigerated and Freezer Cases), or based upon schedules defined in the eQuest models described (all others).

IFkWh Resistance value is developed using EQuest or OpenStudio models consistent with methodology for Waste Heat Factor for Energy.

Heat penalty assumptions are based on converting the IFkWh Resistance multiplier value in to IFtherms or IF kWhHeat Pump  by applying relative heating system efficiencies. The gas efficiency was assumed to be 80% AFUE and the electric resistance is assumed to be 100%, for Heat Pump is assumed to be 2.3COP.

Agriculture lighting loadshapes, operational hours, and HVAC interactive factors were developed based on field experience and research material for the general agriculture, indoor agriculture, poultry and dairy commodities. Please see the excel files, ‘General Agriculture Loadshape’ and ‘Indoor Agriculture Lighting Loadshape’ on the 8760-calculation approach and for more detail. Due to livestock housing having little to no mechanical cooling systems, waste heat cooling and associated demand factors were assumed to be 1.00.

Based on Navigant verified value using 2014 Astronomical Applications Department, U.S. Naval Observatory data for ComEd’s service territory. See Navigant Memorandum ‘RE: LED Street Lighting Program Hours of Use for the ComEd and DCEO Programs. June 21, 2017’.

For closed refrigerated case lighting (open cases should use building type WHF), the value is 1.29 (calculated as (1 + (1.0 / 3.5))). Based on the assumption that all lighting in refrigerated cases is mechanically cooled, with a typical 3.5 COP refrigeration system efficiency, and assuming 100% of lighting heat needs to be mechanically cooled at time of summer peak. Assumes 3.5 COP for medium temp cases based on the average of standard reciprocating and discus compressor efficiencies with Saturated Suction Temperatures of 20°F and a condensing temperature of 90°F.

For closed freezer case lighting (open cases should use building type WHF), the value is 1.50 (calculated as (1 + (1.0 / 2.0))). Based on the assumption that all lighting in freezer cases is mechanically cooled, with a typical 2.0 COP freezer system efficiency, and assuming 100% of lighting needs to be mechanically cooled at time of summer peak. Assumes 2.0 COP for low temp cases based on the average of standard reciprocating and discus compressor efficiencies with Saturated Suction Temperatures of -20°F and a condensing temperature of 90°F.