## Deliverable 1 Comments
Volume | Sector | Client | Section | Measure Name | Comment scope | Comment text | Author | VEIC Assignment | VEIC Response | TAC Discussion?
1 | Policy | ICC | 1.1 | Acknowledgments | Itron | Itron is now Verdant | Jennifer Morris | Sam | Updated | Not required
1 | Policy | ICC | 1.3 | Enabling ICC Policy | Itron | The Itron folks are now Verdant | Jennifer Morris | Sam | Updated | Not required
1 | Policy | ICC | 1.4 | Development Process | Docket Numbers | Added docket number for v9.0. deleted version 10 row because it is not needed yet. Also added calendar years for applicable TRM versions. | Jennifer Morris | Sam | Updated | Not required
1 | Policy | ICC | 1.4 | Development Process | General | Tenth version | Jennifer Morris | Sam | Updated | Not required
1 | Policy | ICC | 1.4 | Development Process | General | nine | Jennifer Morris | Sam | Updated | Not required
1 | Policy | ICC | 1.4 | Development Process | ("CPAS") | no quotes needed here | Jennifer Morris | Sam | Updated | Not required
1 | Policy | ICC | 3.2 | General Savings Assumptions | Measure life definition | Suggest referencing the detailed definition only | Jennifer Morris | Sam | Updated | Not required
1 | Policy | ICC | 3.10 | Discount Rate, Inflation Rates and O&M Costs | v10.0 | I think v10 should be referenced here too | Jennifer Morris | Sam | Updated | Not required
2 | C&I | Ameren | 4.1.13 | Irrigation Pump VFD | Flow𝜂 = Flow rate at a given data point in gallons per minute, use actual values | Does anyone have any data from past participants to simplify this? | Vaughn, Andrew C | Jake | Intending to discuss in TAC on 7/27: Made request for any available project data during 7/27 TAC | 2021-07-27
2 | C&I | Ameren | 4.1.13 | Irrigation Pump VFD | Pressure head at a given data point in feet with a VFD | Can this be assumed to be the same as Head_n so that post-confirmation is not required? | Vaughn, Andrew C | Jake | I don't think so. With the installation of the VFD, flow and head pressure will change depending on the speed of the pump and demand of the irrigation system | 2021-07-27
2 | C&I | Ameren | 4.1.13 | Irrigation Pump VFD | manufatures | manufacturers | Vaughn, Andrew C | Jake | Corrected | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | ; | : | Vaughn, Andrew C | Jake | Corrected | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | Heater_EfficiencyElectric | This can be removed. Built into dryer efficiency | Vaughn, Andrew C | Jake | Removed redundant variable | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | constant | Recommend changing "constant" to "value (Actual efficiencies can be used for EREP)" | Vaughn, Andrew C | Jake | Updated | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | Grain Dryer Description | Modified table to clarify potential fan energy savings | Vaughn, Andrew C | Jake | Adopted changes in draft version of TRM | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | Heater_EfficiencyElectric | This can be removed. Built into dryer efficiency | Vaughn, Andrew C | Jake | Removed redundant variable | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | BU | All "BU" or "bu" can be changed to "Bu" to be consistent | Vaughn, Andrew C | Jake | Done | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | constant | Recommend changing "constant" to "value (Actual efficiencies can be used for EREP)" | Vaughn, Andrew C | Jake | Updated | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | deemed to apply totypical for | Small wording change recommended | Vaughn, Andrew C | Jake | Updated | Not required
2 | C&I | Ameren | 4.1.14 | High Efficiency Grain Dryer | Heater_EfficiencyGas | This can be removed. Built into dryer efficiency | Vaughn, Andrew C | Jake | Removed redundant variable | Not required
2 | C&I | Ameren | 4.1.15 | Grain Dryer Tune-Up | kWh_saved/Bushel | Please show how to use these variables | Vaughn, Andrew C | Jake | Done | Not required
2 | C&I | Ameren | 4.1.15 | Grain Dryer Tune-Up | Actual | Need a kWh example | Vaughn, Andrew C | Jake | Included kWh savings calculation example | Not required
2 | C&I | Ameren | 4.1.17 | Greenhouse Thermal Curtains | area | Suggest adding: "All floor space under the thermal curtains, including pathways and growing canopy" | Vaughn, Andrew C | Jake | Added additional clarification | Not required
2 | C&I | Ameren | 4.1.18 | Infrared Film for Greenhouse | area | Suggest adding: "All floor space under the infrared film, including pathways and growing canopy" | Vaughn, Andrew C | Jake | Added additional clarification | Not required
2 | C&I | Ameren | 4.3.1 | Water Heater | For Residential-sized >55 gallon electric tanks, the baseline should be as provided below unless the existing tank being replaced is <55 gallon, in which case the <55 gallon algorithms should be used. | Not exactly sure what this is saying given that the measure is only TOS and NC | Vaughn, Andrew C | Sam | In the residential measure, we assume that >55 gallon tanks are only larger due to the market practice of using the larger heat pump water heaters to achieve greater efficiency of the heat pump cycle and preventing the unit from going in electric resistance mode. We therefore assume the baseline is a <55 gallon (non-HPWH) tank. For the commercial HPWH we did not feel comfortable making this assumption UNLESS it can be confirmed that the >55 gallon HPWH is replacing an existing tank (even if TOS) that is <55 gallon. If the existing tank is unknown (and for NC) it should be assumed that the baseline capacity is the same as the HPWH being installed. Language updated in attempt to provide more clarity. | 2021-07-20
2 | C&I | Ameren | 4.3.8 | Controls for Central Domestic Hot Water | for | per guest room? | Vaughn, Andrew C | Asa | Yes, per room. Clarification added to TRM | Not required
2 | C&I | Ameren | 4.4.11 | High Efficiency Furnace | General | Changes for Residential furnace should be adopted in this section. | Vaughn, Andrew C | Sam | Reliability review changes discussed in TAC and updated for deliverable 2. Commercial sized units now included. ECM savings now only applicable in early replacement scenario. Costs updated to remove accounting for ECM fan. | 20-Jul, 27-Jul
2 | C&I | Ameren | 4.4.48 | Small Commercial Thermostats | The measure should not be used "when HVAC systems are being replaced" | This part of the sentence may not be needed as the other parts of the sentence cover the concern. | Vaughn, Andrew C | Sam | Although I agree that this is covered by "whenever code compliance is required" - it is our understanding that code compliance will always be required when the HVAC system is being replaced so think this adds extra clarity. No change made. | 2021-07-20
2 | C&I | Ameren | 4.4.48 | Small Commercial Thermostats | Perentage | Percentage | Vaughn, Andrew C | Sam | Typo fixed. | Not required
2 | C&I | Ameren | 4.4.48 | Small Commercial Thermostats | %ElecHeat | 0.03 if unknown (based on Section 5.3.16) | Vaughn, Andrew C | Sam | This is a residential assumption. On 7/27 TAC call ComEd / Guidehouse provided an assumption for commercial buildings of 8%. | 20-Jul, 27-Jul
2 | C&I | Ameren | 4.4.48 | Small Commercial Thermostats | kBtu/hrheat | 114.5 if unknown (based on average capacity for 705 installs of thermostats in Ameren Illinois territory installed from 2015-2020) | Vaughn, Andrew C | Sam | Confirmed at TAC no additional data from ComEd so this Ameren data is used. | 20-Jul, 27-Jul
2 | C&I | Ameren | 4.4.48 | Small Commercial Thermostats | is | if | Vaughn, Andrew C | Sam | Typo fixed. | Not required
2 | C&I | Ameren | 4.4.48 | Small Commercial Thermostats | kBtu/hrCool | 61.1 if unknown (based on average capacity for 639 installs of thermostats on units under 10 tons installed in Ameren Illinois territory installed from 2015-2020) | Vaughn, Andrew C | Sam | ComEd data was provided and merged with this Ameren data. | 20-Jul, 27-Jul
2 | C&I | Ameren | 4.4.50 | Electric Chillers with Integrated Variable Speed Drives | 1,000 tons in nominal capacity | Each chiller or system total cooling tonnage? | Gribovich, Andrey | Asa | Per chiller. Clarification added to TRM | Not required
2 | C&I | Ameren | 4.4.50 | Electric Chillers with Integrated Variable Speed Drives | 550 tons in nominal capacity | Each chiller or system total cooling tonnage? | Gribovich, Andrey | Asa | Per chiller. Clarification added to TRM | Not required
2 | C&I | Ameren | 4.4.50 | Electric Chillers with Integrated Variable Speed Drives | Water-Cooled Centrifugal Chiller Incremental Costs ($/Ton) | Full load or IPLV values? | Gribovich, Andrey | Asa | Full Load. Clarification added to TRM | Not required
2 | C&I | Ameren | 4.4.50 | Electric Chillers with Integrated Variable Speed Drives | cChillers over 1,000 tons would not be applicable to this characterization and measure savings would need to be verified | Is it possible to increase this? It is not uncommon to see chillers in the 1200 ton range. Was data not provided for those by manufacturers or are they custom built and data is not available? | Gribovich, Andrey | Asa | A lack of data precluded chillers above 1K tons. | Not required
2 | C&I | Ameren | 4.4.54 | Process Heating Boiler | RF and EREP. | Suggest changing to "RF and NC. EREP can use existing boiler efficiency determined through a combustion efficiency analysis." | Vaughn, Andrew C | Asa | We removed "RF" as it doesn't apply to equipment replacements. So there is now TOS, NC and EREP. Early replacement assumptions have been added | Not required
2 | C&I | Ameren | 4.4.54 | Process Heating Boiler | Baseline after 2023 | Remove per Asa's comment | Vaughn, Andrew C | Asa | We left for informational purposes, but clarified that effective date for the new baseline would be discussed during TRM v11 update cycle | Not required
2 | C&I | Ameren | 4.4.54 | Process Heating Boiler | 20 years.[1] | This seems very short based on typical process boilers existing in Ameren territory. Recommend the following as a better source for measure life at 24 or 25 years - https://www.govinfo.gov/content/pkg/FR-2020-01-10/pdf/2019-26356.pdf (see the 43rd page, labelled page 1634). Alternatively, is measure life in 4.4.10 better source? For EREP, use Efficiency_exist for 1/3rd of the EUL | Vaughn, Andrew C | Asa | Edit made | Not required
2 | C&I | Ameren | 4.4.54 | Process Heating Boiler | 20 years.[1] | For EREP, use Efficiency_exist for 1/3rd of the EUL | Vaughn, Andrew C | Asa | Edit made | Not required
2 | C&I | Ameren | 4.4.54 | Process Heating Boiler | EfficiencyBase | Add Efficiency_exist = Baseline boiler efficiency rating of existing operational equipment | Vaughn, Andrew C | Asa | Edits made for early replacment scenarios. | Not required
2 | C&I | Ameren | 4.6.2 | Beverage and Snack Machine Controls | Average Annual Hours facility is occupied | Not certain that occupancy information for energy recovery ventilators is appropriate for vending machines, which are generally installed in lower-occupancy locations. You are suggesting that a hospital or motel would see zero lighting savings, which does not seem reasonable given likely occupancy rates and control sequences for lower-occupancy spaces in those facility types. Is there a simplified table that could be created? | Vaughn, Andrew C | Deirdre | Removed ERV reference & updated to reference Section 4.5 Lighting table, Fixture Annual Operating Hours. Copied in unknown option to this measure. | Not required
2 | C&I | Ameren | 4.6.2 | Beverage and Snack Machine Controls | MDEC | Can VEIC provide descriptions of the vending machine classes to facilitate identification in the field? Also, recommend providing an unknown or default option | Vaughn, Andrew C | Deirdre | Copied description from section 4.6.5 ENERGY STAR Refrigerated Beverage Vending Machine for the class definitions. | Not required
2 | C&I | Franklin | 4.4.13 | Package Terminal Air Conditioner (PTAC) and Package Terminal Heat Pump (PTHP) | Early replacement example calculation lifetimes | The total length of remaining useful life of existing equipment and remaining measure life afterwards presented in the Early Replacement example does not agree with the measure life listed in the Deemed Lifetime of Efficient Equipment section (expected measure life of 8 years; remaining measure life of 3 years). Same comment applies in later example. | Cliff Zimmerman | Sam | Agreed. Fixed | Not required
2 | C&I | Franklin | 4.4.14 | Pipe Insulation | Thermal Regain Factor for "Location not specified - Commercial" | Based on note 632, for semi-conditioned spaces, this should actually be (0.7/2 + 0.84/2) = 0.77. Right now, it appears that it is using conditioned space values: (0.15/2 + 0.55/2) = 0.35. Pipe to be insulated is most often located in semi-conditioned spaces and not conditioned spaces. | Cliff Zimmerman | Sam | Agreed. Fixed | 2021-07-20
2 | C&I | Franklin | 4.4.24 | Thermal Regain Factor for "Location not specified - Commercial" | 0.35 | Based on note 709, for semi-conditioned spaces, this should actually be (0.7/2 + 0.84/2) = 0.77. Right now, it appears that it is using conditioned space values: (0.15/2 + 0.55/2) = 0.35. | Cliff Zimmerman | Sam | Agreed. Fixed | 2021-07-20
2 | C&I | Franklin | 4.4.53 | HVAC Supply and Return Fans - Fan Energy Index | Measure Title | , Return and Exhaust Fans | Leo Schaub | Sam | Agreed. Added. | 2021-07-27
2 | C&I | Franklin | 4.4.53 | HVAC Supply and Return Fans - Fan Energy Index | Algorithm | This equation is basically for retrofit where FEI is not known for the baseline fan. It would be possible to modify this equation where the FEIretrofit is know for each of the flow fractions. This could be done for NC, TOS and where the FEI base is unknown. No direction is given how to proceed for either of these scenarios. | Leo Schaub | Sam | Discussed at TAC. The equation terminology was adjusted slightly and the interaction of this measure with the existing measure 4.4.26 specified, both in this new measure and in 4.4.26. | 2021-07-27
2 | C&I | Franklin | 4.4.53 | HVAC Supply and Return Fans - Fan Energy Index | FEPretrofit = Fan Electrical Power of retrofit Fan…. (kW) | At 100% Flow Fraction | Leo Schaub | Sam | Agreed. Added. | 2021-07-27
2 | C&I | Franklin | 4.4.53 | HVAC Supply and Return Fans - Fan Energy Index | Fan Energy Index of retrofit fan... (-) | At 100% Flow Fraction | Leo Schaub | Sam | Agreed. Added. | 2021-07-27
2 | C&I | Franklin | 4.4.53 | HVAC Supply and Return Fans - Fan Energy Index | Fan Energy Index of baseline fan…. (-) | At 100% Flow Fraction | Leo Schaub | Sam | Agreed. Added. | 2021-07-27
2 | C&I | Franklin | 4.4.53 | HVAC Supply and Return Fans - Fan Energy Index | Part load ratio for a given flow fraction range | Reference? And are these values applicable to fans with an FEI meeting current code requirements? | Leo Schaub | Sam | Reference added. | 2021-07-27
2 | C&I | Franklin | 4.4.54 | Process Heating Boiler | General | Would it make sense to merge this measure 4.4.11? There are several advantages: less redundancy in TRM, Uniform formatting of formula and cost assumptions, consistent equipment definitions, for what is essentially the same equipment | Adam Roche | Asa | This characterization is specific to process loads, whereas the existing measures are specific to space heating loads. Given that distinction, we prefer to keep the separate since there could be differences in assumptions. | Not required
2 | C&I | Franklin | 4.4.54 | Process Heating Boiler | applicable to the following program types | Could TOS also be applicable by using similar assumptions to NC? | Adam Roche | Asa | Agreed. TOS added. | Not required
2 | C&I | Franklin | 4.4.54 | Process Heating Boiler | Incremental Measure Cost ($/KBtu)[1] | Measures 4.4.10, High Efficiency Boiler, assumes measure cost per unit. Franklin Energy recommends a consistent approach for estimating incremental cost. Technologies in 4.4.10 and 4.4.54 are the same and should be measured the same way. Incremental cost information developed for this update is likely to be more reliable and should be applied to 4.4.10 | Adam Roche | Asa | Agreed. Costs transferred to 4.4.10. | Not required
2 | C&I | Franklin | 4.4.54 | Process Heating Boiler | Utilization Factor | Would it be acceptable to merge 8,766 and Utilization Factor into an EFLH term (8,766*41.9% = 3,673)? This would be consistent with measure 4.4.10. | Adam Roche | Asa | We'd prefer to leave as orignially drafted to avoid any potential confusion around users looking up EFLH by building type. That's not the intent for this measure, so avoiding EFLH would eliminate potential confusion. | Not required
2 | C&I | Franklin | 4.4.54 | Process Heating Boiler | EfficiencyBase | Franklin Energy recommends providing baseline efficiencies here for NC and TOS, similar to measure 4.4.10. "Use actual" can be specified for existing equipment uses in ER applications. | Adam Roche | Asa | Provided reference to table in Baseline Definition section to avoid having duplicate tables within the same characterization. Early replacement scenario added. | Not required
2 | C&I | Franklin | 4.4.54 | Process Heating Boiler | dependant | Change to “dependent”. | Adam Roche | Asa | Edit made | Not required
2 | C&I | Franklin | 4.4.55 | Commercial Gas Heat Pump | baseline in this case is the existing equipment being replaced | Volume 1 of the IL TRM defines the Time of Sale (TOS) baseline as equipment that could be purchased: “In most cases, the baseline for time of sale initiatives is the least efficient product the customer is permitted to purchase by law (i.e. complies with state and federal product efficiency standards). However, when there is no equipment available at those legal minimums the baseline shall be adjusted to the TAC agreed efficiency that represents the least efficient products that would be commonly purchased in the Illinois market absent efficiency programs. For products for which there are no legal minimum efficiency requirements, the baseline should be the TAC agreed efficiency that represents the least efficient products that would be commonly purchased in the Illinois market absent efficiency programs”. Emphasis is from Franklin Energy. Recommendation is to change this to “baseline in this case is the purchase of new equipment that is similar technology to existing equipment”. | Adam Roche | Asa | Edit to language made | Not required
2 | C&I | Frontier Energy | 4.2.10 | Ice Maker | CEE Tier 2 Advanced efficiency level standards | It appears that the CEE Tier 2 requirements (last updated in 2015) are lagging behind the federal standard (2018). This causes certain CEE Tier 2 qualified products to deliver negative savings. It should be noted that compliance with CEE Tier 2 may or may not indicate an eligible unit. | Angel Moreno | Deirdre | We have removed CEE T2 since the specifications have not been updated since the federal standard and ENERGY STAR update. We understand an update to the CEE T2 spec is expected in 2021 and so have set the review deadline such that we can review next year. | Not required
2 | C&I | Nicor | 4.4.55 | Commercial Gas Heat Pump | Fuel switch scenario | Agreed. The discussion is ongoing in Fuel Conversation TAC and SAG calls. No action needed until the final resolution is adopted from TAC and SAG. | Hardik Shah | Asa | Fuel switch scenario has been updated to be consistent with other fuel switching measures. | Not required
2 | C&I | Opinion Dynamics | 4.4.48 | Small Commercial Thermostats | Programmable to Advanced factor | Consider specifying which program years this data came from, along with when the analysis was completed. | Opinion Dynamics | Sam | Agreed. Added. | Not required
2 | C&I | Opinion Dynamics | 4.5.4 | LED Bulbs and Fixtures | Definition of Baseline Equipment | We believe the following information on NC/IECC is needed from the Residential volume: New Construction Programs Since IECC 2015 energy code, there has been mandatory requirements for lighting in New Construction: “Not less than 75 percent (90 percent in IECC 2018) of the lamps in permanently installed lighting fixtures shall be high-efficacy lamps or not less than 75 percent (90 percent in IECC 2018) of the permanently installed lighting fixtures shall contain only high-efficacy lamps”. To meet the ‘high efficacy’ requirements, lamps need to be CFL or LED, however since CFLs are no longer commonly purchased (only 1% baseline forecast) it is assumed that 75% (IECC 2015) or 90% (IECC 2018) of the New Construction baseline is an LED and therefore savings are reduced by that percentage for bulbs provided in New Construction projects. | Opinion Dynamics | Sam | Since the commercial code is entirely Lighting Power Density based, this is not a requirement like it is in the Residential code. Discussed on TAC and confirmed that commercial new construction lighting is done through LPD so this is not needed in this commercial measure. New construction baselines that were incorrectly added to the tables have been removed. | 2021-07-20
2 | C&I | Opinion Dynamics | 4.5.4 | LED Bulbs and Fixtures | Definition of Baseline Equipment | Additionally, this baseline should be applicable to omnidirectional lamps as well. | Opinion Dynamics | Sam | As above | 2021-07-20
2 | C&I | Opinion Dynamics | 4.5.4 | LED Bulbs and Fixtures | Omnidirectional Lamps | Is there a reason this table does not incorporate the NC baseline wattages similar to specialty lamps and the residential volume? | Opinion Dynamics | Sam | As above | 2021-07-20
2 | C&I | Opinion Dynamics | 4.6.13 | Add Doors to Open Refrigerated Display Cases | vertical display case | The proposed update appears to characterize savings for horizontal display cases. Please update this language to match. | Opinion Dynamics | Jake | Updated language accordingly | Not required
2 | C&I | Opinion Dynamics | 4.6.13 | Add Doors to Open Refrigerated Display Cases | vertical display case | The proposed update appears to characterize savings for horizontal display cases. Please update this language to match. | Opinion Dynamics | Jake | Updated language accordingly | Not required
2 | C&I | Opinion Dynamics | 4.8.22 | Smart Sockets – Provisional Measure | Definition of Baseline Equipment | We recommend adding a note to the baseline equipment definition, that ENERGY STAR equipment are not eligible for being placed on the smart sockets. ENERGY STAR equipment include required power saving settings which will partially offset the savings potential of this measure. | Opinion Dynamics | Sam | Good idea. A note has been added to make sure this is considered. | 2021-08-03
2 | C&I | Opinion Dynamics | 4.8.22 | Smart Sockets – Provisional Measure | Controlled Equipment | Based on the results of the upcoming Guidehouse survey results, we recommend including standby power values for more modern equipment than what is listed in this table. | Opinion Dynamics | Sam | Additions to the table have been provided in deliverable 2. Some wattage assumptions represent the assumed "on" wattage rather than standby. VEIC propose a 50% adjustment to those "on" wattages to account for some participants that would not have always left these on without the socket. | 2021-08-03
2 | C&I | Opinion Dynamics | 4.8.22 | Smart Sockets – Provisional Measure | Controlled Equipment | Can a default assumption be added for standby power when smart sockets are implemented through aac Kits program, as that information will not be obtainable? | Opinion Dynamics | Sam | Added. | 2021-08-03
2 | C&I | Opinion Dynamics | 4.8.22 | Smart Sockets – Provisional Measure | Standby power consumption of smart socket. If unknown, assume 2W. | We recommend providing the source of this 2W assumption. | Opinion Dynamics | Sam | This has been updated to 0.7W as found in the Guidehouse study | 2021-08-03
2 | C&I | Opinion Dynamics | 4.8.22 | Smart Sockets – Provisional Measure | In Service Rate | From our experience, some office equipment is required to be left on overnight, such as computer towers, to enable remote connectivity to a network. The ISR should be developed around proper installation and operation of smart sockets. In the case of smart sockets, proper operation should exclude times when the device is disabled/removed, such as when equipment is left on over nights and weekends to enable remote connectivity. Here is a link to a study that illustrates this point on office equipment operation. We can provide the study upon request. https://www.sciencedirect.com/science/article/abs/pii/S0378778817340550?via%3Dihub | Opinion Dynamics | Sam | Our understanding is this was accounted for in the present Guidehouse study. | 2021-08-03
2 | C&I | Opinion Dynamics | 4.8.24 | Building Operator Certification - Provisional | Building Operator Certification – Provisional Measure | Opinion Dynamics submitted extensive comments on this measure on 6/21. Guidehouse is in the process of updating the measure and we are working with them to try and resolve some points of concern. | Opinion Dynamics | Asa | Latest draft from Guidehouse has been delivered in this 2nd deliverable. | 2021-08-03
3 | RES | Ameren | 5.3.12 | Ductless Heat Pumps | = 43.1%%[1] | Delete extra % sign. | Froio, Zach | Sam | Fixed throughout | Not required
3 | RES | Ameren | 5.3.12 | Ductless Heat Pumps | = 72%%[1] | Delete extra % sign. | Froio, Zach | Sam | Fixed throughout | Not required
3 | RES | Ameren | 5.3.16 | Advanced Thermostats | Eff_ISR | Eff_ISR_Heat | Froio, Zach | Sam | Fixed. | Not required
3 | RES | Ameren | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | Maximum CFM, ASRE and ATRE ratings values. | Recommend changing "ASRE and ATRE" to "Adjusted Sensible Recovery Efficiency (ASRE) and Adjusted Total Recovery Efficiency (ATRE) ratings" | Froio, Zach | Deirdre | Updated language accordingly | Not required
3 | RES | Ameren | 5.4.1 | Domestic Hot Water Pipe Insulation | = 0.56 for Kits distribution,[1] 0.78 for Virtual Assessment and Self-Installation[1], and 1.0 for all other Direct Install program types | "Virtual Assessment and Self-Installation" should change to "Virtual Assessment followed by Self-Installation". The workpaper on which this was developed was for virtual assessments followed by self-installation without verified install (verified by email with Kevin Grabner, Guidehouse and Sam Dent, VEIC). Also, recommend changing "Direct Install" to "Direct Install, TOS, or Verified Install" so that all program types are accounted for. | Froio, Zach | Deirdre | Updated language accordingly | Not required
3 | RES | Ameren | 5.4.1 | Domestic Hot Water Pipe Insulation | Pipe assumptions for unknown. | In the description for "unknown" in the savings tables, the assumption about vertical and horizontal orientation should read: "Assume 3ft of vertical and remaining horizontal." | Froio, Zach | Sam | Agreed. Fixed | Not required
3 | RES | Ameren | 5.4.1 | Domestic Hot Water Pipe Insulation | Pipe assumptions for unknown. | In the description for "unknown" in the savings tables, the assumption about vertical and horizontal orientation should read: "Assume 3ft of vertical and remaining horizontal." | Froio, Zach | Sam | Agreed. Fixed | Not required
3 | RES | Ameren | 5.4.3 | Heat Pump Water Heaters | 49% = Portion of reduced waste heat that results in increased heating load[1] | Per the workpaper submitted: 49% should be changed to 5% to be consistent with the changes made on the Delta_therms equation. | Froio, Zach | Deirdre | Updated accordingly - confirmed with Author | Not required
3 | RES | Ameren | 5.4.4 | Low Flow Faucet Aerators | ISR = In service rate of faucet aerators dependant on install method as listed in table below | Consistent with Comment made in Section 5.4.1, recommend that the "Virtual Assessment/Self-Install" should be changed to "Virtual Assessment followed by Unverified Self-Install" | Froio, Zach | Deirdre | Updated language accordingly | Not required
3 | RES | Ameren | 5.4.5 | Low Flow Showerheads | = Dependant on program delivery method as listed In table below | Consistent with Comment made in Section 5.4.1, recommend that the "Virtual Assessment/Self-Install" should be changed to "Virtual Assessment followed by Unverified Self-Install" | Froio, Zach | Deirdre | Updated language accordingly | Not required
3 | RES | Ameren | 5.5.6 | LED Specialty Lamps | ISR = In Service Rate or the percentage of lamps rebated that get installed | Consistent with Comment made in Section 5.4.1, recommend that the "Virtual Assessment/Self-Install" should be changed to "Virtual Assessment followed by Unverified Self-Install" | Froio, Zach | Deirdre | Updated language accordingly | Not required
3 | RES | Ameren | 5.5.6 | LED Specialty Lamps | ISR = In Service Rate or the percentage of lamps rebated that get installed | Recommend adding 2nd and 3rd year savings to "Virtual Assessment followed by Unverified Self-Install" | Froio, Zach | Deirdre | Updated table savings | Not required
3 | RES | Ameren | 5.5.8 | LED Screw Based Omnidirectional Bulbs | ISR = In Service Rate, the percentage of lamps rebated that are actually in service. | Consistent with Comment made in Section 5.4.1, recommend that the "Virtual Assessment/Self-Install" should be changed to "Virtual Assessment followed by Unverified Self-Install" | Froio, Zach | Deirdre | Updated language accordingly | Not required
3 | RES | Ameren | 5.5.8 | LED Screw Based Omnidirectional Bulbs | ISR = In Service Rate, the percentage of lamps rebated that are actually in service. | Recommend adding 2nd and 3rd year savings to "Virtual Assessment followed by Unverified Self-Install" | Froio, Zach | Deirdre | Updated table savings | Not required
3 | RES | Ameren | 5.6.1 | Air Sealing | Location | Change "Location" to "Residence Type" in this Section and other sections. | Froio, Zach | Deirdre | Updated language accordingly | Not required
3 | RES | Ameren | 5.6.1 | Air Sealing | Typical Reductions in Leakage[1] | Recommend changes to make the deemed kWh savings similar to the therm savings by product type | Froio, Zach | Deirdre | In order to provide a kWh/unit table we would need to have an average n-factor, cooling efficiency, cooling degree day/location etc. This could potentially be proposed using program data in the future, but the current approach allows users to calculate cooling savings for various air sealing activity without the need for blower door testing | Not required
3 | RES | Ameren | 5.5.1 | Compact Fluorescent Lamp (CFL)—Retired 12/31/2018, Removed in v8 | Miscellaneous | All measure subsection numbers in section 5.7 are incorrectly numbered as section “5.5.#” rather than “5.7.#” | Froio, Zach |  | Fixed | Not required
3 | RES | Franklin | 5.3.2 | Boiler Pipe Insulation | Footnote referring to difference in heat loss for horizontal v vertical pipe. | Note 259 below references DHW pipe insulation, but this is the boiler pipe insulation section; there’s a separate section for DHW pipe insulation. Does this characterization and assumed footage of vertical and remaining horizontal (if unknown) apply to space heating pipe as well as domestic hot water pipe. | Cliff Zimmerman | Sam | The footnote has been updated to refer to boilers rather than DHW tanks. The factors derived in the DHW measure should be the same and we believe the assumption of 3ft vertical remains appropriate. Discussed at TAC and no additional feedback received. | 2021-07-27
3 | RES | Franklin | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | 15 | The MN TRM lifetime assumes controls are the limiting factor. If 24 hour operation, what controls are in this system limiting the life? | Leo Schaub | Deirdre | Revision expected from author by 8/13. VEIC will circulate once received. | 2021-08-03
3 | RES | Franklin | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | = 68 F | Rather low for cooling and assumes no setback/setup. Is that typical? Isn’t there some IL thermostat data with average temps for cooling and heating? | Leo Schaub | Deirdre | Revision expected from author by 8/13. VEIC will circulate once received. | 2021-08-03
3 | RES | Franklin | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | 24 | Doesn’t address intermittent operation allowed by code. The most common sequences provide 20/40/60 minutes of operation every hr. See controls in link below. Suggest using average at 40 minutes. Additionally, 24/7 assumes the ERV doesn’t ever freeze up as well and no defrost cycle is required. See spec sheet for defrost cycle sequence. ehb_erv_hrv_2102.pdf (lennoxintl.com) | Leo Schaub | Deirdre | Revision expected from author by 8/13. VEIC will circulate once received. | 2021-08-03
3 | RES | Franklin | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | 68 | See comment above | Leo Schaub | Deirdre | Revision expected from author by 8/13. VEIC will circulate once received. | 2021-08-03
3 | RES | Franklin | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | 24 | See comment above | Leo Schaub | Deirdre | Revision expected from author by 8/13. VEIC will circulate once received. | 2021-08-03
3 | RES | Franklin | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | 8760 | Assumes constant operation and not intermittent operation allowed by code | Leo Schaub | Deirdre | Revision expected from author by 8/13. VEIC will circulate once received. | 2021-08-03
3 | RES | Franklin | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | 24 | See comment above | Leo Schaub | Deirdre | Revision expected from author by 8/13. VEIC will circulate once received. | 2021-08-03
3 | RES | Franklin | 5.4.1 | Domestic Hot Water Pipe Insulation | R value of insulation | At a Mean Rating Temperature of 100 degrees F. (as conductivity is temperature dependent) | Leo Schaub | Sam | Discussed on 7/27 TAC. A footnote has been added stating: "Where possible it should be ensured that the R-value of the insulation is at the appropriate mean rating temperature (100F)." And for Boiler Pipe Insulation (125F). | 2021-07-27
3 | RES | Guidehouse | 5.4.4 | Low Flow Faucet Aerators | MF Virtual Assessment with /Self-Install, Kitchen Aerator | Clarified that the self-install ISR applied only to products received as part of a virtual assessment. These ISRs do not cover retail purchases by an end user | Kevin Grabner | Deirdre | Updated language accordingly | Not required
3 | RES | Guidehouse | 5.4.5 | Low Flow Showerheads | MF Virtual Assessment with /Self-Install, Two Showerheads | These ISRs apply only to self-installs associated with products received through a virtual assessment. These ISRs do not apply to self install for retail purchases. | Kevin Grabner | Deirdre | Updated language accordingly | Not required
3 | RES | ICC | 5.3.8 | Ground Source Heat Pump | Heat Rate and legislation. | Added footnote for definition of Hgrid: If legislation is passed to adopt a site conversion factor for 2022 and beyond, the site conversion factor of 3,412 shall be adopted for the applicable years. VEIC should double check that this is appropriate location for footnote to have calculation performed correctly if legislation is adopted. In addition, please add to all other fuel switching measures. | Morris, Jennifer | Sam | Footnote added to new lifetime heat rate assumptions as discussed in the working group.
3 | RES | Nicor | 5.3.1 | Air Source Heat Pump | Midstream Baseline 13.39 SEER, 10.69 EER, 6.66 HSPF | These values are lower than the federal standards that apply to TOS. This implies that some midstream participants are early replacements or retrofits and dual baseline should apply. These values don’t address installations where current system is central AC only (fuel switching) or current system is no cooling (load building). Can ComEd provide that information (2019-2020 program data)? | Nicor | Sam | Discuss at TAC. VEIC do not agree that any midstream participants should be considered early replacement. A midstream incentive is unlikely to be enough to encourage a participant to change system type, but it could encourage them to install a more efficient one. The baseline is what would have happened absent the program, not what system is existing in the home. We believe that the cooling ratings are appropriate since they simply find the average TOS baseline (ASHP SEER 14 v CAC SEER 13). However we feel that for Central ASHPs the HSPF should be based on the TOS ASHP baseline and not include electric resistance. The proposed baseline (mix of ASHP and resistance) could be appropriate for Ductless Minisplits if midstream assumptions are required there.
3 | RES | Nicor | 5.3.1 | Air Source Heat Pump | SourceEnergySavings (MMBTUs) | Fuel switch is limited to the replacement of gas heat with ASHP and not impacted by additional cooling efficiency savings. The eligibility test should be defined by BTU savings from the heating systems only. This will ensure that fuel switching measures that increase total BTU consumption are not implemented solely due to ancillary cooling savings. | Nicor | Sam | Discussed in Working Group. Decision to include all aspects of the measure (cooling, heating, DHW) and compare baseline condition with measure condition in the determination if the measure is eligible.
3 | RES | Nicor | 5.3.1 | Air Source Heat Pump | Gas utility only N/A SourceEnergySavings * 10 | Sam’s revised approach calculates the net source Btu savings (correctly), and then merely applies factors for Btu content of fuels to express that net source Btu savings as either kWh or therms (depending on the incentive funder). What we instead need to calculate is the site kWh and therm savings that would produce an equivalent net Btu savings at source for a more traditional energy efficiency measure. This is the TRM9 approach, which stated with the source Btu savings, and: Applied the electric heat rate/loss factor to calculate electric savings Source Savings X Heat Rate X Loss Factor Btugenerator X kWhgenerator/Btugenerator X kWhhouse/kWhgenerator, Applied the therm:Btu conversion factor and gas loss factor to calculate gas savings, Source Savings X ThermsPerBtu X Loss Factor, Btupipeline X thermspipeline/Btupipeline X thermshouse/thermspipeline. You can see that this second approach is correct by applying the two methods to the cooling portion of the heat pump example calculation. In the TOS example, cooling savings represent 614 kWh of the 1,463 kWh total savings. In the fuel switch example from the 6/25 draft (using Sam’s new approach), cooling savings represent 1,800 kWh of the 4,010 total kWh savings. Since the cooling savings are identical in the two scenarios (the net Btu effect comes entirely from the difference in heating systems) Sam’s approach is tripling electric savings for fuel switch measures. By correctly applying the heat rate/loss factors (i.e., TRM9 approach), cooling savings for the fuel switch measure are also 614 kWh. | Nicor | Sam | Calculation was reviewed and agreed upon during the working group calls. Updated in second deliverable.
3 | RES | Nicor | 5.3.1 | Air Source Heat Pump | GasSystemDistributionLoss | Nicor gas will provide Nicor specific value | Nicor | Sam | VEIC received the value and have included it in deliverable 2.
3 | RES | Nicor | 5.3.8 | Ground Source Heat Pump | SourceEnergySavings (MMBTUs) | Fuel switch is limited to the replacement of gas heat with GSHP and not impacted by additional cooling efficiency savings. The eligibility test should be defined by BTU savings from the heating systems only. This will ensure that fuel switching measures that increase total BTU consumption are not implemented solely due to ancillary cooling savings. | Nicor | Sam | As above
3 | RES | Nicor | 5.3.8 | Ground Source Heat Pump | Gas utility only | Please check comment on ASHP methodology. Does this need to be updated accordingly | Nicor | Sam | As noted in deliverable 1, only the ASHP measure was adjusted as the final algorithm and other key assumptions had not be finalized through the working group. These have been updated in deliverable 2. | Not required
3 | RES | Nicor | 5.3.12 | Ductless Heat Pumps | SourceEnergySavings (MMBTUs) | Fuel switch is limited to the replacement of gas heat with DMSHP and not impacted by additional cooling efficiency savings. The eligibility test should be defined by BTU savings from the heating systems only. This will ensure that fuel switching measures that increase total BTU consumption are not implemented solely due to ancillary cooling savings. | Nicor | Sam | As above | WG
3 | RES | Nicor | 5.3.12 | Ductless Heat Pumps | ΔThermsFuelSwitch – (ΔkWhFuelSwitch * kWhtoTherm) + (ΔkWhEfficiencyImprovement * kWhtoTherm) | Please check comment on ASHP methodology. Does this need to be updated accordingly | Nicor | Sam | As above | WG
3 | RES | Nicor | 5.3.4 | Duct Insulation and Sealing | %Gas and %Elec | ComEd data assigned to Nicor Gas includes electric customers outside of gas utility customer service territories and all electric homes without gas service. This overstates electric heat saturation in Nicor Gas customers. Nicor Gas recommends applying NSG values as proxy for Nicor Gas | Nicor | Deirdre | DONE - Revised Nicor values to equal NSG not ComEd, for %Gas & %Electric | Not required
3 | RES | Nicor | 5.4.3 | Heat Pump Water Heaters
3 | RES | Nicor | 5.6.1 | Air Sealing
3 | RES | Nicor | 5.6.2 | Basement Sidewall Insulation
3 | RES | Nicor | 5.6.3 | Floor Insulation above Crawlspace
3 | RES | Nicor | 5.6.4 | Wall Insulation
3 | RES | Nicor | 5.6.5 | Ceiling/Attic Insulation
3 | RES | Nicor | 5.6.6 | Rim/Band Joist Insulation
3 | RES | Opinion Dynamics | 5.3.1 | Air Source Heat Pump | EER_Base | Added decimal for consistency. | Opinion Dynamics | Sam | Agreed. Fixed | Not required
3 | RES | Opinion Dynamics | 5.3.1 | Air Source Heat Pump | EER_Base with no central cooling | We recommend adding the following footnote, for consistency with the footnote in the SEER_base tables: “Assumes that the decision to replace existing systems includes desire to add cooling.” | Opinion Dynamics | Sam | Agreed. Fixed | Not required
3 | RES | Opinion Dynamics | 5.3.12 | Ductless Heat Pumps | EER_Base with no central cooling | We recommend adding the following footnote, for consistency with the footnote in the SEER_base tables:“Assumes that the decision to replace existing systems includes desire to add cooling.” | Opinion Dynamics | Sam | Agreed. Fixed | Not required
3 | RES | Opinion Dynamics | 5.4.1 | Domestic Hot Water Pipe Insulation | $0.295-0.332/ft for ¾” insulation.[1] | Consider providing one cost value for ¾” instead of a range between $0.295 to $0.332 per linear foot to avoid inconsistencies in cost effective analyses for the same measure in different jurisdictions with different evaluators. | Opinion Dynamics | Sam | Agreed. Costs have been updated based on average of the range. | Not required
3 | RES | Opinion Dynamics | 5.4.1 | Domestic Hot Water Pipe Insulation | Example kWh calculation | In the example equation below, the algorithm varies slightly from what is presented above. (note, because text boxes do not allow comments, we added it as close as possible) ΔkWh = ((1 / Rexist – 1 / Rnew) * Cinside * Leffective * ΔT * 8,766 * ISR)/ ηDHW / 3412 | Opinion Dynamics | Sam | Agreed. Fixed | Not required
3 | RES | Opinion Dynamics | 5.4.1 | Domestic Hot Water Pipe Insulation | Example kW calculation | In the example below, please revise kW example calculation to use revised 258 kWh value. | Opinion Dynamics | Sam | Agreed. Fixed. We had originally deleted this example calc but have added back in but with the values updated. | Not required
3 | RES | Opinion Dynamics | 5.4.1 | Domestic Hot Water Pipe Insulation | Example Therm calculation | In the example below, we recommend updating the therm savings example to align with therm savings algorithm. | Opinion Dynamics | Sam | Agreed. Fixed. We had originally deleted this example calc but have added back in but with the values updated. | Not required
3 | RES | Opinion Dynamics | 5.6.8 | Triple Pane and Thin Triple Windows | Table 3: Existing Homes – Existing Window Values | We do not see a mention of window U-Values or SHGC in the report cited in footnote 1371. We recommend ensuring the proper source of the U-Value and SHGC in the table is referenced in the footnote. | Opinion Dynamics | Deirdre | Updated language accordingly. Per author, Engineering judgement was a factor. Revised footnote accordingly. | Not required
3 | RES | Opinion Dynamics | 5.6.8 | Triple Pane and Thin Triple Windows | Remaining life of existing equipment – 13 years | For future TRM versions, we recommend RUL be informed from research, if performed, in lieu of the assumption that RUL equals one-third of EUL. | Opinion Dynamics | Deirdre | NOTED - We could add to IL program evaluation recommendations | Not required
3 | RES | Opinion Dynamics | 5.6.8 | Triple Pane and Thin Triple Windows | Table 4: Gas Furnace and Air Conditioner - savings per window area by climate zone and baseline window condition[1] | We recommend adding detail in the footnote to specify that EnergyPlus models were used to develop the savings per Hart paper methods and assumptions. | Opinion Dynamics | Deirdre | Updated footnote language accordingly | Not required
3 | RES | Opinion Dynamics | 5.7.1 | High Efficiency Pool Pumps | Energy Factor | The algorithm defined above uses “Weighted” Energy Factor (WEF_exist). Can you please align the terminology? | Opinion Dynamics | Sam | Fixed. For existing pumps we are assuming single speed and therefore the correct term is Energy Factor rather than Weighted Energy Factor. Updated accordingly. | Not required
3 | RES | Opinion Dynamics | 5.7.1 | High Efficiency Pool Pumps | above | Consider adding language to clarify that the table provides defaults, and practitioners should calculate actual savings when possible. | Opinion Dynamics | Sam | Agreed. Fixed. | Not required
3 | RES | Opinion Dynamics | 5.7.1 | High Efficiency Pool Pumps | Mid life adjustment | Consider “Adjustment Factor applied to annual kWh savings” for clarity. (I recall there being confusion with how to apply the mid-life adjustment with commercial lighting last year, and this was how it was addressed.) | Opinion Dynamics | Sam | Agreed. Fixed. | Not required
4 | XC | Ameren | Attachment B |  | Grain Dryer | There is a deemed measure. Do not see reason to have here. | Vaughn, Andrew C | Sam | This measure has been removed from this table. | 2021-07-20
4 | XC | Ameren | Attachment B |  | Add Doors to Open Refrigerated Cases | Same as above comment | Vaughn, Andrew C | Sam | This measure has been removed from this table. | 2021-07-20
4 | XC | Ameren | Attachment B |  | Commercial Dishwasher | Same as above comment | Vaughn, Andrew C | Sam | This measure has been removed from this table. | 2021-07-20
4 | XC | Ameren | Attachment B |  | To achieve this, the implementer will provide an ex ante EUL for the project/measure and the evaluator will assess it for reasonableness and revise as necessary. | Would like to verify with evaluators that this statement still applies in the unique projects/measures circumstance. (i.e. that the other changes in this section this year do not override this) | Vaughn, Andrew C | Sam | Discussed at TAC. Decision that language is still appropriate as is. No change made. | 2021-08-03
4 | XC | Ameren | Attachment B |  | "Navigant" | evaluator | Vaughn, Andrew C | Sam | Agreed. Fixed. | Not required
4 | XC | ComEd | 6.2.1 | Voltage Optimization | Future feeder language | Typo: Foot note 40 has a typo. The word “we” should be deleted as shown below. To determine the value, ComEd considered several factors including the timeline of commissioning any future feeder, load ramping up for large customers, and the comments we received from ICC and Guidehouse to claim the feeders as soon as ComEd expects to have full load. ComEd considers a feeder to have reached its full load when 70% of the projected load (at the minimum) has been materialized. | Gutierrez, Vincent J:(ComEd) | Asa | Agreed. Fixed. | Not required
4 | XC | ICC | Appendix B |  | Text about retroactive v next program year application of EUL changes. | Sentence didn’t make sense to deleted and left in second sentence but changed default to deemed to be consistent with above. | Morris, Jennifer | Sam | Edits reviewed with TAC and agreed to be applied in Deliverable 2. | 2021-08-03

## Deliverable 2 Comments
Volume | Sector | Client | Section | Measure Name | Comment scope | Comment text | Author | VEIC Assignment | VEIC Response | TAC Discussion? | In memo?
2 | C&I | Ameren | 4.2.6, 4.2.11, 4.3.1, 4.3.2, 4.3.3, 4.3.7, and 4.4.44: | Multiple | TIN = Incoming water temperature from well or municiple system | Comment for 4.2.6, 4.2.11, 4.3.1, 4.3.2, 4.3.3, 4.3.7, and 4.4.44: | Vaughn, Andrew C | Sam | Agree. All measures have been updated. |  | Y
2 | C&I | Ameren | 4.3.1 | Water Heater | = 54°F [1] | Input/Supply water temperature (TIN ) should be updated to 50.7 degF based on Chen, et.al. 2020. |  |  | Done |  | Y
2 | C&I | Ameren | 4.4.54 | Process Heating Boiler | Each gas-fired commercial packaged boiler listed in Table 3 to §431.87 and manufactured on or after January 10, 2023, must meet the applicable energy conservation standard levels as below. This baseline is applicable to NC.Table 3 Boiler baseline efficiency standards (on or after January 10, 2023)Boiler Type | Can we move this under the early replacement section since this only applies to early replacement at this time. (it will apply to new construction in future years)? | Vaughn, Andrew C |  | We think it makes sense to keep where it is since it will be the TOS/NC baseline from 2023. We have made it more clear when this will be the baseline |  | Y
2 | C&I | Ameren | 4.6.3 | Door Heater Controls | The incremental capital cost, including labor costs, for a refrigeration door heater control, regardless of the control strategy, is $1,051. When evaluated on a per door basis, incremental costs are estimated at $131 per cooler door and $231 per freezer door.[1] | Incremental costs are substantially higher than in Wisconsin, which are lower than the prior TRM version. Seeing if data is available from installs in Ameren Illinois territory to provide typical costs | Vaughn, Andrew C | Jake | Ameren provided state-specific historical cost data from prior program participants. The TRM is updated with these incremental cost values ($79.50 per door for coolers and $90.77 per door for freezers). |  | y
2 | C&I | Ameren | 4.6.3 | Door Heater Controls | 45.% for all control types | The Focus on Energy TRM from 2019 by Cadmus has a savings factor of 46.5% for MMIDs 2197, 2198, and 2199 and 74.2% for MMIDs 2200 and 2201. VEIC has chosen 45% as the savings factor only. Why not follow the Wisconsin TRM since you are choosing a Cadmus study as your basis for savings? See https://focusonenergy.com/sites/default/files/Focus_on_Energy_2019_TRM-Update.pdf, "Anti-Sweat Heater Controls." | Vaughn, Andrew C | Jake | VEIC recommends using the 45.1% savings factor over the Ameren recommended values sourced from the WI Focus on Energy TRM. This TRM leverages the Connecticuty Program Savings Documentation, published in 2012, as the basis for their savings factor. However, these values appeared to be sourced from an anecdotal email communication with a vendor. VEIC recommends the 45.1% savings factor, as sourced from a 2015 NEEP Commercial Loadshape Report which actively metered anti-sweat door heater controls. As the basis for the savings factor was derived from more rigorous and substantiated means, this continues to be VEIC's recommendation. |  | n/a
2 | C&I | Ameren | 4.7.2 | Compressed Air Low Pressure Drop Filters | 4-shift (24/7)0.95 | Can we please add Unknown / Weighted average 0.89 Similar to Sections 4.7.1, 4.7.4, 4.7.5, 4.7.6, 4.7.8, 4.7.10, and 4.7.11 | Vaughn, Andrew C |  | Done |  | Y
2 | C&I | ComEd | 4.4.32 | Combined Heat and Power | ) For systems participating in both electric EEPS and gas EEPS programs: | Posing a question for discussion: Does the proposed savings table/value provide a dis-incentive to pursue joint programs? | Stoll, Jacob J. : |  | Decision by TAC to leave CHP measure as v9. Work to update in v11. |  | y
2 | C&I | ComEd | 4.4.32 | Combined Heat and Power | For systems participating in both electric EEPS and gas EEPS programs: | POTENTIAL NON-CONSENSUS: ComEd believes the TRM should determine a measure’s electricity and natural gas savings only. The TRM should not allocate savings based on how a measure is incentivized. For ComEd, NiCor and Peoples, detailed Joint Funding Agreements are executed each year in which the cost and savings allocations are determined. That is and should be up to the utilities to decide, not the TRM Administrator. | Stoll, Jacob J. : |  | Decision by TAC to leave CHP measure as v9. Work to update in v11. |  | y
2 | C&I | ICC | 4.8.24 | Building Operator Certification | Il | Clarified IL | Morris, Jennifer |  | Done |  | Y
2 | C&I | ICC | 4.8.24 | Building Operator Certification | to | Expanded to clarify the purpose of the interviews | Morris, Jennifer |  | Done |  | Y
2 | C&I | ICC | 4.8.24 | Building Operator Certification | . I | Added that Nicor evaluation team is also conducting study to inform the TRM update | Morris, Jennifer |  | Done |  | Y
2 | C&I | ICC | 4.8.24 | Building Operator Certification | T | Minor text edits throughout measure, not adding anymore comments for these | Morris, Jennifer |  | Done |  | Y
2 | C&I | GTI/Nicor | 4.4.55 | Commercial Gas Heat Pump | ((kBtu/hrheat * EFLHheat * (1/COPGHP)) / 1000) * GasSystemDistributionLoss | Should be (1 + GasSystemDistributionLoss) | Ramanathan Dharmarajan |  | Agreed. Fixed throughout |  | Y
2 | C&I | GTI/Nicor | 4.4.55 | Commercial Gas Heat Pump | GasSystemDistributionLoss | Same as above. | Ramanathan Dharmarajan |  | Agreed. Fixed |  | Y
2 | C&I | GTI/Nicor | 4.4.55 | Commercial Gas Heat Pump | GasSystemDistributionLoss | Same as above. Please make this edit in the below example as well. It is in an image format and I am not able to comment there. | Ramanathan Dharmarajan |  | Agreed. Fixed |  | Y
2 | C&I | Opinion Dynamics | 4.8.24 | Building Operator Certification | CY2020 | AIC does not use the “CY” convention. | Opinion Dynamics |  | Done |  | Y
2 | C&I | Opinion Dynamics | 4.8.24 | Building Operator Certification | [1]. | We suggest making this slight edit to the footnote because it is not clear whether sufficient data could ever be available to develop separate savings assumptions for level I and level II (we run into the same issue as deemed savings, in general. For BOC, experiences are so Custom it could be difficult to collect enough data to confidently characterize a difference in savings from level I and level II). | Opinion Dynamics |  |  |  | Y
2 | C&I | Opinion Dynamics | 4.8.24 | Building Operator Certification | Ameren Illinois[1] | Apologies for just noticing this now but it looks like some of the AIC numbers in this table got crossed up between two files Opinion Dynamics shared during the development of this measure. We have updated the table to include the correct per participant savings for kW and therms. We also attempted to update the weighted averages and subsequent per sq. ft. savings values below. | Opinion Dynamics |  |  |  | Y
3 | RES | Ameren | 5.3.1 | Air Source Heat Pump | 8.2 HSPF | Based on 779 Midstream Time-of-Sale applications where existing heating equipment was reported for Ameren Illinois projects from 2018-2020; 336 of the existing equipment was Electric Resistance and 443 was ASHP (43% electric resistance). Therefore, recommended to change to 43%*3.412+57%*8.2=6.135 HSPF instead of 8.2 HSPF. | Vaughn, Andrew C |  | Discussed on 8/31 TAC. Decision to add following language: "Note the above default HSPF assumes an ASHP baseline. If evaluation determines that the program influenced the decision of a participant to replace existing resistance heat with an ASHP (rather than influenced the participant to increase the efficiency of an ASHP they were already intending to purchase) then the baseline efficiency of 3.412 HSPF can be applied. Likewise, if evaluation determines that the program influenced a participant to switch from existing gas heat, time of sale fuel switch calculations can be applied." |  | y
3 | RES | Ameren | 5.3.2 | Boiler Pipe Insulation | L | In the Natural Gas Savings equation, the "L" term should be "L_effective". Also, the example which follows the Savings section has a typo for DeltaT: it is listed as 120, and it should be 110. | Froio, Zach |  | Done |  | Y
3 | RES | Ameren | 5.3.17 | Gas High Efficiency Combination Boiler | TIN = Incoming water temperature from well or municipal system | Input/Supply water temperature should be updated to 50.7 degF based on Chen, et.al. 2020. | Froio, Zach |  | Done |  | Y
3 | RES | Ameren | 5.4.1 | DHW Pipe Insulation | This measure describes adding insulation to un-insulated domestic hot water pipes. The measure assumes the pipe wrap is installed to the first length of both the hot and cold pipe up to the first elbow. This is the most cost-effective section to insulate since the water pipes act as an extension of the hot water tank up to the first elbow which acts as a heat trap. Insulating this length therefore helps reduce standby losses. Default savings are provided per 3ft length and are appropriate up to 6ft of the hot water pipe and 3ft of the cold. | On the first paragraph in the DESCRIPTION for this measure an additional sentence should be added: "Where a hot water recirculating pump is in use, this measure is viable for the entire hot water loop -- savings are consistent with the values in this entry." | Froio, Zach |  | Done |  | Y
3 | RES | Ameren | 5.4.1 | DHW Pipe Insulation | Unknown | The "Unknown Pipe Type" should be split into two categories: 1/2" and 3/4", and the values for: Electric Savings, Summer Peak Coincident Demand Savings, and Therm Savings should be averaged across the sizes. For example, the Electric Savings should be: 3/4" Unknown Pipe Type: 29.25 kwh (for kits) and 52.25 kwh (for All Other Pgms); 1/2" Unknown Pipe Type: 23.4 kwh (for kits) and 41.8 kwh (for All Other Pgms). | Froio, Zach |  | Done |  | Y
3 | RES | Ameren | 5.4.2 | Gas Water Heater | TIN = Incoming water temperature from well or municipal system= 54°F [1] | Input/Supply water temperature should be updated to 50.7 degF based on Chen, et.al. 2020. | Froio, Zach |  | Done | NEED TO DO GSHP | Y
3 | RES | Ameren | 5.4.4 | Low Flow Faucet Aerators | SupplyTemp = Assumed temperature of water entering house= 54.1F [1] | Input/Supply water temperature should be updated to 50.7 degF based on Chen, et.al. 2020. | Froio, Zach |  | Done |  | Y
3 | RES | Ameren | 5.4.5 | Low Flow Showerheads | SupplyTemp = Assumed temperature of water entering house= 54.1F[1] | Input/Supply water temperature should be updated to 50.7 degF based on Chen, et.al. 2020. | Froio, Zach |  | Done |  | Y
3 | RES | Ameren | 5.4.8 | Thermostatic Restrictor Shower Valve | SupplyTemp = Assumed temperature of water entering house= 54.1F [1] | Input/Supply water temperature should be updated to 50.7 degF based on Chen, et.al. 2020. | Froio, Zach |  | Done |  | Y
3 | RES | Ameren | 5.6.1 | Air Sealing | Distributed Self-Install Income-Qualified Kits[1] | Distributed Self install kits do not have an ISR for Door Sweeps and/or "Other" measures | Froio, Zach |  | Done |  | Y
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | Air Source Heat Pump | Please note that the comments in this section also apply to Ductless and Ground Source Heat Pump measures. Additionally, ComEd retains the option to make something non-consensus should Draft 3 make substantive changes to Draft 2 or if comments are not considered or addressed. | Stoll, Jacob J. : |  | The only substantive differences between Draft 2 and this "Almost Final" draft is to add furnace fan kWh savings, set GasDistributionLoss factor to 0% for v10 until we can conclude whether a different value is appropriate, and update the early replacement default. The net effect of these two changes is higher total MMBtu savings. Other changes provide added clarification on the algorithms. |  | n/a
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | 7 | This number is based on an old program design and is over a decade old. We propose updating it this TRM cycle. ComEd has and will provide recent (2018-20) program history data to support an update. | Fay, James M:(ComEd) |  | Data provided and incorporated in to this and DMSHP measures. |  | y
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | [1] | The TRM should specify the baseline assumptions for the unknown case. It should not predetermine what a program “knows”. It should not assign the unknown case to a specific program design. | Fay, James M:(ComEd) |  | Wording adjusted to reflect this. |  | n/a
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | [1] | Or use the alternative wording suggested (original language removed). | Fay, James M:(ComEd) |  | As above |  | n/a
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | [1] | The Unknown Baseline should be based on program history where that data is available, is robust and is relevant. ComEd can provide this data. It includes 2018-20 program data by measure equipment type (ASHP, Ductless HP & GSHP), Early-Replacement vs. Time-of-Sale, and baseline equipment type (ASHP, electric resistance and gas furnace). | Fay, James M:(ComEd) |  | Discussed on 8/31 TAC. Decision to add following language: "Note the above default HSPF assumes an ASHP baseline. If evaluation determines that the program influenced the decision of a participant to replace existing resistance heat with an ASHP (rather than influenced the participant to increase the efficiency of an ASHP they were already intending to purchase) then the baseline efficiency of 3.412 HSPF can be applied. Likewise, if evaluation determines that the program influenced a participant to switch from existing gas heat, time of sale fuel switch calculations can be applied." |  | y
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | Fuel switch measures must produce positive total annual lifecycle source fuel savings | Instead of “Annual”, this should reflect “Lifecycle” savings to be consistent with the statutory language. | Stoll, Jacob J. : |  | Agreed and updated throughout. |  | n/a
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | below | POTENTIAL NON-CONSENSUS: ComEd believes the TRM should determine a measure’s electricity and natural gas savings only. The TRM should not allocate savings based on how a measure is incentivized. For ComEd, NiCor and Peoples, detailed Joint Funding Agreements are executed each year in which the cost and savings allocations are determined. That is and should be up to the utilities to decide, not the TRM Administrator. | Fay, James M:(ComEd) |  | Discussed on 8/31 TAC. Decision to add following note to the joint program row in the tables: "(Note utilities may make alternative agreements to how savings are allocated as long as total MMBtu savings remains the same)." |  | y
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | life | ComEd believes it is more appropriate to use the Tier averages for each Tier: 8300 for the 1st Tier & ~7300 for the 2nd Tier. Using the Tier-average would meet the objective of keeping the lifetime energy savings constant. The method proposed in this TRM version would not. In creating a 2-Tier stream of savings for lighting in V. 9.0 of the TRM, total lifetime savings were held constant after creating the Tiers. The heat rate is an input to the energy savings calculation and not using a Tier-average results in different lifetime energy savings when the site savings vary (for Early Replacement). | Fay, James M:(ComEd) |  | Discussed on 8/31 TAC. While neither the current approach or the approach suggested here by ComEd results in exactly the same lifetime net present value of savings, they are both within 1%. VEIC prefer the approach provided in the draft since it starts with our best estimate of savings in the first year, then applies an adjustment to result in lifetime savings that is consistent with actual lifetime savings. No change. |  | n/a
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | Factor | These numbers must be 1) on a consistent basis with corresponding electric grid losses (i.e., must include gas processing, transmission and distribution efficiency factors, and 2) these must be sourced (either to EIA or a document filed with Illinois regulators). | Fay, James M:(ComEd) |  | Discussed on 8/31 and 9/7 TACs. There remains dispute as to whether there are marginal gas losses that are tied directly to end use consumption. If there are, it is understood that these are likely to be very low. Since this is a new proposed variable, there was not agreement on a value and likely to have negligible impact, decision to keep the variable in the algorithm but set to 0% for v10 with a footnote indicating this will continue to be discussed for v11. |  | y
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | TBD | It should also be noted that the supposition stated on a recent TAC call that gas losses are independent of throughput volumes has not been substantiated and this assumption should not be made in the TRM. | Fay, James M:(ComEd) |  | The gas utilities provided a number of references that they suggest support this supposition. As response above, the TAC did not have time to fully discuss this complex issue. We hope to be able to resolve in v11. |  | y
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | %IncentiveElectric = % of total incentive | See previous comment above re: the purpose of the TRM should be to determine a measure’s electricity and natural gas savings only. The TRM should not allocate savings based on how a measure is incentivized. | Stoll, Jacob J. : |  | See response above. |  | n/a
3 | RES | ICC | 5.4.4 | Low Flow Faucet Aerators | T | I need to better understand the rationale for the statement “This includes the effect of existing low flow fixtures and therefore the freerider rate for this measure should be 0.”Otherwise this should be deleted. | Morris, Jennifer |  | Done. Language moved and clarified |  | Y
3 | RES | ICC | 5.4.5 | Low Flow Showerheads | T | I need to understand the rationale for this statement “This includes the effect of existing low flow fixtures and therefore the freerider rate for this measure should be 0.” Otherwise this should be deleted. | Morris, Jennifer |  | Done. Language moved and clarified |  | Y
3 | RES | Opinion Dynamics | 5.4.1 | DHW Pipe Insulation |  | Should the below example be removed? It appears to be left in from an older version; the updated example is above. | Opinion Dynamics |  | Done - no change |  | Y
3 | RES | Opinion Dynamics | 5.4.1 | DHW Pipe Insulation |  | Should the below example be removed? It appears to be left in from an older version; the updated example is above. | Opinion Dynamics |  | Done - no change |  | Y
3 | RES | Nicor | 5.6.1 | Air Sealing | Distributed Self-Install Income-Qualified Kit | These should include at least some of the ~30% of participants that still plan to install kit contents. This current method is unrealistic as it assumes that none of those participants (who say they plan to install) actually follow through with their intended action.It is more reasonable to assume an addition 50% of those will be installed in year two, perhaps during colder weather months, similar to the policies applied to the ISR of the LED lamp protocol. (section 5.5.8) | Rohith Mannam | Footnote - if research shows that participants indicating that they plan to install, actually do install - these future installs can be claimed in a future through an errata. | Done - added footnote and deleted gas ISR table |  | n/a
3 | RES | Gas Utilities | 5.3.1 | Air Source Heat Pump | Hgrid = Heat rate of the grid in btuBTU/kWh over the lifetime of the measure. based on the average fossil heat rate for the EPA eGRID subregion and includes a factor that considers T&D losses. | The proposed calculations incorporate the Air Source Heat Pump (ASHP) load shape into the hourly PJM marginal generation mix; weighting them higher if they coincide with a time of higher ASHP load. This gave a slightly higher (1.2%) heat rate for the marginal mix based on the ASHP load curve. Since other models didn’t have the same hourly breakdown, a factor of 1.2% was applied everywhere. However, since this heat rate will apply to all other TRM fuel-switch measures as well, a common heat rate value (not dependent on measure or technology load shape) needs to be used across the TRM. We propose to remove the ASHP load shape adjustment and use the ‘Flat’ values in the spreadsheet. Note - Incorporating the above proposed changes would bring the 2022 heat rate to 8,800 Btu/kWh. | Manjarres, Thomas D |  | Discussed during 8/24, 8/31, 9/7 TAC calls. As predicted, opening up the VEIC proposed values to comments resulted in many opinions (often opposing) as to the appopriate adjustments. The SAG requested that VEIC provide a proposal, which we did. We acknowledge that there are many reasons the numbers could be adjusted higher or lower. We have added a footnote to commit to revisiting the assumption in v11 so have decided to stick with our proposal for v10. |  | n/a
3 | RES | Gas Utilities | 5.3.1 | Air Source Heat Pump | For calculating eligibility, the average LifetimeHgrid of 7,700 BTU/kWh. | As discussed in the June 21 and July 15 SAG Fuel Conversion Working Group meetings, using a predicted lifetime heat rate for the source energy savings test would give rise to additional policy questions that have not been addressed. These policy questions include, but are not limited to: Is a measure that increases energy consumption today, but could potentially save energy in the future eligible for fuel switching?Example: source energy savings are negative when using first year heat rate and positive when using lifetime heat rate.Can savings be claimed in the current 4-year plan cycle from a measure that is not projected to save energy until a future plan cycle? As proposed, the SourceEnergySavings term is calculated using the projected lifetime heat rate, which leads to a larger value than if it were calculated using the first year heat rate. The first year savings claimed by the programs are proportional to SourceEnergySavings, which means the programs will be claiming more savings in year one than exist in year one. According to IL statute, does a measure that increases total electric delivery load qualify as energy efficiency? | Manjarres, Thomas D |  | See response above. |  | n/a
3 | RES | Gas Utilities | 5.3.1 | Air Source Heat Pump | For calculating eligibility, the average LifetimeHgrid of 7,700 BTU/kWh. For calculating savings, apply a first year heat rate of 8,600 BTU / kWh for 6 years followed by 7,200 BTU/kWh for the remaining measure | These statements do not match the algorithms in the savings allocation table. | Manjarres, Thomas D |  | Agreed. The variables are now seperately provided (LifetimeHgrid, FirstYearHgrid and PostAdjHgrid) and algorithms appropriately set up to clearly show how the calculations should be performed. |  | y
3 | RES | Gas Utilities | 5.3.1 | Air Source Heat Pump | For calculating eligibility, the average LifetimeHgrid of 7,700 BTU/kWh. For calculating savings, apply a first year heat rate of 8,600 BTU / kWh for 6 years followed by 7,200 BTU/kWh for the remaining measure | Instead of setting the first year heat rate for 6 years as proposed, a 4-year period would be both logical and practical since this would coincide with the quadrennial planning cycle of the utilities. The end of the utility four year cycle would serve as a good time to re-evaluate the heat rate based on the new grid mix at that point (2025). The re-evaluated heat rate would then be used for the next utility quadrennial cycle in the TRM. This process of re-evaluating the heat rate every 4 years would serve to replace the lifetime heat rate and the post-midlife adjusted heat rates that are currently proposed. The 4-yr review period is a long enough time to reflect significant changes in the power generation mix while allowing for plan cycles to be designed with the best information at a time when stakeholders can provide input into plans with this updated information vs in the middle of a cycle. | Manjarres, Thomas D |  | Discussed on 8/31 TAC. The midlife adjustment is provided after 6 years, since when treated as an early replacement measure, there will already be a midlife adjustment accounting for the change in efficiency of existing to new baseline units. Timing this adjustment differently would require a single measure to have multiple adjustments during the measure life. This does not suggest that re-evaluting the heat rate will only occur after 6 years. We are committed to revisiting next year to explore further the different views on the appropriate values, and beyond that believe it will be worth reviewing regularly and whenever a major grid change occurs. |  | n/a
3 | RES | Gas Utilities | 5.3.1 | Air Source Heat Pump | "For the purposes of forecasting load reductions due to fuel switch GSHP projects…" | Update to be specific to air source heat pumps. | Manjarres, Thomas D |  | Agreed. Fixed |  | n/a
3 | RES | Gas Utilities | 5.3.1 | Air Source Heat Pump | ΔkWh = - [ASHP heating consumption] + [Cooling savings] | See policy question 3 in the H grid comment. ∆kWh is negative, does that affect its ability to participate in electric or gas programs? | Manjarres, Thomas D |  | Agreement that requirement is that total source energy savings is positive. |  | n/a
4 | CC | Guidehouse |  | NTG | Nicor Gas | Updated needed per attached spreadsheet | Kevin Grabner |  | Update provded by Opinion Dynamics on 9/8 incorporated.
4 | CC | Guidehouse |  | NTG | Peoples Gas/ North Shore Gas | Updated needed per attached spreadsheet | Kevin Grabner |  | Update provded by Opinion Dynamics on 9/8 incorporated.
4 | CC | Guidehouse |  | NTG | Nicor Gas | Updated needed per attached spreadsheet | Kevin Grabner |  | Update provded by Opinion Dynamics on 9/8 incorporated.
4 | CC | Guidehouse |  | NTG | Peoples Gas/ North Shore Gas | Updated needed per attached spreadsheet | Kevin Grabner |  | Update provded by Opinion Dynamics on 9/8 incorporated.

## Almost Final Comments
Volume | Sector | Client | Section | Measure Name | Comment scope | Comment text | Author | VEIC Assignment | VEIC Response | TAC Discussion?
3 | RES | Ameren | 5.3.1 | Air Source Heat Pump | "the Time of Sale or Federal Standard efficiency level" | Suggested to change to "likely unknown" | Vaughn, Andrew C | Sam | Upon review with the TAC on 9/21, decision to remove deemed unknown assumptions this year. Additional language added that for Time of Sale assumptions when the existing equipment is unknown the baseline should be determined via EM&V. | 2021-09-21
3 | RES | Ameren | 5.3.1 | Air Source Heat Pump | 8.2 HSPF | Suggested to change to "≤8.2 HSPF" | Vaughn, Andrew C | Sam | See above | 2021-09-21
3 | RES | Ameren | 5.3.1 | Air Source Heat Pump | Note the above default HSPF assumes an ASHP baseline. | Suggest deleting this sentence | Vaughn, Andrew C | Sam | See above | 2021-09-21
3 | RES | Ameren | 5.3.1 | Air Source Heat Pump | Midstream Program (Time of Sale): | Suggested addition of sentence at the end of this paragraph " Alternatively, a blended average can be used if determined suitable by evaluators based on data available on a deemed basis before the program year starts." | Vaughn, Andrew C | Sam | See above | 2021-09-21
3 | RES | Ameren | 5.3.20 | Residential Energy Recovery Ventilator (ERV) | Exist_Exh_Fan_Use Algorithm | Seems like there may be a factor missing for how well a base case fan pulls the rated CFM compared to an ERV since the ERV provides a path for both incoming and outgoing CFM. If possible and there is time available, we would like to discuss this on the final TAC call. I don't think it will be a long conversation. | Vaughn, Andrew C | Sam | Discussion on TAC on 9/21. Decision that the existing algorithm is reasonable. Potential updates could be proposed for v11. | 2021-09-21
3 | RES | Ameren | 5.4.4 | Low Flow Faucet Aerators | ∆kWh example calculations | First example should be EPG_electric = 0.1054 Second example should be EPG_electric = 0.879 | Vaughn, Andrew C | Sam | Agreed. Fixed | N/A
4 | CC | Ameren | Attachment B | Effective Useful Life for Custom Measures | 13 (tunnel washers) | Suggest removing or resolving with Section 4.3.11 | Vaughn, Andrew C | Sam | Agreed. Removed | 2021-09-21
4 | CC | Ameren | Attachment B | Effective Useful Life for Custom Measures | Add Doors to Open Refrigerated Cases: 10 (new cases) 3.3 (retrofits) | Suggest removing. Section 4.6.13 has a more recent update | Vaughn, Andrew C | Sam | Agreed. Removed | 2021-09-21
4 | CC | Ameren | Attachment B | Effective Useful Life for Custom Measures | Commercial Dishwasher | Suggest removing. Repeat of 4.2.6 | Vaughn, Andrew C | Sam | Agreed. Removed | 2021-09-21
3 | RES | ComEd | 5.3.1 | Air Source Heat Pump | Midstream Program (Time of Sale) | I think in one of my previous comments on this issue, I left out the word “not”. My mistake. I meant to say that we should not assume the “Unknown Baseline” is always and only associated with the Midstream Program. Unknown Baseline Midstream Program (Time of Sale): If the equipment qualifies for rebates under the midstream program, and the baseline equipment is unknown (for example, in a Midstream Program), the Time of Sale or Federal Standard efficiency level. the baseline equipment values specified below can be used for these program types | Jim Fay | Sam | Upon review with the TAC on 9/21, decision to remove deemed unknown assumptions this year. Additional language added that for Time of Sale assumptions when the existing equipment is unknown the baseline should be determined via EM&V. | 2021-09-21
4 | CC | Ameren | 5.3.1 | Air Source Heat Pump | Midstream Program (Time of Sale) | In our 8/30/21 e-mail, we provided historical program baseline data as follows (I am using round numbers and adding new construction to ASHP Baseline): Air Source HP: Electric Resistance (30%), ASHP (70%) Ductless HP: Electric Resistance (20%), ASHP (30%), Natural Gas Furnace/Boiler (50%). When this was discussed on a recent TAC call, we thought it was decided that a determination of what the customer would otherwise have done is clearly the responsibility of the Independent Evaluator. The current draft of the TRM still assumes customer intent (an evaluation result) and then adds a statement that evaluation results can change the baseline. We think the TRM should use historical baselines to keep the separation between evaluation and the TRM and to be consistent with other TRM sections that address unknown baselines. Any adjustments to baselines or savings based on evaluation research can still be made by the evaluators when they have a basis for doing so. If Program History Baselines are used, the caveat below is not needed. Note the above default HSPF assumes..... | Jim Fay | Sam | See above | 2021-09-21
2 and 3 | C&I and RES | Resouce Innocations | 4.5.4 and 5.5.6 | LED Bulbs and Fixtures, and LED Specialty Lamps | Delta watts table | I am reaching out about MR16 and R20 Bulb wattage assumptions included in the LED Bulbs and Fixtures Measure (V10 Almost Final Draft, screenshot included below for reference). The delta watts calculated in this table for the last 5 line items do not match up with the difference between the baseline and efficient wattage assumptions. Could you please advise on which of these values are correct? | Sanjyot Varade | Sam | Upon review there was a copy error in these tables. Both have been fixed and the correct delta watts applied. | 2021-09-21