2022 Illinois Statewide Technical Reference Manual for Energy Efficiency

Version 10.0

Volume 2: Commercial and Industrial Measures

FINAL

September 24, 2021

Effective:

January 1, 2022

[intentionally left blank]

Volume 1: Overview and User Guide

Volume 2: Commercial and Industrial Measures	9

4.1	Agricultural End Use	9

4.1.1	Engine Block Timer for Agricultural Equipment	9

4.1.2	High Volume Low Speed Fans	11

4.1.3	High Speed Fans	13

4.1.4	Livestock Waterer	15

4.1.5	Fan Thermostat Controller	17

4.1.6	Low Pressure Sprinkler Nozzles	20

4.1.7	Milk Pre-Cooler	22

4.1.8	VSD Milk Pump with Plate Cooler Heat Exchanger	25

4.1.9	Scroll Compressor for Dairy Refrigeration	28

4.1.10	Dairy Refrigeration Heat Recovery	31

4.1.11	Commercial LED Grow Lights	35

4.1.12	Swine Heat Pads	40

4.1.13	Irrigation Pump VFD	44

4.1.14	High Efficiency Grain Dryer	48

4.1.15	Grain Dryer Tune-Up	55

4.1.16	Greenhouse Boiler Tune-Up	60

4.1.17	Greenhouse Thermal Curtains	63

4.1.18	Infrared Film for Greenhouse	66

4.1.19	ENERGY STAR Dairy Water Heater	69

4.2	Food Service Equipment End Use	74

4.2.1	Combination Oven	74

4.2.2	Commercial Solid and Glass Door Refrigerators & Freezers	81

4.2.3	Commercial Steam Cooker	84

4.2.4	Conveyor Oven	91

4.2.5	ENERGY STAR Convection Oven	93

4.2.6	ENERGY STAR Dishwasher	96

4.2.7	ENERGY STAR Fryer	106

4.2.8	ENERGY STAR Griddle	111

4.2.9	ENERGY STAR Hot Food Holding Cabinets	116

4.2.10	Ice Maker	119

4.2.11	High Efficiency Pre-Rinse Spray Valve	123

4.2.12	Infrared Charbroiler	128

4.2.13	Rotisserie Oven	130

4.2.14	Infrared Salamander Broiler	132

4.2.15	Infrared Upright Broiler	134

4.2.16	Kitchen Demand Ventilation Controls	136

4.2.17	Pasta Cooker	139

4.2.18	Rack Oven - Double Oven	141

4.2.19	ENERGY STAR Electric Convection Oven	143

4.2.20	Efficient Dipper Wells	147

4.2.21 On-Demand Package Sealers – Provisional Measure	151

4.3	Hot Water	154

4.3.1	Water Heater	154

4.3.2	Low Flow Faucet Aerators	166

4.3.3	Low Flow Showerheads	174

4.3.4	Commercial Pool Covers	180

4.3.5	Tankless Water Heater – Measure combined with 4.3.1 Water Heater in Version 8	183

4.3.6	Ozone Laundry	184

4.3.7	Multifamily Central Domestic Hot Water Plants	192

4.3.8	Controls for Central Domestic Hot Water	196

4.3.9	Heat Recovery Grease Trap Filter	200

4.3.10	DHW Boiler Tune-up	204

4.3.11	Tunnel Washers	208

4.3.12	Tank Insulation	212

4.4	HVAC End Use	216

4.4.1	Air Conditioner Tune-up	221

4.4.2	Space Heating Boiler Tune-up	224

4.4.3	Process Boiler Tune-up	227

4.4.4	Boiler Lockout/Reset Controls	230

4.4.5	Condensing Unit Heaters	232

4.4.6	Electric Chiller	234

4.4.7	ENERGY STAR and CEE Tier 2 Room Air Conditioner	240

4.4.8	Guest Room Energy Management (PTAC & PTHP)	243

4.4.9	Air and Water Source Heat Pump Systems	250

4.4.10	High Efficiency Boiler	262

4.4.11	High Efficiency Furnace	265

4.4.12	Infrared Heaters	272

4.4.13	Package Terminal Air Conditioner (PTAC) and Package Terminal Heat Pump (PTHP)	275

4.4.14	Pipe Insulation	281

4.4.15	Single-Package and Split System Unitary Air Conditioners	299

4.4.16	Steam Trap Replacement or Repair	308

4.4.17	Variable Speed Drives for HVAC Pumps and Cooling Tower Fans	315

4.4.18	Small Commercial Programmable Thermostats – Retired 12/31/2019. Replaced with 4.4.48 Small Commercial Thermostats	319

4.4.19	Demand Controlled Ventilation	320

4.4.20	High Turndown Burner for Space Heating Boilers	325

4.4.21	Linkageless Boiler Controls for Space Heating	328

4.4.22	Oxygen Trim Controls for Space Heating Boilers	330

4.4.23	Shut Off Damper for Space Heating Boilers or Furnaces	332

4.4.24	Small Pipe Insulation	334

4.4.25	Small Commercial Programmable Thermostat Adjustments – Retired 12/31/2019.	340

4.4.26	Variable Speed Drives for HVAC Supply and Return Fans	341

4.4.27	Energy Recovery Ventilator	347

4.4.28	Stack Economizer for Boilers Serving HVAC Loads	352

4.4.29	Stack Economizer for Boilers Serving Process Loads	355

4.4.30	Notched V Belts for HVAC Systems	358

4.4.31	Small Business Furnace Tune-Up	366

4.4.32	Combined Heat and Power	369

4.4.33	Industrial Air Curtain	377

4.4.34	Destratification Fan	387

4.4.35	Economizer Repair and Optimization	394

4.4.36	Multi-Family Space Heating Steam Boiler Averaging Controls	403

4.4.37	Unitary HVAC Condensing Furnace	405

4.4.38	Covers and Gap Sealers for Room Air Conditioners	413

4.4.39	High Temperature Heating and Ventilation (HTHV) Direct Fired Heater	419

4.4.40	Gas High Efficiency Single Package Vertical Air Conditioner	425

4.4.41	Advanced Rooftop Controls (ARC)	429

4.4.42	Advanced Thermostats for Small Commercial – Retired 12/31/2019. Replaced with 4.4.48 Small Commercial Thermostats	437

4.4.43	Packaged RTU Sealing	438

4.4.44	Commercial Ground Source and Ground Water Source Heat Pump	443

4.4.45	Adsorbent Air Cleaning	466

4.4.46	Server Room Temperature Set back	471

4.4.47	Air Deflectors for Unit Ventilators – Provisional Measure	474

4.4.48	Small Commercial Thermostats	476

4.4.49	Boiler Chemical Descaling	481

4.4.50	Electric Chillers with Integrated Variable Speed Drives	484

4.4.51	Advanced Rooftop Controls with High Rotor Pole Switch Reluctance Motors	491

4.4.52	Hydronic Heating Radiator Replacement	499

4.4.53	HVAC Supply, Return and Exhaust Fans - Fan Energy Index	504

4.4.54	Process Heating Boiler	510

4.4.55	Commercial Gas Heat Pump	514

4.5	Lighting End Use	531

4.5.1	Commercial ENERGY STAR Compact Fluorescent Lamp (CFL) – Retired 12/31/2018, Removed in v8	536

4.5.2	Fluorescent Delamping	537

4.5.3	High Performance and Reduced Wattage T8 Fixtures and Lamps	541

4.5.4	LED Bulbs and Fixtures	554

4.5.5	Commercial LED Exit Signs	570

4.5.6	LED Traffic and Pedestrian Signals	574

4.5.7	Lighting Power Density	577

4.5.8	Miscellaneous Commercial/Industrial Lighting	592

4.5.9	Multi-Level Lighting Switch	596

4.5.10	Lighting Controls	599

4.5.11	Solar Light Tubes	605

4.5.12	T5 Fixtures and Lamps	608

4.5.13	Occupancy Controlled Bi-Level Lighting Fixtures	617

4.5.14	Commercial ENERGY STAR Specialty Compact Fluorescent Lamp (CFL) – Retired 12/31/2018, Removed in v8	621

4.5.15	LED Open Sign	622

4.5.16	LED Streetlighting	626

4.5.17	Exterior Photocell Repair	629

4.6	Refrigeration End Use	631

4.6.1	Automatic Door Closer for Walk-In Coolers and Freezers	631

4.6.2	Beverage and Snack Machine Controls	633

4.6.3	Door Heater Controls for Cooler or Freezer	637

4.6.4	Electronically Commutated Motors (ECM) for Walk-in and Reach-in Coolers / Freezers	640

4.6.5	ENERGY STAR Refrigerated Beverage Vending Machine	643

4.6.6	Evaporator Fan Control for Electrically Commutated Motors	646

4.6.7	Strip Curtain for Walk-in Coolers and Freezers	649

4.6.8	Refrigeration Economizers	652

4.6.9	Night Covers for Open Refrigerated Display Cases	655

4.6.10	High Speed Rollup Doors	658

4.6.11	Q-Sync Motors for Walk-in and Reach-in Coolers/Freezers	663

4.6.12	Variable Speed Drive for Condenser Fans	670

4.6.13	Add Doors to Open Refrigerated Display Cases	672

4.6.14	Floating Head Pressure Control	677

4.7	Compressed Air	681

4.7.1	VSD Air Compressor	681

4.7.2	Compressed Air Low Pressure Drop Filters	685

4.7.3	Compressed Air No-Loss Condensate Drains	688

4.7.4	Efficient Compressed Air Nozzles	691

4.7.5	Efficient Refrigerated Compressed Air Dryer	694

4.7.6	Vortex Tube Thermostat - Provisional Measure	697

4.7.7	Efficient Desiccant Compressed Air Dryer	700

4.7.8	Desiccant Dryer Dew Point Demand Controls	704

4.7.9	Compressed Air Heat Recovery	708

4.7.10	Compressed Air Storage Receiver Tank	711

4.7.11	Reduce Compressed Air Setpoint	715

4.7.12	AODD Pump Controls	718

4.8	Miscellaneous End Use	721

4.8.1	Pump Optimization	721

4.8.2	Roof Insulation for C&I Facilities	723

4.8.3	Computer Power Management Software	729

4.8.4	Modulating Commercial Gas Clothes Dryer	733

4.8.5	High Speed Clothes Washer	735

4.8.6	ENERGY STAR Computers	739

4.8.7	Advanced Power Strip – Tier 1 Commercial	743

4.8.8	High Efficiency Transformer	746

4.8.9	High Frequency Battery Chargers	750

4.8.10	Commercial Clothes Dryer Moisture Sensor	753

4.8.11	Efficient Thermal Oxidizers	757

4.8.12	Spring-Loaded Garage Door Hinge	762

4.8.13	Variable Speed Drives for Process Fans	767

4.8.14	Low Flow Toilets and Urinals	772

4.8.15	Smart Irrigation Controls	775

4.8.16	Commercial Weather Stripping	779

4.8.17	Switch Peripheral Equipment Consolidation	782

4.8.18	ENERGY STAR Uninterruptible Power Supply	786

4.8.19	Energy Efficient Rectifier	789

4.8.20	Energy Efficient Hydraulic Oils - Provisional Measure	792

4.8.21	Energy Efficient Gear Lubricants - Provisional Measure	795

4.8.22	Smart Sockets	798

4.8.23	Lithium Ion Forklift Batteries	802

4.8.24	Building Operator Certification	805

4.8.25	Warm-Mix Asphalt Chemical Additives	809

4.8.26	Energy Efficient Hand Dryers	812

Volume 3: Residential Measures

Volume 4: Cross Cutting Measures and Attachments

# Volume 2: Commercial and Industrial Measures

## Agricultural End Use

### Engine Block Timer for Agricultural Equipment

###### Description

The measure is a plug-in timer that is activated below a specific outdoor temperature to control an engine block heater in agricultural equipment. Engine block heaters are typically used during cold weather to pre-warm an engine prior to start, for convenience, heaters are typically plugged in considerably longer than necessary to improve startup performance. A timer allows a user to preset the heater to come on for only the amount of time necessary to pre-warm the engine block, reducing unnecessary run time even if the baseline equipment has an engine block temperature sensor.

This measure was developed to be applicable to the following program types: RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient measure is an engine block heater operated by an outdoor plug-in timer (15 amp or greater) that turns on the heater only when the outdoor temperature is below 25 °F.

###### Definition of Baseline Equipment

The baseline scenario is an engine block heater that is manually plugged in by the farmer to facilitate equipment startup at a later time.

###### Deemed Lifetime of Efficient Equipment

The expected measure life if assumed to be 3 years.

###### Deemed Measure Cost

The incremental cost per installed plug-in timer is $10.19.

###### Coincidence Factor

Engine block timers only operate in the winter, so the summer peak demand savings is zero.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

kWh 	= ISR * Use Season * %Days * HrSave/Day * kWheater - ParaLd

Where:

ISR 			= In Service Rate

= 78.39%

Use Season 	= The number of days in the use season in which the temperature drops below 25°F in the state of Illinois

= 75 days

%Days			= Propoortion of days timer is used with the Use Season

= 84.23%

HrSave/Day 		= Hours of savings per day when timer is used

= 7.765 hours per day

kWheater 			= Connected load of the engine block heater

= 1.5 kW

ParaLd			= Parasitic load

= 5.46 kWh

For example, using the default assumptions on the installation of a timer on an engine block with a 1.5 kW heater:

###### ΔkWh  	= 78.39% *   75 days * 84.23% * 7.765 Hr/Day * 1.5 kW -  5.46 kWh

= 571 kWh

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-EBLT-V02-190101

###### Review Deadline: 1/1/2024

### High Volume Low Speed Fans

###### Description

The measure applies to 20-24 foot diameter horizontally mounted ceiling high volume low speed (HVLS) fans that are replacing multiple non HVLS fans that have reached the end of useful life in agricultural applications.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be classified as HVLS and have a VFD.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline condition is assumed to be multiple non HVLS existing fans that have reached the end of useful life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

###### Deemed Measure Cost

The incremental capital cost for the fans are as follows:

| Fan Diameter Size (feet) | Incremental Cost |
| --- | --- |
| 20 | $4150 |
| 22 | $4180 |
| 24 | $4225 |

###### Loadshape

Loadshape C34 - Industrial Motor

###### Coincidence Factor

The measure has deemed kW savings therefore, a coincidence factor is not applied.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

The annual electric savings from this measure are deemed values depending on fan size and apply to all building types:

| Fan Diameter Size (feet) | kWh Savings |
| --- | --- |
| 20 | 6,577 |
| 22 | 8,543 |
| 24 | 10,018 |

###### Summer Coincident Peak Demand Savings

The annual kW savings from this measure are deemed values depending on fan size and apply to all building types:

| Fan Diameter Sixe (feet) | kW Savings |
| --- | --- |
| 20 | 2.4 |
| 22 | 3.1 |
| 24 | 3.7 |

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-HVSF-V02-190101

###### Review Deadline: 1/1/2024

### High Speed Fans

###### Description

The measure applies to high speed exhaust, ventilation and circulation fans that are replacing an existing unit that reached the end of its useful life in agricultural applications.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be diffuser equipped and meet the following minimum efficiency criteria.

| Diameter of Fan (inches) | Minimum Efficiency for Exhasut & Ventilation Fans | Minimum Efficiency for Circulation Fans |
| --- | --- | --- |
| 24 through 35 | 14.0 cfm/W at 0.10 static pressure | 12.5 lbf/kW |
| 36 through 47 | 17.1 cfm/W at 0.10 static pressure | 18.2 lbf/kW |
| 48 through 71 | 20.3 cfm/W at 0.10 static pressure | 23.0 lbf/kW |

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline condition is assumed to be an existing fan that reached the end of its useful life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 7 years.

###### Deemed Measure Cost

The incremental capital cost for all fan sizes is $150.

###### Loadshape

Loadshape C34 - Industrial Motor

###### Coincidence Factor

The measure has deemed kW savings therefore, a coincidence factor is not applied.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

The annual electric savings from this measure are deemed values depending on fan size and apply to all building types:

| Diameter of Fan (inches) | kWh |
| --- | --- |
| 24 through 35 | 372 |
| 36 through 47 | 625 |
| 48 through 71 | 1,122 |

###### Summer Coincident Peak Demand Savings

The annual kW savings from this measure are deemed values depending on fan size and apply to all building types:

| Diameter of Fan (inches) | kW |
| --- | --- |
| 24 through 35 | 0.118 |
| 36 through 47 | 0.198 |
| 48 through 71 | 0.356 |

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-HSF-V02-190101

###### Review Deadline: 1/1/2024

### Livestock Waterer

###### Description

This measure applies to the replacement of electric open waterers with sinking or floating water heaters with equivalent herd size watering capacity of the old unit. Livestock waterers utilize electric heating elements and are used in cold climate locations in order to prevent water from freezing. Energy efficient livestock waterers, also called no or low energy livestock waterers, are closed and insulated watering containers that use lower wattage heating elements, thermostatically controlled, and water agitation (either in the form of air bubbles or floating balls), to prevent water from freezing, using less energy.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to an electrically heated thermally insulated waterer with minimum 2 inches of insulation. A thermostat is required on unit with heating element greater than or equal to 250 watts.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to be an electric open waterer with sinking or floating water heaters that have reached the end of useful life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

###### Deemed Measure Cost

The incremental capital cost for the waterers are $787.50:

###### Loadshape

Loadshape C04 - Non-Residential Electric Heating

###### Coincidence Factor

Heated livestock waterers only operate in the winter in order to keep water from freezing so the summer peak coincident demand savings is zero.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

The annual electric savings from this measure is a deemed value and assumed to be 1,592.85 kWh.

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-LSW1-V03-190101

###### Review Deadline: 1/1/2024

### Fan Thermostat Controller

###### Description

Incorporating a ventilation fan thermostat controller can reduce energy consumed where livestock is housed. Livestock ventilation fans reduce heat stress during the warmer months of the year.

For the purposes of this measure characterization, the installed ventilation fan thermostat controllers are temperature based on/off controls. While the complexity and intelligence of available controls can vary widely, where integrated controls can automate multiple modes and stages of ventilation, this measure assumes the control functionality is turning off the fan once the temperature falls to a certain point. It is recommended that other intelligent control technologies and strategies be handled through a custom approach, as these control installations require commissioning to optimize the functionality based on unique site and design considerations.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

This measure applies to the incorporation of thermostatic controller for ventilation fans used in the livestock industry. To qualify, the ventilation fan must be used to modulate the temperature to reduce heat stress in a livestock facility.

###### Definition of Baseline Equipment

The baseline for this measure is a non-thermostatically controlled livestock ventilation fan that operates constantly in their maximum capacity.

###### Deemed Lifetime of Efficient Equipment

The life expectancy of this measure is 15 years.

###### Deemed Measure Cost

The incremental cost is estimated at $50 per fan.

###### Loadshape

Loadshape C34 – Industrial Motor

###### Coincidence Factor

The savings come from a reduction in nighttime operation, so a coincidence factor is not applicable for this measure.

Algorithm

###### Calculation of Energy Savings

The annual energy savings are generated by the fan being disabled at temperatures below 70°F. Typically the evening hours are cooler, and the ventilation fans are not required at these lower temperatures. It is assumed, prior to retrofit, that baseline ventilation fans are operating continuously from May 1st through October 31st, encapsulating the entire portion of the year in which hot temperatures exist and the need for livestock housing ventilation is prevalent. The efficient fan operation is derived from regional TMY3 data for the state of Illinois and represent, over the same timeline that was used for the baseline, the number of hours in which the temperature is above 70°F.  Electric Energy Savings

∆kWhHP=HPFan×LF×CME×∆Hours÷Effmotor

Where:

HPFan		= Motor horsepower of the controlled fan

= Actual; if unknown, default to 1 horsepower

LF		= Fan load factor

= 0.75

CME		= 0.746 kW to HP conversion factor

∆Hours	= Reduction in fan run hours as a result of the thermostat controller, dependent on location

| Zone | HoursBase | HoursEff | ΔHours |
| --- | --- | --- | --- |
| Rockford | 4,416 | 1,559 | 2,857 |
| Chicago | 4,416 | 1,596 | 2,820 |
| Springfield | 4,416 | 2,054 | 2,362 |
| Belleville | 4,416 | 2,148 | 2,268 |
| Marion | 4,416 | 2,224 | 2,192 |

For example, using the default assumptions on a 1 horsepower fan thermostat controller for a single fan on a farm in Marion:

ΔkWh=1 HP×0.75×0.746×2,192 hours / 82.5% efficency

= 1,487 kWh

Effmotor		= 82.5%, motor efficiency

###### Summer Coincident Peak Demand Savings

N/A – Assume fans will be in operation at maximum capacity during the coincident peak demand periods, resulting in zero potential demand savings during the hottest periods of the summer.

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-FNTC-V01-200101

###### Review Deadline: 1/1/2024

### Low Pressure Sprinkler Nozzles

###### Description

Incorporating low pressure sprinkler nozzles can decrease the energy and water consumed by reducing required water supply pressure to irrigate crop fields. Low pressure sprinkler nozzles can provide uniform water application by using various orifice applications and configurations while operating at a lower pressure compared to standard, impact driven sprinkler heads. Energy savings are achieved by the irrigation system operating at a lower water pressure while maintaining the same water distribution.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Low Pressure Irrigation Nozzles operate at 35 psi or lower at rated/required flow. Annual Electric Savings obtained will be based on the number of nozzles replaced. To qualify the nozzles must operate for more than 500 hours per year and provide the equivalent flow at the reduced pressure. The maximum pump pressure must also be reduced accordingly.

###### Definition of Baseline Equipment

This measure applies to the replacement of high pressure irrigation nozzles that operate at 50 psi or greater at rated/required flow.

###### Deemed Lifetime of Efficient Equipment

The life expectancy of this measure is 5 years.

###### Deemed Measure Cost

The incremental cost, including labor, is $1.74 per nozzle.

###### Loadshape

Loadshape C59 – Agriculture and Well Pumping

###### Coincidence Factor

Coincidence Factor = 0.793

Algorithm

###### Calculation of Energy Savings

The annual energy savings and coincidental electric demand savings is based on PG&E research on irrigation well pumping systems and corrected based upon the type of crop, irrigated acres, and average acre-feet of water applied per acre.

###### Electric Energy Savings

Annual kWh Savings = 4.06 kWh/yr/nozzle

###### Summer Coincident Peak Demand Savings

Annual kW Savings = 0.0017 kW/yr/nozzle

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-LPSN-V01-200101

###### Review Deadline: 1/1/2024

### Milk Pre-Cooler

###### Description

There is energy savings for adding a plate heat exchanger (pre‐cooler) ahead of the milk storage tank. This addresses the electrical energy savings associated with the decreased milk cooling load. Installing a pre‐cooler reduces milk temperature from 100°F to 55-70°F before it enters the bulk tank.

It is important to determine if the site has an adequate supply of water, as milk plate coolers require 1 to 2 times the amount of water as compared to processed milk, to be effective. However, sites leveraging plate coolers will repurpose the warm, discharged water, either for watering cows, wash-down, or other purposes on the farm. As there are indirect benefits associated with the warmer water, and because it is typically repurposed, it is assumed that there are no negative water impacts for this measure. There are also no interactive domestic hot water savings attributable to the installation of a pre-cooler as the discharged water is typically not re-directed to the existing hot water heater.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The installation of the heat exchanger to decrease the cooling requirement of the primary milk bulk tank refrigeration system. The heat exchanger fluid medium used for heat rejection is well or ground water as this produces the largest temperature differential for energy savings. For water requirements, the water supply system must have capacity to keep up with the existing farm water demands and additional demands of the pre‐cooler. To minimize the volume of water used for pre-cooling, a solenoid valve should be installed on the water supply line to the pre‐cooler and be actuated only when the milk pump is in operation. A bypass line around the solenoid valve or a time delay relay can also be used to provide additional cooling of the residual milk in the pre‐cooler between pumping cycles. A storage tank will be necessary for used cooling water storage until it is re‐used for watering cows, cleanup or another purpose on the farm.

###### Definition of Baseline Equipment

The baseline conditions assume that no previous pre‐cooler heat exchanger was installed and the entire milk cooling load is on the milk bulk tank.

###### Deemed Lifetime of Efficient Equipment

The life expectancy of this measure is 15 years.

###### Deemed Measure Cost

The average equipment cost of a plate cooler is $2,950 with an installation cost of $494, for a total incremental measure of $3,444.

###### Loadshape

Loadshape C58 – Farm Plate Cooler / Heat Recovery Unit

###### Coincidence Factor

Coincidence factor of 0.16

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Milk Pre-Cooler Heat Exchanger – Chiller Savings

∆kWh=∆T×Lbs of Milk×Cows×Cp,m×DaysEER×1,000

Where:

∆T		= Change in milk temperature attributable to the pre-cooler

= 30˚F

Lbs of Milk	= The pounds of milk produced per day that needs to be cooled

= 68 lbs of milk per cow

Cows		= Number of milking cows per farm

= Actual; if unknown use 101

Cp,m		= Specific heat of milk

= 0.93 Btu/lb ˚F

Days		= 365 days/yr

EER		= Efficiency of the existing compressor

= 8.0 Btuh/watt

1,000		= 1,000 Watts to kW conversion factor

###### Summer Coincident Peak Demand Savings

∆kW=∆kWhHours×CF

Where:

Hours		= 2920 hours

CF		= 0.16

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-MLKP-V01-200101

###### Review Deadline: 1/1/2024

### VSD Milk Pump with Plate Cooler Heat Exchanger

###### Description

This technology incorporates adding a variable speed drive to a milk transfer pump. The VSD drive reduces the heat transferred to milk during pumping operation as well increases the amount of time the milk is in the free cooling heat exchanger. The VFD regulates the milk pump in order to increase the efficacy of the plate cooler heat exchanger by slowing the flow of milk. This results in a maximum heat transfer between the warm milk and the cold water used in the plate cooler.

Energy savings are realized by the reduced load on the primary milk cooling system. A milk transfer pump VSD is only effective if paired with a plate cooler.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Installation of a new variable speed drive (VSD) on a new or existing milk transfer process pump.

###### Definition of Baseline Equipment

Must have a constant speed milk transfer process pump with no existing VSD controls. A plate cooling heat exchanger can already be a part of the system, or one installed in concert with the VSD.

###### Deemed Lifetime of Efficient Equipment

The life expectancy of this measure is 15 years.

###### Deemed Measure Cost

The average equipment cost of a milk vacuum pump variable speed drive is $3,871 with an installation cost of $1,177, for a total incremental measure of $5,048.

###### Loadshape

Loadshape C57 – Milk Pump

###### Coincidence Factor

There are no summer coincident peak savings for VFD dairy milk pumps. Through research of refrigeration compressor power demands, no substantial evidence has arisen that any notable kW demand reduction is possible in relation to using a VFD with a milk pre-cooler to pre-cool milk that would otherwise need to be chilled through mechanical refrigeration means.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh=1EER×Cp,m×∆T×Lbs of Milk×Cows×Days / 1,000

Where:

EER		= Efficiency of the existing compressor

= 8.0 Btu/watt

Cp,m		= Specific heat of milk

= 0.93 Btu/lb ˚F

∆T	= Change in milk temperature as a result of the milk transfer pump VSD. This value is the additional benefits of a VSD on the milk pump over a standard plate cooler

= 11.7 ˚F

Lbs of Milk	= The pounds of milk produced per day that needs to be cooled

= 68 lbs of milk per cow

Cows	= Number of milking cows per farm

= Actual, if unknown use 101

Days	= 365 days of milking per year

For example, using the default assumptions, the average kWh savings resulting from the installation of a milk transfer pump VSD is:

∆kWh=18.0 Btu/Watt×0.93×11.7°F×68lbsmilk/cow×101 cows×365daysyr/ 1,000=3,410 kWh

1,000	= Watts to kW conversion factor

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-VSDM-V01-200101

###### Review Deadline: 1/1/2024

### Scroll Compressor for Dairy Refrigeration

###### Description

Incorporating a more efficient compressor for process milk refrigeration can decrease the energy consumed at dairy farms. This measure is for the installation of a scroll compressor to replace an existing reciprocating compressor on a milk refrigeration bulk tank. The milk refrigeration system is used to cool milk for preservation and packaging. Milk is extracted from the cow at 98°F and cooled to 38°F, resulting in a substantial load on the milk cooling equipment, which is typically the largest energy use on a dairy farm. Scroll compressors can provide increased refrigeration efficiencies with improved EERs over baseline reciprocating compressors.

The energy savings for this measure is dependent on if the site is utilizing pre-cooling equipment such as a milk plate cooler. Plate coolers can reduce the incoming temperature of the milk into the refrigeration bulk tank, reducing the overall load on the compressor and the potential savings benefits.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

For an efficient scroll compressor with or without a plate cooler heat exchanger, the proposed compressor must be rated at 10.6 EER or greater on a process milk refrigeration system. The calculation assumes the cooling capacity of the compressor remains the same.

###### Definition of Baseline Equipment

The baseline condition is assumed to be a reciprocating compressor.

###### Deemed Lifetime of Efficient Equipment

The expected life of this measure is 15 years.

###### Deemed Measure Cost

The incremental cost is $447 per compressor.

###### Loadshape

Loadshape C56 – Dairy Farm Combined End Use

###### Coincidence Factor

Coincidence factor of 0.34

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

∆kWh=1EERbase-1EEReff×Process Load1,000

Where:

EERbase		= Efficiency of the existing compressor

= 8.4 Btu/watt

EEReff		= Efficiency of the installed, scroll compressor

= 10.6 Btu/watt

Process Load		= CP,Milk×∆T×Lbs of Milk×Cows×Days

Where:

CP,Milk		= Specific heat of milk

= 0.93 Btu/lb ˚F

∆T		= Change in milk temperature as result of the primary cooling system

= 60˚F without a milk plate cooler

= 30˚F with a milk plate cooler

Lbs of Milk	= The pounds of milk produced per day that needs to be cooled

= 68 lbs of milk per cow

Cows		= Number of milking cows per farm

= Actual; if unknown use 101

Days		= 365 days per year

1,000		= 1000 watts to kW conversion factor

For example, using the default assumptions, average kWh savings of an installed scroll compressor on the milk refrigeration bulk tank with a dairy using an existing plate cooler is:

∆kWh=18.4 EER-110.6 EER×0.93 Btulb of Milk×98℉-30℉-38℉×68lbs milkcow×101 cows×365 Days1000 Watts/kW

∆kWh=1,728 kWh

###### Summer Coincident Peak Demand Savings

∆kW= ∆kWhHours ×CF

Where:

Hours		= 2,920 hours

CF 		= 0.34

For example, using the default assumptions, average coincident peak demand savings of an installed scroll compressor on the milk refrigeration bulk tank with a dairy using an existing plate cooler is:

∆kW= 1,728 kWh2,920 Hours ×0.34

∆kW=0.201 kW

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

###### Measure Code: CI-AGE-SCRC-V01-200101

###### Review Deadline: 1/1/2024

### Dairy Refrigeration Heat Recovery

###### Description

A refrigeration heat recovery (RHR) unit captures waste heat from the refrigeration system and uses a heat exchange to transfer some of that heat into incoming well water. That captured waste heat is used to pre-heat ground water before it enters the primary water heater and brought to the desired final temperature needed for cleaning farm equipment. The hot compressed refrigerant is diverted and flows through the heat exchanger, attached to a secondary water tank, on its way to the condenser unit. The heat from the refrigerant is transferred through the tank into the water. Thermal buoyancy causes the warmest water to rise to the top of the tank. When hot water is used, water flows from the RHR tank into the water heater, and well water flows into the heat recovery tank. These units can assist in reducing water heating energy use by approximately 50%.

It is important to note that if a dairy farm installs an RHR unit and a milk plate cooler, (with or without the use of milk pump VFD control), the plate cooler will impact the savings potential of the RHR unit. The use of a plate cooler will reduce the total milk mechanical refrigeration load. Due to this refrigeration load reduction, the amount of heat rejection possible to the RHR system is diminished.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient condition is farm refrigeration equipment where an RHR tank is installed and captures waste refrigerant heat from the refrigeration system compressor and transfers that waste into an RHR tank, supplied with cool ground water, through a heat exchanger before continuing through the refrigeration system condensing unit. The newly preheated water in the RHR tank is supplied into the farm’s main water heater unit, which will have a smaller temperature differential to overcome, compared to a direct ground water heater feed.

###### Definition of Baseline Equipment

The baseline condition is an existing dairy farm with refrigeration equipment and a water heater unit without the use of an RHR unit to feed preheated water to the water heater. Water heater is fed directly with ground water.

###### Deemed Lifetime of Efficient Equipment

The expected useful life is 15 years.

###### Deemed Measure Cost

The incremental cost is $4,353.

###### Loadshape

Loadshape C58 – Farm Plate Cooler / Heat Recovery Unit

###### Coincidence Factor

There are no summer coincident peak savings for RHR units. It is assumed that electric water heaters have a single element and will still be used to heat water up to full temperature, and that the kW rating is unchanged when an RHR unit is added in the water heating loop (resulting in no demand reduction).

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

∆kWh=BtuRecovered ×Days × 1EFelec/ 3,412

Where:

BtuRecovered=BtuMilk Potential or BtuRHR Storage (lesser of the two)

Where:

BtuMilk Potential=Lbs of Milk ×Cows ×CP,Milk×∆TMilk×SF

and

BtuStorage=Hot Water×CP,Water×PWater×∆TWater

Days		= Number of milking days per year

= 365 days

3,412		= Btu to kWh electric conversion factor

EFelec		= Energy factor for a standard electric water heater

= 90%

Lbs of Milk	= The pounds of milk produced per day per cow that needs to be cooled

=68 lbs of milk per cow

Cows		= Number of milking cows per farm

= Actual, if unknown use 101

CP,Milk	= Specific heat of milk

= 0.93 Btu/(lb-˚F)

∆TMilk	= Change in milk temperature

= ˚FIN - ˚FFINAL

˚FIN	= Temperature of milk being supplied that needs to be cooled

= 98˚F if no pre-cooler is used in operation; 68˚F if a milk pre-cooler is used; 56.3˚F if a milk pre-cooler and VFD milk transfer pump are used.

˚FFINAL	= Final stored temperature of cooled milk

= 38˚F

SF	= Savings factor for the percentage of energy able to be captured from the milk cooling process

= 55%

Hot Water	= Amount of hot water per day in gallons that the site uses for washing and cleaning purposes

= 131.7 gallons

CP,Water	= Specific heat of water

= 1 Btu/lb-˚F

PWater	= Density of water

= 8.34 lbs/gallon

∆TWater	= Temperature difference = Tempwarm water – Tempcold water

Tempwarm water	= 120˚F, expected temperature a refrigeration heat recovery unit can pre-heat well water up to.

Tempcold water	= 52.3˚F, average well water temperature

###### Summer Coincident Peak Demand Savings

###### Natural Gas Savings

∆Therms=BtuRecovered ×Days ×1EFgas/ 100,000

100,000		=Btu to therms natural gas conversion factor

EFgas		= Energy factor for a standard natural gas water heater

= 59%

Other variables remain consistent with ‘Electric Energy Savings’ calculation method.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-DRHR-V01-200101

###### Review Deadline: 1/1/2024

### Commercial LED Grow Lights

###### Description

LED lamp technology offers reduced energy and maintenance costs when compared with conventional light sources.  LED technology has a significantly longer useful life lasting 30,000 hours or more and significantly reduces maintenance costs.  The savings and costs for this measure are evaluated with the replacement of HID grow lights with LED fixtures.  LED lamps offer a more robust lighting source, longer lifetime, and greater electrical efficiency than conventional supplemental grow lights.

This measure is designed for other interior horticultural applications that use artificial light stimulation in an indoor conditioned space.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

LED fixtures must have a reduced wattage, be listed on the Design Lights Consortium (DLC) qualified products list, be UL Listed, have a power factor (PF) ≥0.90, a photosynthetic photon efficacy (PPE) of no less than 1.9 micromoles per joule, a minimum rated lifetime of 50,000 hours, and a minimum warranty of 5 years. If DLC PPE requirements for LED grow lighting exceeds the current requirements, the new PPE will become the efficient equipment standard.

###### Definition of Baseline Equipment

The baseline equipment is the industry established grow light based on the horticultural application, as detailed in the table below. HID fixtures are assumed for flowering and vegetative crops. T5 high-output fixtures are assumed for seedling and microgreen crops.

| Crop Type | Baseline Technology Type | Baseline PPE (μmol/J) | Baseline Watts per Square Foot | Baseline Fixture Wattage |  |
| --- | --- | --- | --- | --- | --- |
| Flowering Crops (Tomatoes and Peppers) | High Pressure Sodium | 1.7 | 68.8 | 1,100 W |
| Vegetative Growth | Metal Halide | 1.25 | 40 | 640 W |
| Microgreens | T5 HO Fixture | 0.84 | 22.4 | 358 W |
| Propagation | T5 HO Fixture | 0.84 | 14.6 | 234 W |
| Medical Cannabis – Flowering Stage | High Pressure Sodium | 1.7 | 68.8 | 1,100 W |
| Recreational Cannabis – Flowering Stage | HID/LED/Other | 2.2 | 36 | 576 W |

Cannabis cultivation facilities have a separate equipment definition due to Illinois legislation. See cannabis cultivation code from “Cannabis Regulation and Tax Act, Illinois HB 1438:

“The Lighting Power Densities (LPD) for cultivation space commits to not exceed an average of 36 watts per gross square foot of active and growing space canopy, or all installed lighting technology shall meet a photosynthetic photon efficacy (PPE) of no less than 2.2 micromoles per joule fixture and shall be featured on the Design Lights Consortium (DLC) Horticultural Specification Qualified Products List (QPL).”

###### Deemed Lifetime of Efficient Equipment

The expected measure life is 9.5 years (average rated life of 50,000 hours).

###### Deemed Measure Cost

LED Fixture Costs:

≤ 250 Watts = $ 325.87 per fixture

> 250 Watts = $ 535.04 per fixture

###### Loadshape

Loadshape C65 – Non-Residential Indoor Agriculture Vegetative Room

Loadshape C66 – Non-Residential Indoor Agriculture Flowering Room

###### Coincidence Factor

Summer coincidence factor for vegetative rooms = 0.95

Summer coincidence factor for flowering rooms = 0.76

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Grow Space Square Footage Method:

∆kWh=((W/sqftBASE-W/sqftEE)1000)×Area×Hours ×WHFe

Per Fixture Method:

∆kWh=((WattsBASE-WattsEE)1000)×Hours ×WHFe

Where:

W/sqftBASE	= Baseline wattage per square foot. If unknown, typical baseline watts per square feet by crop type can be found in the baseline equipment definition.

W/sqftBASE=WattsBASEFixture Area

WattsBASE 	= Baseline fixture wattage, see typical baseline wattages by crop type in baseline equipment definition.

W/sqftEE		= Efficient wattage per square foot

= Actual

W/sqftEE=WattsEEArea

WattsEE		= Efficient fixture wattage.

Fixture Area	= Square footage of grow canopy covered by one fixture.

= 16 sqft.

Area		= Illuminated area in square feet of active and growing space canopy

= Actual.

Hours	= Annual operating hours. See table below for typical hours of operation breakdown by crop type.

| Crop Types | Hours of Operation per Day | Annual Hours of Operation |
| --- | --- | --- |
| Flowering Crops (Tomatoes/Peppers) | 12 | 4,200 |
| Vegetative/Propagation Growth | 18 | 6,300 |
| Microgreens | 18 | 6,300 |
| Medical Cannabis – Flower Stage | 12 | 4,200 |
| Recreational Cannabis – Flowering Stage | 12 | 4,200 |

WHFe	= 1.21

1000			= Watts to kW conversion factor

Heating Penalty

If electrically heated building:

Grow Space Square Footage Method

∆kWhheat penalty=((W/sqftBASE-W/sqftEE)1000)×Area×Hours ×-IFkWh

Per Fixture Method:

∆kWhheat penalty=((WattsBASE-WattsEE)1000)×Hours ×-IFkWh

Where:

IFkWh	= 0 if gas heating, 0.284 if electric resistance heating, 0.124 if electric heat pump heating; lighting-HVAC Interactive Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting.

###### Summer Coincident Peak Demand Savings

Grow Space Square Footage Method:

∆kW=((W/sqftBASE-W/sqftEE)1000)×Area×CF ×WHFd

Per Fixture Method:

∆kW=((WattsBASE-WattsEE)1000)×CF ×WHFd

Where:

WHFd	= 1.22 if cooling or 1.00 if none; waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings.

CF		= 0.95 for vegetative crops or 0.76 for flowering crops

###### Natural Gas Savings

Heating Penalty if fossil fuel heated building (or if heating fuel is unknown):

Grow Space Square Footage Method:

∆Therms=((W/sqftBASE-W/sqftEE)1000)×Area×Hours×-IFTherms

Per Fixture Method:

∆Therms=((WattBASE-WattEE)1000)×Hours×-IFTherms

Where:

IFTherms	= 0.043 if gas heating, 0 if other heating; lighting-HVAC Interactive Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

Any costs associated with moving the LED lighting fixture to different heights throughout the different growing phases should also be included as an O&M consideration.

###### Measure Code: CI-AGE-GROW-V03-220101

###### Review Deadline: 1/1/2024

### Swine Heat Pads

###### Description

This measure applies to the large Commercial and Industrial sector, specifically for the agriculture industry.  Swine farmers will typically keep their newborn piglets alongside their mothers (sows) for up to three to four weeks until they gain sufficient weight and can be moved to a nursery barn. During this farrowing stage, the piglets must be kept at temperatures ranging from 32 to 35°C (90 to 95°F). A sow and her piglets are kept in private farrowing crates, where the sow is kept in a separate and railed cage. This allows the piglets to still suckle from their mother and keeps the sow from crushing her piglets. These farrowing crates can be arranged in single or double systems. Typically, farmers will utilize a heat lamp as the primary heating source for these piglets, which can range from 125 W to 250 W and have an average measure life of 5,000 hours. More energy efficient technology has emerged in the form of heated mats. These mats require significantly less energy than a traditional heat lamp and have no known negative impacts on piglet health. Heating mats come in two options, single (typically rated at ≤100W) or double (typically rated at ≤200W) mats. Single mats serve one litter, and double mats serve two litters.

###### Definition of Efficient Equipment

The use of heat mats in swine farrowing will result in electrical savings for the customer. Research has also shown that newborn piglets do not prefer mat heating over lamp heating, but as they grow, they tend to prefer mat heating. Applied research in large industrial settings found no significant differences between lamp and mat heating on the behavior and well-being of piglets. Therefore, the only difference to note between the two methods is the energy saved in using heating mats.

###### Definition of Baseline Equipment

The baseline measure for swine farrowing heating is heat lamps, typically ranging from 125 to 250 Watts. Most studies conducted on swine farrowing heat lamps have used 125 watt or 175 watt lamps per litter.,

###### Deemed Lifetime of Efficient Equipment

The measure life of a farrowing heat mat is 5 years.

###### Deemed Measure Cost

Heat mat prices will vary somewhat with size but a typical single mat costs $125 and double mat costs $250. Additional costs can be incurred if a thermostat controller is included, these vary widely depending on controller complexity.

###### Loadshape

Loadshape C04 - Non-Residential Electric Heating

###### Coincidence Factor

The coincidence factor is assumed to be 0.018.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

kWhsaved=kWhbase-kWhEE

kWhbase=Cratestotal ×Hours ×Fixturecrate ×Lampfixture ×Wattagelamp1000 WattskW

kWhEE=Hours ×Matssingle×Wattagesingle+Matsdouble×Wattagedouble1000 WattskW

Where:

Cratestotal= Cratessingle-row+Cratesdouble-row ×Rows×Rooms

MatsSingle=Cratessingle-row×Rows ×Rooms

MatsDouble=Cratesdouble-row×Rows ×Rooms

Cratestotal	= Number of Farrowing Crates

Cratessingle-row	= Number of single crates in a row

Cratesdouble-row	= Number of double crates in a row

Rows		= Number of rows in a room

Rooms		= Number of rooms in a farrowing barn

Matssingle		= Number of single mats

Matsdouble	= Number of double mats

Wattagesingle	= Default 100W; Wattage of a single heat mat

Wattagedouble	= Default 200W; Wattage of a double heat mat

Hours		= Default 5,105 hours; Annual hours of operation

Fixturecrate	= Number of heat lamp fixtures per farrowing crate

Lampfixture	= Number of heat lamps per fixture

Wattagelamp	= Default 125W or 175W; Heat lamp wattage

###### Default Savings for Single Unit Replacement

| Replacement Type | Baseline Heat Lamp | Annual kWh Savings |
| --- | --- | --- |
| Single Mat replacing one Heat Lamp | 125W | 127.6 |
| Double Mat replacing two Heat Lamps |  | 255.3 |
| Single Mat replacing one Heat Lamp | 175W | 382.9 |
| Double Mat replacing two Heat Lamps |  | 765.8 |

###### Summer Coincident Peak Demand Savings

kWSaved=(kWhSavedHours)×CF

Where:

kWhSaved		= kWh savings, see above equation and table.

Hours		= Operating hours, 5,105.

CF		= Coincidence Factor, 0.018.

###### Default Savings for Single Unit Replacement

| Replacement Type | Baseline Heat Lamp | Peak kW Savings |
| --- | --- | --- |
| Single Mat replacing one Heat Lamp | 125W | 0.0005 |
| Double Mat replacing two Heat Lamps |  | 0.0009 |
| Single Mat replacing one Heat Lamp | 175W | 0.0014 |
| Double Mat replacing two Heat Lamps |  | 0.0027 |

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

Approximately 1% of mats are likely to be damaged by swine each year and require full replacement.

Additionally, depending on the flooring, some mats may become loose on steel slated floors. This can be prevented by buying mats that have a channel or groove where it sits in the partition. Another option is to buy tie down clips that cost approximately $24 per double mat.

The NPV for replacement heat lamps and annual levelized replacement costs using the societal real discount rate of 0.42% are presented below. The O&M cost adjustments are based on a 1-year measure life for heat lamps and a 5-year analysis period for heat pads. The measure life assumptions indicate an annual lamp replacement cost for the baseline equipment. The heat lamp replacement cost is assumed to be $5.50.

| Replacement Type | NPV of replacement costs for period | Levelized annual replacement cost savings |
| --- | --- | --- |
| Single Mat replacing one Heat Lamp | $21.78 | $4.41 |
| Double Mat replacing two Heat Lamps | $43.56 | $8.82 |

###### Measure Code: CI-AGE-HPAD-V01-210101

###### Review Deadline: 1/1/2024

### Irrigation Pump VFD

###### Description

This measure applies to variable speed drives (VSD) installed on irrigation pump motors for the agriculture industry. This characterization does not apply to positive displacement pumps. The VFD will modulate the speed of the motor when it does not need to run at full load. Since the power of the motor is proportional to the cube of the speed for these types of applications, significant energy savings will result.

This measure was developed to be applicable to the following program types: TOS, RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The VFD is applied to a motor that does not yet have one. The irrigation system must have a variable load, and installation is to include the necessary controls as determined by a qualified engineer. Savings are based on application of VFDs to a range of baseline load conditions.

###### Definition of Baseline Equipment

The time of sale baseline is a new motor installed without a VFD or other methods of control. The retrofit baseline is an existing motor operating as is. Retrofit baselines may or may not include guide vanes, throttling valves, or other methods of control. This information shall be collected from the customer.

Installations of new equipment with VFDs that are required by IECC 2018 as adopted by the State of Illinois are not eligible to claim savings.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is 15 years.

###### Deemed Measure Cost

Customer provided costs will be used when available. Default measure costs are noted below for up to 75 hp motors. Custom costs must be gathered from the customer for motor sizes not listed below.

| HP | Cost |
| --- | --- |
| 1-9 HP | $1,874 |
| 10-19 HP | $2,967 |
| 20-29 HP | $4,060 |
| 30-39 HP | $5,154 |
| 40-49 HP | $6,247 |
| 50-59 HP | $7,340 |
| 60-69 HP | $8,433 |
| 70-75 HP | $9,526 |

###### Loadshape

Loadshape C59 – Agriculture and Water Pumping

###### Coincidence Factor

The installation of a VFD on an irrigation pump should not cause any energy reduction during peak runtimes.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

###### ∆kWh=kWhBase-kWhVFD

kWhBase=1ηHPη*0.746kWHP*Hoursyear*%Hoursη

kWhVFD=1ηHPVFD,η*0.746kWHP*Hoursyear*%Hoursη

HPη=Flowη*Headη3960×Effpump*Effmotor

HPVFD,η=Flowη×HeadVFD,η3960×Effpump*EffVFD*Effmotor

Hoursyear=Acres×Irrigation12inft*60minhr*GPMSystem7.481galft3*43,560ft2acre

Where:

kWhBase		= Annual energy required for the baseline pump condition

kWhVFD		= Annual energy required with a VFD pump installed

HP𝜂		= Baseline horsepower required for a given flow rate

HPVFD,𝜂		= Horsepower required for a given flow rate with the VFD installed

Hoursyear		= Annual Hours of irrigation

%Hours𝜂		= Percent of time irrigation pump will be operating at a given flow rate

𝜂		= Number of data points needed or collected

Flow𝜂		= Flow rate at a given data point in gallons per minute, use actual values

Head𝜂		= Pressure head at a given data point in feet, use actual values

HeadVFD,𝜂	= Pressure head at a given data point in feet with a VFD

Effpump		= Percent efficiency of the pump, taken from manufacturers pump curve

Effmotor		= Percent efficiency of the pump motor

NEMA Premium Efficiency Motors Default Efficiencies

| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | # of Poles |  |  | # of Poles |  |  |
|  | 6 | 4 | 2 | 6 | 4 | 2 |
|  | Speed (RPM) |  |  | Speed (RPM) |  |  |
|  | 1200 | 1800 Default | 3600 | 1200 | 1800 | 3600 |
| 1 | 0.825 | 0.855 | 0.770 | 0.825 | 0.855 | 0.770 |
| 1.5 | 0.865 | 0.865 | 0.840 | 0.875 | 0.865 | 0.840 |
| 2 | 0.875 | 0.865 | 0.855 | 0.885 | 0.865 | 0.855 |
| 3 | 0.885 | 0.895 | 0.855 | 0.895 | 0.895 | 0.865 |
| 5 | 0.895 | 0.895 | 0.865 | 0.895 | 0.895 | 0.885 |
| 7.5 | 0.902 | 0.910 | 0.885 | 0.910 | 0.917 | 0.895 |
| 10 | 0.917 | 0.917 | 0.895 | 0.910 | 0.917 | 0.902 |
| 15 | 0.917 | 0.930 | 0.902 | 0.917 | 0.924 | 0.910 |
| 20 | 0.924 | 0.930 | 0.910 | 0.917 | 0.930 | 0.910 |
| 25 | 0.930 | 0.936 | 0.917 | 0.930 | 0.936 | 0.917 |
| 30 | 0.936 | 0.941 | 0.917 | 0.930 | 0.936 | 0.917 |
| 40 | 0.941 | 0.941 | 0.924 | 0.941 | 0.941 | 0.924 |
| 50 | 0.941 | 0.945 | 0.930 | 0.941 | 0.945 | 0.930 |
| 60 | 0.945 | 0.950 | 0.936 | 0.945 | 0.950 | 0.936 |
| 75 | 0.945 | 0.950 | 0.936 | 0.945 | 0.954 | 0.936 |
| 100 | 0.950 | 0.954 | 0.936 | 0.950 | 0.954 | 0.941 |
| 125 | 0.950 | 0.954 | 0.941 | 0.950 | 0.954 | 0.950 |
| 150 | 0.954 | 0.958 | 0.941 | 0.958 | 0.958 | 0.950 |
| 200 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.954 |
| 250 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.958 |
| 300 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 350 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 400 | 0.958 | 0.958 | 0.958 | 0.958 | 0.962 | 0.958 |
| 450 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |
| 500 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |

EffVFD		= Percent efficiency of the VFD

= 97%

Acres		= Size of the field that is being irrigated in acres

Irrigation	= Gross irrigation required in inches per year

GPMSystem	= Required system flow rate in gallons per minute

###### Summer Coincident Peak Demand Savings

There are no expected peak demand impacts for this measure.

###### Natural Gas Savings

There are no expected fossil fuel impacts for this measure.

###### Water and Other Non-Energy Impact Descriptions and Calculation

While there may be water savings from the installation of a VFD on an irrigation pump, they are not being included at this time. Any water savings calculations should be handled in a custom manner.

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-PUMP-V01-220101

###### Review Deadline: 1/1/2025

### High Efficiency Grain Dryer

###### Description

This measure characterizes the energy savings from the replacement of an existing inefficient grain dryer with a new efficient grain dryer (Early Replacement incentive program).  Alternatively, this measure is for the purchase of a new high efficiency grain dryer instead of a new standard efficiency grain dryer for an existing facility (Time of Sale program) or a new facility (New Construction incentive program).  Energy savings are achieved by drying grain more efficiently through: improved dryer air flow design, improved dryer controls, warm air heat recovery, and burner efficiency improvements.  Efficient dryers also have the benefits of increased throughput capacity and reduced annual hours of operation.

This measure was developed to be applicable to the following program types: TOS, EREP, and NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

###### The efficient equipment is assumed to be a new, high efficiency grain dryer. Bushels per hour must be provided by the manufacturer, as rated at 5% moisture removal rate per bushel processed.

###### Definition of Baseline Equipment

The baseline for this measure is a standard efficiency grain dryer currently on the market.  Bushels per hour must be provided by the manufacturer, as rated at 5% moisture removal rate per bushel processed.

###### Deemed Lifetime of Efficient Equipment

The measure life for the energy-efficient grain dryer is deemed to be 20 years.

###### Deemed Measure Cost

If known, the actual material and labor cost of installation should be used. If unknown, the cost of the measure is assumed to be the values summarized in the table below:

| Tier (bushels per hour) |  | Tier (annual bushels) | High-Efficiency Dryer Total Installation Cost (for Early Replacement only) |  | Average Incremental Cost of of High-Efficiency Dryer vs Standard Dryer |  | Average Incremental Cost of Variable Speed Drive added to Cost of High-Efficiency Dryer |
| --- | --- | --- | --- | --- | --- | --- | --- |
| <500 | < 170,000 | $83,000 (Based on baseline price of $50,000 + ($50/Bu/hr * 250 Rated Bu/hr) + Incremental Cost of High Efficiency) |  | $20,000 |  |  | $4,000 (Based on baseline price of $2,500 + 0.046kW/Bu/hr * 250 Rated Bu/hr) *$100/kW) |  |
| ≥ 500 and < 1000 | ≥ 170,000 and < 330,000 | $118,000 (Based on 750 Rated Bu/hr) |  | $30,000 |  |  | $6,000 (Based on 750 Rated Bu/hr) |  |
| ≥ 1000 and < 2000 | ≥ 330,000 and < 670,000 | $165,000 (Based on 1,500 Rated Bu/hr) |  | $40,000 |  |  | $9,000 (Based on 1,500 Rated Bu/hr) |  |
| ≥ 2000 and < 3500 | ≥ 670,000 and < 1,200,000 | $258,000 (Based on 2,750 Rated Bu/hr) |  | $70,000 |  |  | $15,000 (Based on 2,750 Rated Bu/hr) |  |
| ≥ 3500 and ≤ 5000 | ≥ 1,200,000 and ≤ 1,700,000 | $363,000 (Based on 4,250 Rated Bu/hr) |  | $100,000 |  |  | $22,000 (Based on 4,250 Rated Bu/hr) |  |
| > 5000 | > 1,700,000 | $488,000 (Based on 6,250 Rated Bu/hr) |  | $125,000 |  |  | $31,000 (Based on 6,250 Rated Bu/hr) |  |

Early Replacement: The full installation cost is provided in the table above. The assumed deferred cost (after 6.5 years [one third of useful life]) of replacing existing equipment with a new baseline unit is assumed to be the installation cost discounted to present value using the nominal discount rate.

###### Loadshape

Loadshape NRE11 – Non-Residential Agriculture

###### Coincidence Factor

There are no summer peak savings associated with this measure as it is assumed grain dryers do no operate during peak summer months.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

If grain dryer is heated exclusively with electricity:

∆kWh  =  Bushels/HrCapacity * Annual_Hr_Use@Rated_Capacity * (Moisture_%In - Moisture_%Out) *  Grain_Lb_Moisture_/_Bushel * Btu/LbEvap * (1 / Dryer_EffcyStd -1/ Dryer_EffcyEff) / 3,412  + (Dryer_Fan_PowerStandard - Dryer_Fan_PowerEfficient) * Bushels/HrCapacity  * Annual_Hr_Use@Rated_Capacity

Where:

Bushels/HrCapacity 	= Capacity of Grain Dryer in Bushels/Hr when reducing grain moisture 
content by 5%

Annual_Hr_Use@Rated_Capacity	= Average annual hours of use of typical grain dryer

= Deemed value of 336.3 hr/year

Annual hours of use were calculated based on following table.  Deemed value is arithmetic average of Average Use per Year

| Savings Tier (Bushels/hr) from manufacturer | Savings Tier (Bushels/yr) | Average Hours/yr @ Rated Capacity |
| --- | --- | --- |
| >= 0 Bu/Hr | 170,000 | 340 |
| >= 500 Bu/Hr | 330,000 | 330 |
| >= 1,000 Bu/Hr | 670,000 | 335 |
| >= 2,000 Bu/Hr | 1,200,000 | 343 |
| >= 3,500 Bu/Hr | 1,700,000 | 340 |
| >= 5,000 Bu/Hr | 2,475,000 | 330 |

Moisture_%In	= 23%, a deemed value representing average % moisture in grain arriving at grain dryer facility

Moisture_%Out	= 15%, a deemed value representing average % moisture in grain after being dried at grain dryer facility

Grain_Lb_Moisture_/_Bushel    = Lookup value from following table, Lb Moisture per Bushel per 1% of moisture content reduction.

| Grain Type | Weight of "Standard Bushel" | Lb Moisture/Bu/1% Evap |
| --- | --- | --- |
| Alfalfa | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |
| Barley | 48.0 Lb/Std Bu | 0.48 Lb Evap/Std Bu/Delta% |
| Clover | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |
| Corn, Shelled (15.5%) | 56.0 Lb/Std Bu | 0.56 Lb Evap/Std Bu/Delta% |
| Corn, Ear (15.5%) | 68.4 Lb/Std Bu | 0.68 Lb Evap/Std Bu/Delta% |
| Cotton | 32.0 Lb/Std Bu | 0.32 Lb Evap/Std Bu/Delta% |
| Cowpeas | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |
| Flax | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |
| Grass, Exc Timothy | 14.0 Lb/Std Bu | 0.14 Lb Evap/Std Bu/Delta% |
| Grass, Timothy | 45.0 Lb/Std Bu | 0.45 Lb Evap/Std Bu/Delta% |
| Lespedeza | 45.0 Lb/Std Bu | 0.45 Lb Evap/Std Bu/Delta% |
| Millet | 80.0 Lb/Std Bu | 0.80 Lb Evap/Std Bu/Delta% |
| Oats | 32.0 Lb/Std Bu | 0.32 Lb Evap/Std Bu/Delta% |
| Rape | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |
| Tye | 56.0 Lb/Std Bu | 0.56 Lb Evap/Std Bu/Delta% |
| Sorghum, Forage | 50.0 Lb/Std Bu | 0.50 Lb Evap/Std Bu/Delta% |
| Sorghum, grain (13.0%) | 56.0 Lb/Std Bu | 0.56 Lb Evap/Std Bu/Delta% |
| Soybeans | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |
| Sudan grass | 28.0 Lb/Std Bu | 0.28 Lb Evap/Std Bu/Delta% |
| Sunflower, oil type | 28.0 Lb/Std Bu | 0.28 Lb Evap/Std Bu/Delta% |
| Trefoil, Birdsfoot | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |
| Vetch | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |
| Wheat (13.5%) | 60.0 Lb/Std Bu | 0.60 Lb Evap/Std Bu/Delta% |

Btu/LbEvap	= 990 Btu per Lb of Water Evaporated; an engineering constant

Dryer_EffcyStd 	= Electric grain dryer efficiency of a standard-efficiency electric bin dryer, expressed as a %, defined as Btu of moisture evaporated in the dryer divided by the heating Btu input into the dryer

=71%, a deemed value, based on the following table, which represents BTU/Lb evaporated and equivalent Overall Efficiency for the dryers and heating sources used in this TRM:

| Grain Dryer Description | Dryer Efficiency (Dryer_Effcy) |  | Dryer Fan Power (Dryer_Fan_Power) |
| --- | --- | --- | --- |
|  | Dryer_Effcy | Btu/lb Water Evaporated (Btu/lb Water) | kW / Bushel |
| Baseline Gas Grain Dryer w/ Constant Speed Fan Operation | 44% | 2,241 | 0.044 |
| Efficient Gas Grain Dryer w/ Constant Speed Fan Operation | 61% | 1,625 | 0.044 |
| Efficient Gas Grain Dryer w/ Damper Fan Operation | 61% | 1,625 | 0.035 |
| Efficient Gas Grain Dryer w/ Fan VFD | 61% | 1,625 | 0.002 |
| Baseline Electric Bin Grain Dryer w/ Constant Speed Fan Operation | 71% | 1,400 | 0.44 |
| Efficient Electric Bin Grain Dryer w/ Constant Speed Fan Operation | 88% | 1,120 | 0.044 |
| Efficient Electric Bin Grain Dryer w/ Damper Fan Operation | 88% | 1,120 | 0.035 |
| Efficient Electric Bin Grain Dryer w/ Fan VFD | 88% | 1,120 | 0.002 |

Dryer_EffcyEff  	= 88%, a deemed value; or Actual.  See prior footnote for derivation of this value.

3,412	= Conversion factor of kWh to Btu; engineering constant.

Dryer_Fan_PowerStandard	= 0.044 kW/Bu, from above table, a deemed value, based on the following average standard bin dryer operational parameters, and the engineering equation:

kW/BuStd 	= CFM/BuStd *  in._wcStd  /  6,354 / Fan_EffieciencyStd  * 0.746  /  Motor_EffcyStd.

In the above equation, the following deemed constants are typical for standard-efficiency Grain Dryers:

Where:
CFM/BuStd 		= 61 CFM/Bu

in._wcStd	 	= 3.0” wc

6,354	 	=Units conversion from cfm * in. wc. / Fan_Efficiency to BHP

Fan_EffieciencyStd 	= 60%

0.746 		= Units conversion from BHP to kW

Motor_EffcyStd 	= 80%.

kW/Bu = 61 * 3.0 / 6,354 / 60% * 0.746 / 80%
              = 0.044 kW/Bu

Dryer_Fan_PowerEfficient	= 0.035 kW/Bu, if fan volume is controlled using outlet damper, or

= 0.002 kW/Bu, if fan volume is controlled using VFD.

Above values are deemed constants, based on the following average high-efficiency bin dryer operational parameters, and the engineering equation:

kW/BuEff = CFM/BuEff *  in._wcEff  /  6,354 / Fan_EffieciencyEff  * 0.746  /  Motor_EffcyEff  /  Drive_EffcyEff

In the above equation, the following deemed constants are assumed to apply to high-efficiency Grain Dryers:

Where:
CFM/BuEff 		= 22

in._wcEff 		= 4.4” if Outlet Damper control; 0.4” if VFD control

6,354		=Units conversion from cfm * in. wc. / Fan_Efficiency to BHP

Fan_EffieciencyEff 	= 60%

0.746 		= Units conversion from BHP to kW

Motor_EffcyEff 	= 80%

Drive_EffcyEff 	= 100% if Outlet Damper control; 95% if VFD control.

For high-efficiency dryer with VFD control:

kW/Bu 	= 22  *  0.4  /  6,354 /  60% *  0.746  /  80%  /  95%
            	= 0.002 kW/Bu

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

If grain dryer is heated exclusively with natural gas:

∆Therms = Bushels/HrCapacity * Annual_Hr_Use@Rated_Capacity * (Moisture_%In - Moisture_%Out) *  Grain_Lb_Moisture_/_Bushel * Btu/LbEvap * (1 / Dryer_EffcyStd -1/ Dryer_EffcyEff) / 100,000

Where:

100,000	= Conversion factor of Therms to Btu; engineering constant.

All variables are as defined and derived in the preceding electric savings calculations, but using values in the dryer efficiency table above for Baseline or Efficient "Gas or Propane Grain Dryer".

Note: When a variable frequency drive (VFD) is incorporated on the drying fan, electrical savings may be claimed by the fan power derivation in the electric savings algorithm for additive electrical savings for a gas heated grain dryer.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-GDRY-V01-220101

###### Review Deadline: 1/1/2025

### Grain Dryer Tune-Up

###### Description

This measure is for commercial grain dryers for agricultural operations. Tune-ups improve grain drying efficiency by maintaining dryer components that have become clogged, dirty, or uncalibrated. This measure involves cleaning and/or inspecting burners, fans, and screens and cleaning and recalibrating all temperature and moisture sensors, if applicable.

Crops such as grain, soybeans, and corn need to be dried after harvest to prevent rot, mold, and animals from destroying the crop. After harvest, these wet crops are loaded into a grain dryer where they are dried. Grain drying processes vary but consist of warm (or high temperature) air forced through the crop. The air may be heated electrically or by fossil fuels. Once the grain is dried, it is stored in grain bins or silos until transport. At the time of harvest, moisture content inside grain varies between 17% and 40%. After drying, moisture levels are kept between 13% and 14% to improve shelf life. Maintaining peak efficiency of grain dryers through tune-ups is important for equipment efficiency and grain drying performance. Tune-ups save energy by removing impediments to airflow and calibrating sensors so that equipment capacity is maximized and drying time is minimized.

###### Definition of Efficient Equipment

To qualify for this measure, the facility must, as applicable, complete the tune-up requirements by an approved technican as specified below:

- Inspect and clean screens

- Inspect and clean fans

- Clean and calibrate all temperature sensors

- Clean and calibrate all moisture sensors*

- Inspect and adjust grain dryer controls including temperature setpoint, as needed

- Lubricate bearings

Task marks with an asterisk (*) are only required if the existing grain dryer contains this equipment.

###### Definition of Baseline Equipment

The baseline condition of this measure is a commercial-grade grain dryer that has not been tuned-up within the past 12 months.

###### Deemed Lifetime of Efficient Equipment

The life of this measure is 1 year.

###### Deemed Measure Cost

The cost of this measure is $500.00, which includes service and labor.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

∆kWh=BushelsANNUAL*kWh Saved per BushelGDEFF*LbsH2O REMOVED*kWh%3,412*SF

Where:

BushelsANNUAL	= Number of bushels of grain to be dried per year (bushels/yr)

= Custom

Where:

kWh Saved per Bushel=GDEFF*LbsH2O REMOVED*kWh%3,412*SF

Where:

kWh Saved per Bushel	= Amount of energy saved per bushel of grain dried. Use actual if known. If unknown, default to calculated values in table below based on grain dryer type and efficiency.

GDEFF		= Existing grain dryer efficiency (Btu/Lbs_H20)

= Custom, or default value in table below based on type of grain dryer

| Grain Dryer Type | GD_EFF (Btu/Lbs_H2O) | kWh% | kWh Saved per Bushel | Therm Saved per Bushel |
| --- | --- | --- | --- | --- |
| Low Temperature Bin Dryer | 1,600 | 100% | 0.11723 | 0 |
| Continuous Mixed Flow Bin Dryer | 2,000 | 2% | 0.00293 | 0.00490 |
| Mixed Flow Dryer | 2,000 | 2% | 0.00293 | 0.00490 |
| High Temperature Batch Bin Dryer | 2,400 | 2% | 0.00352 | 0.00588 |
| Continuous Cross-Flow (Tower) Dryer | 2,400 | 2% | 0.00352 | 0.00588 |
| Cross-Flow Batch Dryer | 2,500 | 2% | 0.00366 | 000613 |

LbsH2O REMOVED=GrainLBS MOISTURE*% MoistureIN- % MoistureOUT

Where:

LbsH2O REMOVED	= Pounds of water removed per bushel

= Default value in table or Custom calculation as detailed below

| Crop Type | Moisture Removal Assumption | LBS_H2O Removed per Bushelsannual |
| --- | --- | --- |
| Corn | 7% reduction (from 22% initial moisture content (MC) to 15% final MC) | 5.00 |
| Soybean | 7% reduction (from 20% initial MC to 13% final MC) | 5.04 |

GrainLBS MOISTURE 	= Lbs of moisture per bushel per 1% of moisture content reduction. Value is specific to    grain type and is based on the following table:

| Grain Type | Lb Moisture/Bushel/1% Evaporation |
| --- | --- |
| Alfalfa | 0.60 Lb Evap/Std Bu/Delta% |
| Barley | 0.48 Lb Evap/Std Bu/Delta% |
| Clover | 0.60 Lb Evap/Std Bu/Delta% |
| Corn, Shelled (15.5%) | 0.56 Lb Evap/Std Bu/Delta% |
| Corn, Ear (15.5%) | 0.68 Lb Evap/Std Bu/Delta% |
| Cotton | 0.32 Lb Evap/Std Bu/Delta% |
| Cowpeas | 0.60 Lb Evap/Std Bu/Delta% |
| Flax | 0.60 Lb Evap/Std Bu/Delta% |
| Grass, Exc Timothy | 0.14 Lb Evap/Std Bu/Delta% |
| Grass, Timothy | 0.45 Lb Evap/Std Bu/Delta% |
| Lespedeza | 0.45 Lb Evap/Std Bu/Delta% |
| Millet | 0.80 Lb Evap/Std Bu/Delta% |
| Oats | 0.32 Lb Evap/Std Bu/Delta% |
| Rape | 0.60 Lb Evap/Std Bu/Delta% |
| Tye | 0.56 Lb Evap/Std Bu/Delta% |
| Sorghum, Forage | 0.50 Lb Evap/Std Bu/Delta% |
| Sorghum, grain (13.0%) | 0.56 Lb Evap/Std Bu/Delta% |
| Soybeans | 0.60 Lb Evap/Std Bu/Delta% |
| Sudan grass | 0.28 Lb Evap/Std Bu/Delta% |
| Sunflower, oil type | 0.28 Lb Evap/Std Bu/Delta% |
| Trefoil, Birdsfoot | 0.60 Lb Evap/Std Bu/Delta% |
| Vetch | 0.60 Lb Evap/Std Bu/Delta% |
| Wheat (13.5%) | 0.60 Lb Evap/Std Bu/Delta% |

% MoistureIN 	= Average % moisture of grain as it arrives at the grain dryer

= Actual

% MoistureOUT = Average % moisture of grain as it exits the grain dryer after being dried

= Actual

kWh%		= Percentage of overall dryer energy consumption that is electricity

= Default value in table above based on type of grain dryer

3,412		= Conversion from Btu to kWh

SF		= Savings factor

= 5%

LbsH2O REMOVED=GrainLBS MOISTURE*% MoistureIN- % MoistureOUT

LbsH2O REMOVED

GrainLBS MOISTURE

% MoistureIN

% MoistureOUT

For example, for a Low Temperature Bin Dryer that produces 100,000 bushels of corn per year.

∆kWhTherms=100,000Buyr× 1,6002,000Btulb H2O× 5.00lbsH20bu× 98100 % ThermkWh 3,412100,000BtuTherm× 5%

∆kWhTherms=11,723490

For example, for a Mixed Flow Dryer that produces 100,000 bushels of corn per year.

∆Therms=100,000Buyr× 2,000Btulb H2O× 5.00lbsH20bu× 98 % Therm 100,000BtuTherm× 5%

∆Therms=490

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

∆Therms=BushelsANNUAL*Therms Saved per BushelGDEFF* LbsH2O REMOVED* Therms%100,000*SF

Therms Saved per Bushel=GDEFF* LbsH2O REMOVED* Therms%100,000*SF

Where:

Therms Saved per BushelTherms Saved per Bushel	= Amount of energy saved per bushel of grain dried. Use actual if known. If unknown, default to calculated values in table above based on grain dryer type and efficiency.

Where:

BushelsANNUAL	= Number of bushels of grain to be dried per year (bushels/yr)

= Custom

GDEFF		= Existing grain dryer efficiency (Btu/Lbs_H20)

= Custom, or default value in table below based on type of grain dryer

Where:

kWh%		= Percentage of overall dryer energy consumption that is electricity

= Default value in table above based on type of grain dryer

3,412		= Conversion from Btu to kWh

SF		= Savings factor

= 5%

Therms%	= Percentage of overall dryer energy consumption that is natural gas

= (1 – kWh%)

100,000		= Conversion factor

LbsH20 REMOVED	= GrainLBS MOISTURE * (%MoistureIN - %MoistureOUT)

Wheree:

All other variables as above

= Default value in table or Custom calculation as detailed below

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

###### N/A

###### Measure Code: CI-AGE-DTUNE-V01-220101

###### Review Deadline: 1/1/2025

### Greenhouse Boiler Tune-Up

###### Description

This measure is for a non-residential greenhouse boiler. For space heating other than greenhouses, see measure 4.4.2 Space Heating Boiler Tune-Up. For process heating other than greenhouses, see measure 4.4.3 Process Boiler Tune-Up. The tune-up will improve boiler efficiency by cleaning and/or inspecting burners, combustion chamber, and burner nozzles. Adjust air flow and reduce excessive stack temperatures, adjust burner and gas input. Check venting, safety controls, and adequacy of combustion air intake. Combustion efficiency should be measured before and after tune-up using an electronic flue gas analyzer.

###### Definition of Efficient Equipment

To qualify for this measure the facility must, as applicable, complete the tune-up requirements by approved technician as specified below:

•	Measure combustion efficiency using an electronic flue gas analyzer

•	Adjust airflow and reduce excessive stack temperatures

•	Adjust burner and gas input, manual or motorized draft control

•	Check for proper venting

•	Complete visual inspection of system piping and insulation

•	Check safety controls

•	Check adequacy of combustion air intake

•	Clean fireside surfaces

•	Inspect all refractory. Patch and wash coat as required.*

•	Inspect gaskets on front and rear doors and replace as necessary.*

•	Seal and close front and rear doors properly.*

•	Clean low and auxiliary low water cut-off controls, then re-install using new gaskets.*

•	Clean plugs in control piping.*

•	Remove all hand hole and man hole plates. Flush boiler with water to remove loose scale and sediment.*

•	Replace all hand hole and man hole plates with new gaskets.*

•	Open feedwater tank manway, inspect and clean as required. Replace manway plate with new gasket.*

•	Clean burner and burner pilot.

•	Check pilot electrode and adjust or replace.

•	Clean air damper and blower assembly.

•	Clean motor starter contacts and check operation.*

•	Make necessary adjustments to burner for proper combustion.

•	Perform all flame safeguard and safety trip checks.

•	Check all hand hole plates and man hole plates for leaks at normal operating temperatures and pressures.

•	Troubleshoot any boiler system problems as requested by on-site personnel

Note: Tune-up activities marked with an asterisk (*) are eligible to be performed by internal maintenance staff at periods of boiler shutdown.

###### Definition of Baseline Equipment

The baseline condition of this measure is a boiler that has not had a tune-up within the past 36 months.

###### Deemed Lifetime of Efficient Equipment

The life of this measure is 3 years.

###### Deemed Measure Cost

The cost of this measure is $0.83/MBtu/hr per tune-up.

###### DEEMED O&M COST ADJUSTMENTS

N/A

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

ΔTherms	= ((Capacity * 8766 * UF) / 100) * (1 - (Effpre / Effmeasured))

Where:

Capacity	= Boiler gas input size (kBtu/hr)

= Custom

UF 	= Utilization Factor

= Default Utilization Factor for heating in a greenhouse for agricultural end use are listed in the table below, or use a custom value based on modeling.,

| Building Type | Heating UF Existing Buildings |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Greenhouses with curtains | 0.473 | 0.445 | 0.383 | 0.328 | 0.321 | Virtual Grower 3.1, with ASHRAE HDD |
| Greenhouses without curtains | 0.476 | 0.447 | 0.385 | 0.330 | 0.323 | Virtual Grower 3.1, with ASHRAE HDD |

Effpre 	= Boiler Combustion Efficiency Before Tune-Up

= Actual. Default value is 80.3%

Note: Contractors should select a firing rate that appropriately represents the average operating condition and take readings at a consistent firing rate for pre and post tune-up.

Effmeasured	= Boiler Combustion Efficiency after Tune-Up

= Actual. Default value is 82.6%

100	= Converstion from kBtu to therms

8766	= Hours per year

For example, a greenhouse 80.3% efficient, 1050 kBtu boiler is tuned-up resulting in final efficiency of 82.6%:

Δtherms		=((1050 * 8766 * 0.419) / 100) * (1 - (0.803 / 0.826))

= 1074 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-GTUNE-V01-220101

###### Review Deadline: 1/1/2025

### Greenhouse Thermal Curtains

###### Description

Existing greenhouse construction with polyethlene (PE) roofs allows for significant heat loss overnight. The existing PE roofs cause radiant heat to enter the space during daytime, but also lead to heat loss to outside the structure during the night. This can be addressed using thermal curtains which decrease conduction, convection, and radiation heat losses in greenhouses. Thermal curtains are installed inside the greenhouse and are designed to be placed horizontally above the growing zone within a greenhouse. In addition to retaining heat, thermal curtains are commonly used for shading. Thermal insulating curtains are sheets of fabric that extend above the plant growing zone and span the length of the greenhouse. These curtain barriers can reduce nighttime heat loss by more than 20%. Operation of thermal curtains can be manual or motorized, but must be installed to ensure a tight seal at all connection points.

This measure case is defined as the installation of a single-layer heat curtain with infrared film in a greenhouse area in which a heat curtain was not present. It is assumed that the thermal curtains are deployed during nighttime hours, and open during daytime hours. This measure was developed to be applicable to the following program types: NC, RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

This measure case is defined as the installation of a single-layer heat curtain with infrared film in a greenhouse area in which a heat curtain was not present. It is assumed that the thermal curtains are deployed during nighttime hours, and open during daytime hours. They can either be manual or motorized thermal curtains installed in greenhouse constructed of PE glazing.

###### Definition of Baseline Equipment

The baseline equipment is a greenhouse constructed of PE glazing and no thermal curtain.

###### Deemed Lifetime of Efficient Equipment

The measure lifetime for greenhouse thermal curtains is 5 years.

###### Deemed Measure Cost

Measure cost for greenhouse thermal curtains is $1.50 per square foot.

###### Loadshape

NA

###### Coincidence Factor

NA

Algorithm

###### Calculation of Energy Savings

Energy savings are estimated using EnergyPlus version 9.4 whole-building energy simulation. The greenhouse geometry used in the EnergyPlus model consists of 4 connected bays, each bay with a gable type roof construction, measuring 36 feet wide by 100 feet long. The total conditioned floor area of the modeled greenhouse is 14,210 square feet, and savings are normalized per square foot floor area. The greenhouse is conditioned by gas-fired unit heaters and no cooling system. Greenhouse thermal curtain U values vary depending on the material type like spunbonded polyster, double-knit cloth, aluminized vinyl, aluminum strips, etc. They can have U values as low as 0.26 up to as high as 0.77. However, an average case of 0.483 U value has been simulated here which is assumed to represent a majority of thermal curtains. The area of the thermal curtain equals the conditioned floor area of the greenhouse.

Baseline and efficient models were developed for each Illinois climate zone using inputs for key greenhouse construction characteristics and sources as listed in the following table:

| Input Parameter | Baseline Value | Efficient Value |
| --- | --- | --- |
| Roof Glazing | Double PE film, U-value 0.7 (Btu/h · ft2 · °F) | Same as baseline. |
| Thermal Curtain | None. | Sunset - Sunrise, U-value 0.483 (Btu/h · ft2 · °F) |
| Wall Glazing | Single PE film, U-value 1.1 (Btu/h · ft2 · °F) | Same as baseline. |
| Infiltration | 1.5 Air Change per Hour (ACH) | Same as baseline. |
| Ventilation | 10 cubic feet per minute (CFM) per area (ft2) | Same as baseline. |
| Heating System | Gas-fired unit heater, 0.8 efficiency | Same as baseline. |
| Thermostat Setpoint | Heating setpoint 70°F | Same as baseline. |
| Cooling System | Natural Ventilation | Same as baseline. |
| Occupancy Schedule | 8am – 4pm | Same as baseline. |
| Lighting Power Density | 1.83 watts per square foot | Same as baseline. |
| Lighting Schedule | Varies monthly based on available daylight hours, supplemental lighting operates between 5 – 11 hours per day to target 20 total light hours. | Same as baseline. |

###### Electric Energy Savings

NA

###### Summer Coincident Peak Demand Savings

NA

###### Natural Gas Savings

Natural gas savings are presented for each climate zone per square foot of greenhouse floor area, which constitutes all floor space under the thermal curtains, including pathways and growing canopy.

| Zone | Therm Savings per Square Foot |
| --- | --- |
| Rockford | 0.394 |
| Chicago | 0.361 |
| Springfield | 0.325 |
| Belleville | 0.317 |
| Marion | 0.265 |

Example:

A 15,000 sq.ft greenhouse located in Chicago is retrofitting a thermal curtain with an IR film above the growing zone. The annual savings for the installation will be computed as:

Savings = 15,000 * 0.361 = 5,415 therms.

###### Water and Other Non-Energy Impact Descriptions and Calculation

NA

###### Deemed O&M Cost Adjustment Calculation

NA

###### Measure Code: CI-AGE-GHEAT-V01-220101

###### Review Deadline: 1/1/2025

### Infrared Film for Greenhouse

###### Description

Existing greenhouse construction with polyethlene (PE) roofs allows for heat transmission loss up to 50%. The existing PE roofs cause radiant heat to enter the space during daytime, but also lead to heat loss to the outside during the night. This issue can be addressed using Infrared-treated (IR) films. They can be applied on the interior side of the PE roof, reducing heat loss through the roof overnight by absorbing and re-emitting infrared radiation and can reduce heat loss by up to 20%. Reduction in heat loss through the roof overnight reduces the heating load on the greenhouse heating system. This measure applies to greenhouses with polyethlene roof construction.

This measure case is defined as a greenhouse roof with infrared (IR) inhibiting film additive on the inflated double polyethylene roof. This measure was developed to be applicable to the following program types: NC, RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is infrared film installed on the interior of a PE roof glazing in a gas-heated greenhouse. The recommendation is to use one layer of IR film placed as the inner layer of the roof glazing. Doing this allows the wetting agent that is also included in most films to conduct the condensed moisture away.

###### Definition of Baseline Equipment

The baseline equipment is a gas-heated greenhouse with PE roof glazing construction and no infrared film.

###### Deemed Lifetime of Efficient Equipment

The measure lifetime for infrared film is 5 years.

###### Deemed Measure Cost

Incremental cost for IR films installed in new/retrofit applications is $0.02 per square foot of IR film.

###### Loadshape

NA

###### Coincidence Factor

NA

Algorithm

###### Calculation of Energy Savings

Energy savings are estimated using EnergyPlus version 9.4 whole-building energy simulation. The greenhouse geometry used in the EnergyPlus model consists of 4 connected bays, each bay with a gable type roof construction, measuring 36 feet wide by 100 feet long. The total conditioned floor area of the modeled greenhouse is 14,210 square feet, and savings are normalized per square foot of conditioned floor area. The greenhouse is conditioned by gas-fired unit heaters and has no dedicated cooling system. Cooling is typically achieved by natural ventilation and exhaust/ventilations fans in the greenhouse space.

Baseline and efficient models were developed for each Illinois climate zone using inputs for key greenhouse construction characteristics and sources as listed in the following table:

| Input Parameter | Baseline Value | Efficient Value |
| --- | --- | --- |
| Roof Glazing | Double PE film, U-value 0.7 (Btu/h · ft2 · °F) | IR-treated double PE film, U-value 0.5 (Btu/h · ft2 · °F) |
| Wall Glazing | Single PE film, U-value 1.1 (Btu/h · ft2 · °F) | Same as baseline. |
| Infiltration | 1.5 Air Change per Hour (ACH) | Same as baseline. |
| Ventilation | 10 cubic feet per minute (CFM) per area (ft2) | Same as baseline. |
| Heating System | Gas-fired unit heater, 0.8 efficiency | Same as baseline. |
| Thermostat Setpoint | Heating setpoint 70°F | Same as baseline. |
| Cooling System | Natural Ventilation | Same as baseline. |
| Occupancy Schedule | 8am – 4pm | Same as baseline. |
| Lighting Power Density | 1.83 watts per square foot | Same as baseline. |
| Lighting Schedule | Varies monthly based on available daylight hours, supplemental lighting operates between 5 – 11 hours per day to target 20 total light hours. | Same as baseline. |

###### Electric Energy Savings

NA

###### Summer Coincident Peak Demand Savings

NA

###### Natural Gas Savings

Natural gas savings are presented for each climate zone per square foot of greenhouse floor area, which constitutes all floor space under the thermal curtains, including pathways and growing canopy.

| Zone | Therm Savings per Square Foot of Floor Area |
| --- | --- |
| Rockford | 0.256 |
| Chicago | 0.232 |
| Springfield | 0.206 |
| Belleville | 0.198 |
| Marion | 0.163 |

For example:

A 15,000 sq.ft greenhouse located in Chicago is retrofitting its roof glazing material with an infrared film. The annual savings for the installation will be computed as:

Savings = 15,000 * 0.232 = 3,480 therms.

###### Water and Other Non-Energy Impact Descriptions and Calculation

NA

###### Deemed O&M Cost Adjustment Calculation

NA

###### Measure Code: CI-AGE-GFILM-V01-220101

###### Review Deadline: 1/1/2025

### ENERGY STAR Dairy Water Heater

###### Description

This measure is for upgrading from federal minimum code efficiency to an ENERGY STAR commercial or residential high efficiency water heater on a dairy farm. Water heaters may have a tank for water storage or may be instantaneous. For electric water heaters to be certified by ENERGY STAR, heat pump technology is required. Energy performance of residential water heaters is typically measured by Uniform Energy Factor (UEF) [large sizes are measured by Energy Factor (EF)], gas commercial water heaters are rated by Thermal Efficiency (Et), and electric commercial water heaters are rated by Coefficient of Performance (COP).

###### Definition of Efficient Equipment

The high efficiency equipment must meet ENERGY STAR specifications.

###### Definition of Baseline Equipment

Time of sale: The baseline condition is assumed to be a new standard water heater of the same type and service (residential, commercial) as the existing unit being replaced. The new equipment must exceed federal standard efficiency based on equipment type, size category, and subcategory/rating condition.

New Construction: The baseline condition is a new standard water heater of the same type as the efficient, meeting the IECC code level in place at the time the building permit was issued. Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

For dairies, efficiency requirements assume a high draw pattern.

| Service Type | Equipment Type | Size Category | Federal Minimum Efficiency Requirements |
| --- | --- | --- | --- |
| Residential | Gas-Fired Storage Water Heater ≤75,000 Btu/h | ≥20 gal and ≤55 gal | UEF = 0.6920 – 0.0013 × Vr |
|  |  | >55 gal and ≤100 gal | UEF = 0.8072 – 0.0003 × Vr |
|  |  | > 100 gal | EF = 0.6200 – 0.0019 × Vr |
|  | Gas Fired Instantaneous Water Heater | < 2 gal and > 50,000 Btu/h | UEF = 0.81 |
|  | Electric Storage Water Heater | ≥20 gal and ≤55 gal | UEF = 0.9349 – 0.0001 × Vr |
|  |  | >55 gal and ≤120 gal | UEF = 2.2418−0.0011 × Vr |
|  |  | > 120 gal | EF = 0.9300−0.00132 × Vr |
| Residential-duty Commercial | High Capacity Storage Gas-Fired Storage Water Heaters > 75,000 Btu/h. | ≤120 gallon tanks | UEF = 0.6597 – (0.0009 * Vr |
| Commercial | Gas Storage | Any | 80% Et |
|  | Gas Instantaneous | Any | 80% Et |
|  | Electric Storage | Any | 2.18 COP |

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years for storage units, 20 years for tankless water heaters.

###### Deemed Measure Cost

The full install cost and incremental cost assumptions are provided below. Actual costs should be used where available:

| Equipment Type | Category | Installed Cost | Incremental Cost |
| --- | --- | --- | --- |
| Gas Storage Water Heaters ≥ 75,000 Btu/hr, ≤55 gallons | Baseline | $616 | N/A |
|  | Efficient | $1,055 | $440 |
| Gas Storage Water Heaters > 75,000 Btuh/h | 80% Et | $4,886 | N/A |
|  | 83% Et | $5,106 | $220 |
|  | 84% Et | $5,299 | $413 |
|  | 85% Et | $5,415 | $529 |
|  | 86% Et | $5,532 | $646 |
|  | 87% Et | $5,648 | $762 |
|  | 88% Et | $5,765 | $879 |
|  | 89% Et | $5,882 | $996 |
|  | 90% Et | $6,021 | $1,135 |
| Electric Storage Water Heaters | 50 gallons |  | $1,050 |
|  | 80 gallons |  | $1,050 |
|  | 100 gallons |  | $1,950 |

###### Loadshape

For electric hot water heaters, use Loadshape C02 – Commercial Electric DHW.

###### Coincidence Factor

The coincidence factor is assumed to be 0.925.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Electric energy savings are calculated for electric water heaters per the equations given below.

∆kWh= (TOUT-TIN)*HotWaterUseGallon* γWater*1*1UEFelecbase- 1UEFEff3412

Where:

TOUT		= Tank Temperature

= 170°F

TIN		= Incoming water temperature from well or municipal system or other

= Take measurement if possible, otherwise use the following assumptions.

= 52.3°F, average well water temperature if no Dairy Refrigeration Heat Recovery system installed

= 120°F, if Dairy Refrigeration Heat Recovery system is operational

= 86°F, if unknown

HotWaterUseGallon	= Estimated annual hot water consumption (gallons)

= Actual if possible to provide reasonable custom estimate. If not, use the following formula:

= GPD * 365

GPD = average gallons of hot water usage per day (=1.30 gallons per cow per day) * Number of Milking Cows being served by the water heater

γWater 			= Density of Water (lb/gal)

= 8.33 lbs/gal

1			= Specific Heat of Water (Btu/lb°F)

UEFelecbase	= Rated efficiency of baseline water heater expressed as Uniform Energy Factor (UEF)

UEFeff	= Rated efficiency of the efficient water heater expressed as Uniform Energy Factor (UEF)

= Actual per ENERGY STAR certified equipment product list

3412	= Converts Btu to kWh

###### Summer Coincident Peak Demand Savings

ΔkW= ΔkWhHours*CF

Where:

Hours			= Full load hours of water heater

= 6,461

CF			= Summer Peak Coincidence Factor for measure

= 0.925

For example, a residential ENERGY STAR water heater of 100 gallons rated capacity and UEF of 3.5 will be serving hot water to 101 cows milked daily. The farm does not currently have any dairy refrigeration heat recovery system so they are directly getting the water from a well and heating it to 170°F to clean the milking equipment.

∆kWh= (TOUT-TIN)*HotWaterUseGallon* γWater*1*1UEFelecbase- 1UEFEff3,412

∆kWh∆kWhyr= 170 °F-52.3 °F*101 cows*1.30galcowday* 8.33lbgal*1Btulb°F*12.2418-0.0011 × 100-13.53,412BtukWh* 365daysyr

=2,527 kWhkWhyr

For Demand Saving:

ΔkW= ΔkWhHours*CF

ΔkW= 2,5276,461*0.925=0.36 kW

###### Natural Gas Savings

Natural gas energy savings are calculated for natural gas storage water heaters per the quations given below.

∆Therms= Tout-Tin*HotWaterUseGallon* γWater*1*1UEFgasbase- 1UEFEff100,000

Where:

100,000			= Converts Btu to Therms

For example, a 150,000 Btu/h gas storage water heater of 100 gallons rated volume and UEF of 0.9 delivers hot water for 101 cows milked daily. The farm has a dairy refrigeration heat recovery system that supplies 120 °F water to the heater. The farm uses 170°F hot water for milking equipment cleaning.

∆Therms= (TOUT-TIN)×HotWaterUseGallon× γWater×1×1UEFgasbase- 1UEFEff100,000Btutherm

∆Therms= 170-120℉ ×101 cows×1.30galcowday× 365daysyr×8.33lbgal×1Btulb℉×10.8072 – 0.0003 × 100- 10.9100,000BtuTherm×365Daysyr

∆Therms=35Thermsyr Therms

UEFgasbase	= Rated efficiency of baseline water heater (Expressed as Uniform Energy Factor (UEF).

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-ESWH-V01-220101

###### Review Deadline: 1/1/2025

## Food Service Equipment End Use

### Combination Oven

###### Description

This measure applies to both natural gas fired and electric high efficiency combination convection and steam ovens installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS, RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure, the installed equipment must be a new natural gas or electric combination oven meeting the ENERGY STAR idle rate and cooking efficiency requirements as specified below.

ENERGY STAR Requirements (Version 2.1, Effective January 1, 2014)

| Fuel Type | Operation | Idle Rate (Btu/h for Gas, kW for Electric) | Cooking-Energy Efficiency, (%) |
| --- | --- | --- | --- |
| Natural Gas | Steam Mode Convection Mode | ≤ 200P+6,511 ≤ 150P+5,425 | ≥ 41 ≥ 56 |
| Electric | Steam Mode Convection Mode | ≤ 0.133P+0.6400 ≤ 0.080P+0.4989 | ≥ 55 ≥ 76 |

Note: P = Pan capacity as defined in Section 1.S, of the Commercial Ovens Program Requirements Version 2.1

###### Definition of Baseline Equipment

The baseline equipment is a natural gas or electric combination oven that is not ENERGY STAR certified.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The costs vary based on the efficiency and make of the equipment. Actual costs should be used.

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

Summer Peak Coincidence Factor for measure is provided below for different building type:

| Location | CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

The algorithm below applies to electric combination ovens only.

∆kWh 	= (CookingEnergyConvElec + CookingEnergySteamElec + IdleEnergyConvElec + 	IdleEnergySteamElec) * Days / 1,000

Where:

CookingEnergyConvElec	= Change in total daily cooking energy consumed by electric oven in convection 					mode

= LBElec * (EFOODConvElec / ElecEFFConvBase - EFOODConvElec / ElecEFFConvEE) * %Conv

CookingEnergySteamElec	= Change in total daily cooking energy consumed by electric oven in steam 					mode

= LBElec * (EFOODSteamElec / ElecEFFSteamBase – EFOODSteamElec / ElecEFFSteamEE) * 					%Steam

IdleEnergyConvElec	= Change in total daily idle energy consumed by electric oven in convection 					mode

= [(ElecIDLEConvBase * ((HOURS – LBElec/ElecPCConvBase) * %Conv)) - (ElecIDLEConvEE * 					((HOURS - LBElec/ElecPCConvEE) * %Conv))]

IdleEnergySteamElec	= Change in total daily idle energy consumed by electric oven in convection 					mode

= [(ElecIDLESteamBase * ((HOURS – LBElec/ElecPCSteamBase) * %Steam)) - (ElecIDLESteamEE 					* ((HOURS - LBElec/ElecPCSteamEE) * %Steam))]

Where:

LBElec 			= Estimated mass of food cooked per day for electric oven (lbs/day)

= Custom, or if unknown, use 200 lbs (If P <15) or 250 lbs (If P >= 15)

EFOODConvElec 		= Energy absorbed by food product for electric oven in convection mode

= Custom or if unknown, use 73.2 Wh/lb

ElecEFF			= Cooking energy efficiency of electric oven

= Custom or if unknown, use values from table below

|  | Base | EE |
| --- | --- | --- |
| ElecEFFConv | 72% | 76% |
| ElecEFFSteam | 49% | 55% |

%Conv 			= Percentage of time in convection mode

= Custom or if unknown, use 50%

EFOODSteamElec 		= Energy absorbed by food product for electric oven in steam mode

= Custom or if unknown, use 30.8 Wh/lb

%steam 			= Percentage of time in steam mode

= 1 - %conv

ElecIDLEBase 		= Idle energy rate (W) of baseline electric oven

= Custom or if unknown, use values from table below

| Pan Capacity | Convection Mode (ElecIDLEConvBase) | Steam Mode (ElecIDLESteamBase) |
| --- | --- | --- |
| < 15 | 1,320 | 5,260 |
| > = 15 | 2,280 | 8,710 |

HOURS		 	= Average daily hours of operation

= Custom or if unknown, use 12 hours

ElecPCBase 		= Production capacity (lbs/hr) of baseline electric oven

= Custom of if unknown, use values from table below

| Pan Capacity | Convection Mode (ElecPCConvBase) | Steam Mode (ElecPCSteamBase) |
| --- | --- | --- |
| < 15 | 79 | 126 |
| > = 15 | 166 | 295 |

ElecIDLEConvEE		 = Idle energy rate of ENERGY STAR electric oven in convection mode

= (0.08*P +0.4989)*1000

ElecPCEE 			= Production capacity (lbs/hr) of ENERGY STAR electric oven

= Custom of if unknown, use values from table below

| Pan Capacity | Convection Mode (ElecPCConvEE) | Steam Mode (ElecPCSteamEE) |
| --- | --- | --- |
| < 15 | 119 | 177 |
| > = 15 | 201 | 349 |

ElecIDLESteamEE		= Idle energy rate of ENERGY STAR electric oven in steam mode

= (0.133* P+0.64)*1000

Days			= Days of operation per year

= Custom or if unknown, use 365 days per year

1,000			= Wh to kWh conversion factor

For example, a 10-pan capacity electric combination oven would save:

∆kWh	 = (CookingEnergyConvElec + CookingEnergySteamElec + IdleEnergyConvElec + IdleEnergySteamElec) * Days / 1,000

CookingEnergyConvElec	= 200 * (73.2 / 0.72 – 73.2 / 0.76) * 0.50

= 535 Wh

CookingEnergySteamElec	= 200 * (30.8 / 0.49 – 30.8 / 0.55) * (1 – 0.50)

= 686 Wh

IdleEnergyConvElec	= [(1,320 * ((12 – 200/79) * 0.50)) - (1,299 *((12 - 200/119) * 0.50))]

= -453 Wh

IdleEnergySteamElec	= [(5,260 * ((12 – 200/126) * (1 – 0.50))) - (1,970 * ((12 - 200/177) * (1 – 0.50)))]

= 16,678 Wh

∆kWh 	= (535 + 686 + -453 + 16,678) * 365 /1,000

= 6,368 kWh

###### Summer Coincident Peak Demand Savings

∆kW 	= ∆kWh / (HOURS * DAYS) *CF

Where:

CF		 = Summer peak coincidence factor is dependent on building type:

| Location | CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |

All other variables as defined above.

For example, a 10-pan capacity electric combination oven in a Full Service Limited Menu  restaurant would save:

∆kW	= ∆kWh / (HOURS * DAYS) *CF

= 6,368/ (12 * 365) * 0.51

= 0.74 kW

###### Natural Gas Energy Savings

The algorithm below applies to natural gas combination ovens only.

∆Therms  = (CookingEnergyConvGas + CookingEnergySteamGas + IdleEnergyConvGas + 		     IdleEnergySteamGas) * Days / 100,000

Where:

CookingEnergyConvGas	= Change in total daily cooking energy consumed by gas oven in convection 					mode

= LBGas * (EFOODConvGas / GasEFFConvBase - EFOODConvGas / GasEFFConvEE) * %Conv

CookingEnergySteamGas	= Change in total daily cooking energy consumed by gas oven in steam 						mode

= LBGas * (EFOODSteamGas / GasEFFSteamBase – EFOODSteamGas / GasEFFSteamEE) * 					%Steam

IdleEnergyConvGas		= Change in total daily idle energy consumed by gas oven in convection 					mode

= [(GasIDLEConvBase * ((HOURS – LBGas/GasPCConvBase) * %Conv)) - (GasIDLEConvEE * 					((HOURS - LBGas/GasPCConvEE) * %Conv))]

IdleEnergySteamGas	= Change in total daily idle energy consumed by gas oven in convection 					mode

= [(GasIDLESteamBase * ((HOURS – LBGas/GasPCSteamBase) * %Steam)) - (GasIDLESteamEE 					* ((HOURS - LBGas/GasPCSteamEE) * %Steam))]

Where:

LBGas			= Estimated mass of food cooked per day for gas oven (lbs/day)

= Custom, or if unknown, use 200 lbs (If P <15), 250 lbs (If 15 <= P 30), or 400 				lbs (If P = >30)

EFOODConvGas 		= Energy absorbed by food product for gas oven in convection mode

= Custom or if unknown, use 250 Btu/lb

GasEFF			= Cooking energy efficiency of gas oven

= Custom or if unknown, use values from table below

|  | Base | EE |
| --- | --- | --- |
| GasEFFConv | 52% | 56% |
| GasEFFSteam | 39% | 41% |

EFOODSteamGas 		= Energy absorbed by food product for gas oven in steam mode

= Custom or if unknown, use 105 Btu/lb

GasIDLEBase 		= Idle energy rate (Btu/hr) of baseline gas oven

= Custom or if unknown, use values from table below

| Pan Capacity | Convection Mode (GasIDLEConvBase) | Steam Mode (GasIDLESteamBase) |
| --- | --- | --- |
| < 15 | 8,747 | 18,656 |
| 15-30 | 10,788 | 24,562 |
| >30 | 13,000 | 43,300 |

GasPCBase 		= Production capacity (lbs/hr) of baseline gas oven

= Custom of if unknown, use values from table below

| Pan Capacity | Convection Mode (GasPCConvBase) | Steam Mode (GasPCSteamBase) |
| --- | --- | --- |
| < 15 | 125 | 195 |
| 15-30 | 176 | 211 |
| >30 | 392 | 579 |

GasIDLEConvEE		 = Idle energy rate of ENERGY STAR gas oven in convection mode

= 150*P + 5,425

GasPCEE 			= Production capacity (lbs/hr) of ENERGY STAR gas oven

= Custom of if unknown, use values from table below

| Pan Capacity | Convection Mode (GasPCConvEE) | Steam Mode (GasPCSteamEE) |
| --- | --- | --- |
| < 15 | 124 | 172 |
| 15-30 | 210 | 277 |
| >30 | 394 | 640 |

GasIDLESteamEE		= Idle energy rate of ENERGY STAR gas oven in steam mode

= 200 * P +6511

100,000 			= Conversion factor from Btu to therms

All other variables as defined above.

For example, a 10-pan capacity gas combination oven would save:

∆Therms	 = (CookingEnergyConvGas + CookingEnergySteamGas + IdleEnergyConvGas + 	IdleEnergySteamGas) * Days / 100,000

CookingEnergyConvGas	= 200 * (250 / 0.52 – 250 / 0.56) * 0.50

=3,434 therms

CookingEnergySteamGas	= 200 * (105 / 0.39 – 105 / 0.41) * (1 – 0.50)

= 1,313 therms

IdleEnergyConvGas		= [(8,747 * ((12 – 200/125) * 0.50)) - (6,925 *((12 - 200/124) * 0.50))]

= 9,519 therms

IdleEnergySteamGas	= [(18,658 * ((12 – 200/195) * (1 – 0.50))) - (8,511 * ((12 - 200/172) * (1 – 0.50)))]

= 56,251 therms

∆Therms 	= (3,434 + 1,313 + 9,519 + 56,251) * 365 /100,000

= 257 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-CBOV-V02-160601

###### Review Deadline: 1/1/2023

### Commercial Solid and Glass Door Refrigerators & Freezers

###### Description

This measure relates to the installation of a new reach-in commercial refrigerator or freezer meeting ENERGY STAR efficiency standards. ENERGY STAR labeled commercial refrigerators and freezers are more energy efficient because they are designed with components such as ECM evaporator and condenser fan motors, hot gas anti-sweat heaters, or high-efficiency compressors, which will significantly reduce energy consumption.

This measure was developed to be applicable to the following program types: TOS and NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be a new ENERGY STAR certified vertical closed solid or glass door refrigerator or freezer meeting energy consumptions requirements as determined by door type (solid or glass) and refrigerated volume (V).

ENERGY STAR Requirements (Version 4.0, Effective March 27, 2017)

| Volume (ft3) | Maximum Daily Energy Consumption (kWh/day) |  |
| --- | --- | --- |
|  | Refrigerator | Freezer |
| Vertical Closed |  |  |
| Solid Door |  |  |
| 0 < V < 15 | ≤ 0.022V + 0.97 | ≤ 0.21V + 0.9 |
| 15 ≤ V < 30 | ≤ 0.066V + 0.31 | ≤ 0.12V + 2.248 |
| 30 ≤ V < 50 | ≤ 0.04V + 1.09 | ≤ 0.285V -2.703 |
| V ≥ 50 | ≤ 0.024V + 1.89 | ≤ 0.142V + 4.445 |
| Glass Door |  |  |
| 0 < V < 15 | ≤ 0.095V + 0.445 | ≤ 0.232V + 2.36 |
| 15 ≤ V < 30 | ≤ 0.05V + 1.12 |  |
| 30 ≤ V < 50 | ≤ 0.076V + 0.34 |  |
| V ≥ 50 | ≤ 0.105V – 1.111 |  |

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to be a new vertical closed solid or glass door refrigerator or freezer that is not ENERGY STAR certified.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost per cubic foot of chilled or frozen compartment volume for this measure is provided below.

| Equipment Type | Incremental Cost per Cubic Foot (ft3) |
| --- | --- |
| Solid Door |  |
| Refrigerator | $24.21 |
| Freezer | $30.41 |
| Glass Door |  |
| Refrigerator | $24.77 |
| Freezer | $33.01 |

###### Loadshape

Loadshape C23 - Commercial Refrigeration

###### Coincidence Factor

The summer peak coincidence factor for this measure is assumed to be 0.937.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh	= (kWhbase – kWhee) * 365.25

Where:

kWhbase	= baseline maximum daily energy consumption in kWh

= calculated using actual chilled or frozen compartment volume (V) of the efficient unit as shown in the table below.

| Type | kWhbase |
| --- | --- |
| Solid Door Refrigerator | 0.05 * V + 1.36 |
| Glass Door Refrigerator | 0.1 * V + 0.86 |
| Solid Door Freezer | 0.22 * V + 1.38 |
| Glass Door Freezer | 0.29 * V + 2.95 |

kWhee	= efficient maximum daily energy consumption in kWh

= calculated using actual chilled or frozen compartment volume (V) of the efficient unit as shown in the table below.

| Volume (ft3) | kWhee |  |
| --- | --- | --- |
|  | Refrigerator | Freezer |
| Vertical Closed |  |  |
| Solid Door |  |  |
| 0 < V < 15 | ≤ 0.022V + 0.97 | ≤ 0.21V + 0.9 |
| 15 ≤ V < 30 | ≤ 0.066V + 0.31 | ≤ 0.12V + 2.248 |
| 30 ≤ V < 50 | ≤ 0.04V + 1.09 | ≤ 0.285V -2.703 |
| V ≥ 50 | ≤ 0.024V + 1.89 | ≤ 0.142V + 4.445 |
| Glass Door |  |  |
| 0 < V < 15 | ≤ 0.095V + 0.445 | ≤ 0.232V + 2.36 |
| 15 ≤ V < 30 | ≤ 0.05V + 1.12 |  |
| 30 ≤ V < 50 | ≤ 0.076V + 0.34 |  |
| V ≥ 50 | ≤ 0.105V – 1.111 |  |

V	= the chilled or frozen compartment volume (ft3) (as defined in the Association of Home Appliance Manufacturers Standard HRF1–1979)

= Actual installed

365.25 		= days per year

For example, a solid door refrigerator with a volume of 15 would save

ΔkWh	= (2.11 – 1.30) * 365.25

= 296 kWh

###### Summer Coincident Peak Demand Savings

ΔkW 	= ΔkWh / HOURS * CF

Where:

HOURS		= equipment is assumed to operate continuously, 24 hours per day, 365.25 days per year.

= 8766

CF 		= Summer Peak Coincidence Factor for measure

= 0.937

For example, a solid door refrigerator with a volume of 15 would save

ΔkW 		= 296/ 8766 * .937

=0.0316 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-CSDO-V02-190101

###### Review Deadline: 1/1/2024

### Commercial Steam Cooker

###### Description

To qualify for this measure the installed equipment must be an ENERGY STAR® steamer in place of a standard steamer in a commercial kitchen.  Savings are presented dependent on the pan capacity and corresponding idle rate at heavy load cooking capacity and if the steamer is gas or electric.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be as follows:

| Gas | Electric |
| --- | --- |
| ENERGY STAR® qualified with 38% minimum cooking energy efficiency at heavy load (potato) cooking capacity for gas steam cookers. | ENERGY STAR® qualified with 50% minimum cooking energy efficiency at heavy load (potato) cooking capacity for electric steam cookers. |

###### Definition of Baseline Equipment

The baseline condition is assumed to be a non-ENERGY STAR® commercial steamer at end of life.  It is assumed that the efficient equipment and baseline equipment have the same number of pans.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $998 for a natural gas steam cooker  or $2490 for an electric steam cooker.

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

Summer Peak Coincidence Factor for measure is provided below for different building type:

| Location | CF CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |
| Unknown | 0.41 |

Algorithm

###### Calculation of Savings

Formulas below are applicable to both gas and electric steam cookers.  Please use appropriate lookup values and identified flags.

###### Energy Savings

ΔSavings  	= (ΔIdle Energy + ΔPreheat Energy + ΔCooking Energy)  * Z

For a gas cooker:  	 	ΔSavings  = ΔBtu * 1/100,000  * Z

For an electric steam cooker:  	ΔSavings  = ΔkWh *Z

Where:

Z 	= days/yr steamer operating (use 365.25 days/yr if heavy use restaurant and exact number unknown)

ΔIdle Energy 	= ((((1- CSM%Baseline)* IDLEBASE  + CSM%Baseline * PCBASE * EFOOD / EFFBASE) * (HOURSday - (F / PCBase) - ( PREnumber *0.25))) - (((1- CSM%ENERGYSTAR) * IDLEENERGYSTAR  + CSM%ENERGYSTAR  * PCENERGY * EFOOD / EFFENERGYSTAR) * (HOURSDay - (F l/ PCENERGY ) - (PREnumber * 0.25 ))))

Where:

CSM%Baseline 	= Baseline Steamer Time in Manual Steam Mode (% of time)

= 90%

IDLEBase 		= Idle Energy Rate of Base Steamer

| Number of Pans | IDLEBASE - Gas, Btu/hr | IDLEBASE - Electric, kw |
| --- | --- | --- |
| 3 | 11,000 | 1.0 |
| 4 | 14,667 | 1.33 |
| 5 | 18,333 | 1.67 |
| 6 | 22,000 | 2.0 |

PCBase 			= Production Capacity of Base Steamer

| Number of Pans | PCBASE, gas (lbs/hr) | PCBASE, electric (lbs/hr) |
| --- | --- | --- |
| 3 | 65 | 70 |
| 4 | 87 | 93 |
| 5 | 108 | 117 |
| 6 | 130 | 140 |

EFOOD= 	Amount of Energy Absorbed by the food during cooking known as ASTM Energy to Food (Btu/lb or kW/lb)

=105 Btu/lb (gas steamers) or 0.0308 (electric steamers)

EFFBASE			=Heavy Load Cooking Efficiency for Base Steamer

=15% (gas steamers) or 26% (electric steamers)

HOURSday 		= Average Daily Operation (hours)

| Type of Food Service | Hoursday |
| --- | --- |
| Fast Food, limited menu | 4 |
| Fast Food, expanded menu | 5 |
| Pizza | 8 |
| Full Service, limited menu | 8 |
| Full Service, expanded menu | 7 |
| Cafeteria | 6 |
| Unknown | 6 |
| Custom | Varies |

F			= Food cooked per day (lbs/day)

= custom or if unknown, use 100 lbs/day

CSM%ENERGYSTAR		= ENERGY STAR Steamer's Time in Manual Steam Mode (% of time)

= 0%

IDLEENERGYSTAR 		= Idle Energy Rate of ENERGY STAR®

| Number of Pans | IDLEENERGY STAR – gas, (Btu/hr) | IDLEENERGY STAR – electric, (kW) |
| --- | --- | --- |
| 3 | 6,250 | 0.40 |
| 4 | 8,333 | 0.53 |
| 5 | 10,417 | 0.67 |
| 6 | 12,500 | 0.80 |

PCENERGY			= Production Capacity of ENERGY STAR® Steamer

| Number of Pans | PCENERGY - gas(lbs/hr) | PCENERGY – electric (lbs/hr) |
| --- | --- | --- |
| 3 | 55 | 50 |
| 4 | 73 | 67 |
| 5 | 92 | 83 |
| 6 | 110 | 100 |

EFFENERGYSTAR		= Heavy Load Cooking Efficiency for ENERGY STAR® Steamer(%)

=38% (gas steamer) or 50% (electric steamer)

PREnumber	= Number of preheats per day

=1 (if unknown, use 1)

ΔPreheat Energy 	= ( PREnumber  * Δ Preheat)

Where:

PREnumber	= Number of Preheats per Day

=1 (if unknown, use 1)

PREheat 		= Preheat energy savings per preheat

=  11,000 Btu/preheat (gas steamer) or 0.5 kWh/preheat (electric steamer)

ΔCooking Energy 	= ((1/ EFFBASE) - (1/ EFFENERGY STAR®)) * F * EFOOD

Where:

EFFBASE		=Heavy Load Cooking Efficiency for Base Steamer

=15% (gas steamer) or 26% (electric steamer)

EFFENERGYSTAR 	=Heavy Load Cooking Efficiency for ENERGY STAR® Steamer

=38% (gas steamer) or 50% (electric steamer)

F		= Food cooked per day (lbs/day)

= custom or if unknown, use 100 lbs/day

EFOOD 	= Amount of Energy Absorbed by the food during cooking known as ASTM Energy to Food

| EFOOD - gas(Btu/lb) | EFOOD (kWh/lb) |
| --- | --- |
| 105 | 0.0308 |

For example, for a gas steam cooker:  A 3 pan steamer in a full service restaurant

ΔSavings  		= (ΔIdle Energy + ΔPreheat Energy + ΔCooking Energy)  * Z * 1/100.000

ΔIdle Energy 	= ((((1- 0.9)* 11000 + 0.9 * 65 * 105 /0.15 )*(7 - (100 / 65)-(1*0.25))) - (((1-0) * 6250 + 0  * 55 * 105   / 0.38) * (7 - (100 / 55) - (1*0.25))))

= 188,321

ΔPreheat Energy 	= (1 *11,000)

= 11,000

ΔCooking Energy 	= (((1/ 0.15) - (1/ 0.38)) * (100 lb/day * 105 btu/lb)))

= 42368

ΔTherms = (188321 + 11000 + 42368) * 365.25 *1/100,000

= 883 therms

For an electric steam cooker:  A 3 pan steamer in a cafeteria:

ΔSavings  		= (ΔIdle Energy + ΔPreheat Energy + ΔCooking Energy) * Z

ΔIdle Energy 	= ((((1- .9)* 1.0 + .9 * 70 * 0.0308 /0.26 )*(6 - (100 / 70)-(1*.25))) - (((1-0) * 0.4 + 0  * 50 * 0.0308   / 0.50) * (6 - (100 / 50) - (1*0.25))))

= 31.18

ΔPreheat Energy 	= (1 *0.5))

= 0.5

ΔCooking Energy 	= (((1/ 0.26) - (1/ 0.5)) * (100 * 0.0308)))

= 5.69

ΔkWh	= (31.18 + 0.5 + 5.69) * 365.25 days

= 13,649 kWh

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure, but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater supply

Where

Ewater supply	= IL Supply Energy Factor (kWh/Million Gallons)

=2,571

For example, an electric 3 pan steamer with average efficiency in a full service restaurant

ΔWater (gallons)		= (40 - 10) * 7 * 365.25

= 76,703 gallons

ΔkWhwater 	= 76,703/1,000,000*2,571

= 197 kWh

###### Summer Coincident Peak Demand Savings

This is only applicable to the electric steam cooker.

ΔkW = (ΔkWh/(HOURSDay *DaysYear))  *  CF

Where:

ΔkWh 	= Annual kWh savings from measure as calculated above. Note do not include the secondary savings in this calculation.

CF	=Summer Peak Coincidence Factor for measure is provided below for different locations:

| Location | CF CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |

DaysYear		=Annual Days of Operation

=custom or 365.25 days a year

Other values as defined above

For example, for 3 pan electric steam cooker located in a cafeteria:

ΔkW		= (ΔkWh/(HOURSDay *DaysYear))  *  CF

= (13,649/ (6 * 365.25)) * 0.39

= 2.43 kW

###### Water Impact Descriptions and Calculation

This is applicable to both gas and electric steam cookers.

ΔWater (gallons) = (WBASE -WENERGYSTAR®)*HOURSDay *DaysYear

Where

WBASE		= Water Consumption Rate of Base Steamer (gal/hr)

= 40

WENERGYSTAR 	= Water Consumption Rate of ENERGY STAR® Steamer look up

| CEE Tier | gal/hr |
| --- | --- |
| Tier 1A | 15 |
| Tier 1B | 4 |
| Avg Efficient | 10 |
| Avg Most Efficient | 3 |

DaysYear		=Annual Days of Operation

=custom or 365.25 days a year

For example, an electric 3 pan steamer with average efficiency in a full service restaurant

ΔWater (gallons)	= (40 -10) * 7 * 365.25

= 76,703 gallons

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-STMC-V05-190101

###### Review Deadline: 1/1/2023

### Conveyor Oven

###### Description

This measure applies to natural gas fired high efficiency conveyor ovens installed in commercial kitchens replacing existing natural gas units with conveyor width greater than 25 inches.

Conveyor ovens are available using four different heating processes: infrared, natural convection with a ceramic baking hearth, forced convection or air impingement, or a combination of infrared and forced convection.  Conveyor ovens are typically used for producing a limited number of products with similar cooking requirements at high production rates.  They are highly flexible and can be used to bake or roast a wide variety of products including pizza, casseroles, meats, breads, and pastries.

Some manufacturers offer an air-curtain feature at either end of the cooking chamber that helps to keep the heated air inside the conveyor oven.  The air curtain operates as a virtual oven wall and helps reduce both the idle energy of the oven and the resultant heat gain to the kitchen.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a natural gas conveyor oven with a tested baking energy efficiency > 42% and an idle energy consumption rate < 57,000 Btu/hr utilizing ASTM standard F1817.

###### Definition of Baseline Equipment

The baseline equipment is an existing pizza deck oven at end of life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 17 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $1800.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

The annual natural gas energy savings from this measure is a deemed value equaling 884 Therms.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-CVOV-V02-180101

###### Review Deadline: 1/1/2024

### ENERGY STAR Convection Oven

###### Description

This measure applies to natural gas fired ENERGY STAR convection ovens installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a natural gas convection oven with a cooking efficiency ≥ 46% utilizing ASTM standard 1496 and an idle energy consumption rate < 12,000 Btu/hr.

###### Definition of Baseline Equipment

The baseline equipment is a natural gas convection oven that is not ENERGY STAR certified and is at end of life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $50.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

Custom calculation below; otherwise, use deemed value of 306 therms.

ΔTherms 	= (ΔDailyIdle Energy + ΔDailyPreheat Energy + ΔDailyCooking Energy) * Days /100000

Where:

ΔDailyIdleEnergy 		= (IdleBase* IdleBaseTime)- (IdleENERGYSTAR * IdleENERGYSTARTime)

ΔDailyPreheatEnergy 	= (PreHeatNumberBase * PreheatTimeBase / 60 * PreheatRateBase) – (PreheatNumberENERGYSTAR * PreheatTimeENERGYSTAR/60 * PreheatRateENERGYSTAR)

ΔDailyCookingEnergy 	= (LB * EFOOD/ EffBase) - (LB * EFOOD/ EffENERGYSTAR)

Where:

HOURSday 		= Average Daily Operation

= custom or if unknown, use 12 hours

Days 			= Annual days of operation

= custom or if unknown, use 365.25 days a year

LB 			= Food cooked per day

= custom or if unknown, use 100 pounds

EffENERGYSTAR 		= Cooking Efficiency ENERGY STAR

= custom or if unknown, use 46%

EffBase 			= Cooking Efficiency Baseline

= custom or if unknown, use 30%

PCENERGYSTAR 		= Production Capacity ENERGY STAR

= custom or if unknown, use 80 pounds/hr

PCBase 			= Production Capacity base

= custom or if unknown, use 70 pounds/hr

PreheatNumberENERGYSTAR	= Number of preheats per day

= custom or if unknown, use 1

PreheatNumberBase 	= Number of preheats per day

= custom or if unknown, use 1

PreheatTimeENERGYSTAR 	= preheat length

= custom or if unknown, use 15 minutes

PreheatTimeBase 	= preheat length

= custom or if unknown, use 15 minutes

PreheatRateENERGYSTAR = preheat energy rate high efficiency

= custom or if unknown, use 44000 btu/h

PreheatRateBase 		= preheat energy rate baseline

= custom or if unknown, use 76000 btu/h

IdleENERGYSTAR 		= Idle energy rate

= custom or if unknown, use 12000 btu/h

IdleBase			= Idle energy rate

= custom or if unknown, use 18000 btu/h

IdleENERGYSTARTime 	= ENERGY STAR Idle Time

=HOURsday-LB/PCENERGYSTAR –PreHeatTimeENERGYSTAR/60

=12 – 100/80 – 15/60

=10.5 hours

IdleBaseTime		= BASE Idle Time

= HOURsday-LB/PCbase –PreHeatTimeBase/60

=Custom or if unknown, use

=12 – 100/70-15/60

=10.3 hours

EFOOD 			= ASTM energy to food

= 250 btu/pound

For example, an ENERGY STAR Oven with a cooking energy efficiency of 46% and default values from above would save.

ΔTherms = (ΔIdle Energy + ΔPreheat Energy + ΔCooking Energy) * Days /100000

Where:

ΔDailyIdleEnergy 		=(18000*10.3)- (12000*10.5)

= 59,400 btu

ΔDailyPreheatEnergy 	= (1 * 15 / 60 *76000) – (1 * 15 / 60 *44000)

= 8,000 btu

ΔDailyCookingEnergy 	= (100 * 250/ .30) - (100 * 250/ .46)

=28,986 btu

ΔTherms 		= (59,400 + 8,000 + 28,986) * 365.25 /100000

= 352 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-ESCV-V02-180101

###### Review Deadline: 1/1/2024

### ENERGY STAR Dishwasher

###### Description

This measure applies to ENERGY STAR high and low temp under counter, stationary single tank door type, single tank conveyor, and multiple tank conveyor dishwashers, as well as high temp pot, pan, and utensil dishwashers installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be an ENERGY STAR certified dishwasher meeting idle energy rate (kW), washing energy and water consumption (gallons/rack) limits, as determined by both machine type and sanitation approach (chemical/low temp versus high temp).

ENERGY STAR Requirements (Version 3.0, effective July 27, 2021)

| Dishwasher Type | High Temp Efficiency Requirements |  |  | Low Temp Efficiency Requirements |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Idle Energy Rate | Washing Energy | Water Consumption | Idle Energy Rate | Washing Energy | Water Consumption |
| Under Counter | ≤ 0.30 kW | ≤ 0.35 kWh/rack | ≤ 0.86 GPR | ≤ 0.25 kW | ≤ 0.15 kWh/rack | ≤ 1.19 GPR |
| Stationary Single Tank Door | ≤ 0.55 kW | ≤ 0.35 kWh/rack | ≤ 0.89 GPR | ≤ 0.30 kW | ≤ 0.15 kWh/rack | ≤ 1.18 GPR |
| Pot, Pan, and Utensil | ≤ 0.90 kW | ≤ 0.55 + 0.05 * SFrack | ≤ 0.58 GPSF | N/A |  |  |
| Single Tank Conveyor | ≤ 1.20 kW | ≤ 0.36 kWh/rack | ≤ 0.70 GPR | ≤ 0.85 kW | ≤ 0.16 kWh/rack | ≤ 0.79 GPR |
| Multiple Tank Conveyor | ≤ 1.85 kW | ≤ 0.36 kWh/rack | ≤ 0.54 GPR | ≤ 1.00 kW | ≤ 0.22 kWh/rack | ≤ 0.54 GPR |

###### Definition of Baseline Equipment

The baseline equipment is a new dishwasher that is not ENERGY STAR certified.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be:

| Dishwasher Type |  | Equipment Life |
| --- | --- | --- |
| Low Temp | Under Counter | 10 |
|  | Stationary Single Tank Door | 15 |
|  | Single Tank Conveyor | 20 |
|  | Multi Tank Conveyor | 20 |
| High Temp | Under Counter | 10 |
|  | Stationary Single Tank Door | 15 |
|  | Single Tank Conveyor | 20 |
|  | Multi Tank Conveyor | 20 |
|  | Pot, Pan, and Utensil | 10 |

###### Deemed Measure Cost

The incremental capital cost for this measure is provided below:

| Dishwasher Type |  | Incremental Cost |
| --- | --- | --- |
| Low Temp | Under Counter | $234 |
|  | Stationary Single Tank Door | $662 |
|  | Single Tank Conveyor | $0 |
|  | Multi Tank Conveyor | $970 |
| High Temp | Under Counter | $2,025 |
|  | Stationary Single Tank Door | $995 |
|  | Single Tank Conveyor | $2,050 |
|  | Multi Tank Conveyor | $970 |
|  | Pot, Pan, and Utensil | $1,710 |

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

Summer Peak Coincidence Factor for measure is provided below for different restaurant types:

| Location | CF CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |

Algorithm

###### Calculation of Savings

ENERGY STAR dishwashers save energy in three categories: building water heating, booster water heating and idle energy. Building water heating and booster water heating could be either electric or natural gas.

###### Electric Energy Savings

Custom calculation below, otherwise use deemed values found within the tables that follow.

∆kWh=∆BuildingEnergy+ ∆BoosterEnergy+ ∆IdleEnergy

Where:

ΔBuildingEnergy	= Change in annual electric energy consumption of building water heater

= [(WaterUseBase * RacksWashed * Days) * (∆Tin *1.0 * 8.2 ÷ EffHeater ÷ 3,412)] -  [(WaterUseESTAR * RacksWashed * Days) * (∆Tin *1.0 * 8.2 ÷ EffHeater ÷ 3,412)]

ΔBoosterEnergy	= Annual electric energy consumption of booster water heater

= [(WaterUseBase * RacksWashed * Days) * (∆Tin *1.0 * 8.2 ÷ EffHeater ÷ 3,412)] -  [(WaterUseESTAR * RacksWashed * Days) * (∆Tin *1.0 * 8.2 ÷ EffHeater ÷ 3,412)]

ΔIdleEnergy	= Annual idle electric energy consumption of dishwasher

= [IdleDrawBase* (Hours *Days – Days * RacksWashed * WashTime ÷ 60)] –

[IdleDrawESTAR* (Hours *Days – Days * RacksWashed * WashTime ÷ 60)]

Where:

WaterUseBase	= Water use per rack (gal) of baseline dishwasher

= Custom or if unknown, use value from table below as determined by machine type and sanitation method

WaterUseESTAR	= Water use per rack (gal) of ENERGY STAR dishwasher

= Custom or if unknown, use value from table below as determined by machine type and sanitation method

RacksWashed	= Number of racks washed per day

= Custom or if unknown, use value from table below as determined by machine type and sanitation method

Days		= Annual days of dishwasher operation

= Custom or if unknown, use 365.25 days per year

Tin		= Inlet water temperature increase (°F)

= Custom or if unknown, use 70 °F for building water heaters and 40 °F for booster water heaters

1.0		= Specific heat of water (Btu/lb/°F)

8.2 		= Density of water (lb/gal)

EffHeater		= Efficiency of water heater

= Custom or if unknown, use 98% for electric building and booster water heaters

3,412		= kWh to Btu conversion factor

IdleDrawBase	= Idle power draw (kW) of baseline dishwasher

= Custom or if unknown, use value from table below as determined by machine type and sanitation method

IdleDrawESTAR	= Idle power draw (kW) of ENERGY STAR dishwasher

= Custom or if unknown, use value from table below as determined by machine type and sanitation method

Hours		= Average daily hours of dishwasher operation

= Custom or if unknown, use 18 hours per day

WashTime	= Typical wash time (min)

= Custom or if unknown, use value from table below as determined by machine type and sanitation method

60		= Minutes to hours conversion factor

For example, an ENERGY STAR high-temperature, under counter dishwasher with electric building and electric booster water heating with defaults from the calculation above and the table below would save:

ΔkWh = ΔBuildingEnergy + ΔBoosterEnergy + ΔIdleEnergy

Where:

ΔBuildingEnergy	= [(1.09 * 75 * 365.25) * (70 *1.0 * 8.2 ÷ 0.98 ÷ 3,412)] -  [(0.86 * 75 * 365.25) * (70 *1.0 * 8.2 ÷ 0.98 ÷ 3,412)]

= 1,082 kWh

ΔBoosterEnergy	= [(1.09 * 75 * 365.25) * (40 *1.0 * 8.2 ÷ 0.98 ÷ 3,412)] -  [(0.86 * 75 * 365.25) * (40 *1.0 * 8.2 ÷ 0.98 ÷ 3,412)]

= 618 kWh

ΔIdleEnergy 		= [0.76 * (18 *365.25 – 365.25 * 75 * 2.0 ÷ 60)] –

[0.30 * (18 *365.25 – 365.25 * 75 * 2.0 ÷ 60)]

= 2,604 kWh

ΔkWh 		 	= 1,082 + 618 + 2,604

= 4,514 kWh

Default values for WaterUse, RacksWashed, kWIdle, and WashTime are presented in the table below.

|  | RacksWashed | WashTime | WaterUse |  | IdleDraw |  |
| --- | --- | --- | --- | --- | --- | --- |
| Low Temperature | All Dishwashers | All Dishwashers | Conventional | ENERGY STAR | Conventional | ENERGY STAR |
| Under Counter | 75 | 2.0 | 1.73 | 1.19 | 0.50 | 0.25 |
| Stationary Single Tank Door | 280 | 1.5 | 2.10 | 1.18 | 0.60 | 0.30 |
| Single Tank Conveyor | 400 | 0.3 | 1.31 | 0.79 | 1.60 | 0.85 |
| Multi Tank Conveyor | 600 | 0.3 | 1.04 | 0.54 | 2.00 | 1.00 |
| High Temperature | All Dishwashers | All Dishwashers | Conventional | ENERGY STAR | Conventional | ENERGY STAR |
| Under Counter | 75 | 2.0 | 1.09 | 0.86 | 0.76 | 0.30 |
| Stationary Single Tank Door | 280 | 1.0 | 1.29 | 0.89 | 0.87 | 0.55 |
| Single Tank Conveyor | 400 | 0.3 | 0.87 | 0.70 | 1.93 | 1.20 |
| Multi Tank Conveyor | 600 | 0.2 | 0.97 | 0.54 | 2.59 | 1.85 |
| Pot, Pan, and Utensil | 280 | 3.0 | 0.70 | 0.58 | 1.20 | 0.90 |

Savings for all water heating combinations are presented in the tables below (calculated without rounding variables as provided above).

Electric building and electric booster water heating

| Dishwasher type |  | kWhBase | kWhESTAR | ΔkWh |
| --- | --- | --- | --- | --- |
| Low Temp | Under Counter | 10,972 | 7,016 | 3,957 |
|  | Stationary Single Tank Door | 39,306 | 21,937 | 17,369 |
|  | Single Tank Conveyor | 42,230 | 24,795 | 17,434 |
|  | Multi Tank Conveyor | 50,112 | 25,809 | 24,303 |
| High Temp | Under Counter | 12,363 | 8,058 | 4,305 |
|  | Stationary Single Tank Door | 39,852 | 27,250 | 12,602 |
|  | Single Tank Conveyor | 45,593 | 34,621 | 10,971 |
|  | Multi Tank Conveyor | 72,523 | 42,759 | 29,764 |
|  | Pot, Pan, and Utensil | 21,079 | 17,328 | 3,751 |

Electric building and natural gas booster water heating

| Dishwasher type |  | kWhBase | kWhESTAR | ΔkWh |
| --- | --- | --- | --- | --- |
| Low Temp | Under Counter | 10,972 | 7,016 | 3,957 |
|  | Stationary Single Tank Door | 39,306 | 21,937 | 17,369 |
|  | Single Tank Conveyor | 42,230 | 24,795 | 17,434 |
|  | Multi Tank Conveyor | 50,112 | 25,809 | 24,303 |
| High Temp | Under Counter | 9,432 | 5,746 | 3,687 |
|  | Stationary Single Tank Door | 26,901 | 18,315 | 8,586 |
|  | Single Tank Conveyor | 33,115 | 24,582 | 8,533 |
|  | Multi Tank Conveyor | 51,655 | 31,141 | 20,513 |
|  | Pot, Pan, and Utensil | 14,052 | 11,505 | 2,547 |

Natural gas building and electric booster water heating

| Dishwasher type |  | kWhBase | kWhESTAR | ΔkWh |
| --- | --- | --- | --- | --- |
| Low Temp | Under Counter | 2,831 | 1,415 | 1,415 |
|  | Stationary Single Tank Door | 2,411 | 1,205 | 1,205 |
|  | Single Tank Conveyor | 9,350 | 4,967 | 4,383 |
|  | Multi Tank Conveyor | 10,958 | 5,479 | 5,479 |
| High Temp | Under Counter | 7,234 | 4,011 | 3,223 |
|  | Stationary Single Tank Door | 17,188 | 11,614 | 5,574 |
|  | Single Tank Conveyor | 23,757 | 17,052 | 6,704 |
|  | Multi Tank Conveyor | 36,004 | 22,429 | 13,575 |
|  | Pot, Pan, and Utensil | 8,781 | 7,138 | 1,643 |

Natural gas building and natural gas booster water heating

| Dishwasher type |  | kWhBase | kWhESTAR | ΔkWh |
| --- | --- | --- | --- | --- |
| Low Temp | Under Counter | 2,831 | 1,415 | 1,415 |
|  | Stationary Single Tank Door | 2,411 | 1,205 | 1,205 |
|  | Single Tank Conveyor | 9,350 | 4,967 | 4,383 |
|  | Multi Tank Conveyor | 10,958 | 5,479 | 5,479 |
| High Temp | Under Counter | 4,303 | 1,698 | 2,604 |
|  | Stationary Single Tank Door | 4,237 | 2,679 | 1,558 |
|  | Single Tank Conveyor | 11,279 | 7,013 | 4,266 |
|  | Multi Tank Conveyor | 15,136 | 10,811 | 4,325 |
|  | Pot, Pan, and Utensil | 1,753 | 1,315 | 438 |

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure, but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater total

Where

Ewater total		= IL Total Water Energy Factor (kWh/Million Gallons)

= 5,010

For example, an ENERGY STAR low-temperature, under-counter dishwasher with defaults from the calculation above and the table within the electric energy savings characterization would save:

∆Water = (WaterUseBase * RacksWashed * Days) - (WaterUseESTAR * RacksWashed * Days)

ΔWater (gallons)		= (1.73 * 75 * 365.25) - (1.19 * 75 * 365.25)

= 14,793 gallons

ΔkWhwater 		= 14,793/1,000,000*5,010

= 74 kWh

###### Summer Coincident Peak Demand Savings

ΔkW 	= ΔkWh/ AnnualHours * CF

Where:

ΔkWh 	= Annual kWh savings from measure as calculated above. Note: do not include the secondary savings in this calculation.

AnnualHours 	= Hours * Days

= Custom, or if unknown assume (18 * 365.25 =) 6575 annual hours

CF		= Summer Peak Coincidence Factor

= dependent on restaurant type:

| Location | CF CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |

For example, a low temperature undercounter dishwasher in a Full Service Limited Menu restaurant with electric building and booster water heaters would save:

ΔkW 	= ΔkWh/ AnnualHours * CF

= 3957/6575*0.51

= 0.307 kW

###### Natural Gas Energy Savings

∆Therms= ∆BuildingEnergy+ ∆BoosterEnergy

Where:

ΔBuildingEnergy	      = Change in annual natural gas consumption of building water heater

= [(WaterUseBase * RacksWashed * Days)*(∆Tin * 1.0 * 8.2 ÷ EffHeater  ÷ 100,000)] - [(WaterUseESTAR* RacksWashed * Days)*(∆Tin * 1.0*8.2 ÷ EffHeater  ÷ 100,000)]

ΔBoosterEnergy        = Change in annual natural gas consumption of booster water heater

= [(WaterUseBase * RacksWashed * Days)*(∆Tin * 1.0 * 8.2 ÷ EffHeater  ÷ 100,000)] - [(WaterUseESTAR* RacksWashed * Days)*(∆Tin * 1.0*8.2 ÷ EffHeater  ÷ 100,000)]

Where:

WaterUseBase	= Water use per rack (gal) of baseline dishwasher

= Custom or if unknown, use value from table within the electric energy savings characterization as determined by machine type and sanitation method

WaterUseESTAR	= Water use per rack (gal) of ENERGY STAR dishwasher

= Custom or if unknown, use value from table within the electric energy savings characterization as determined by machine type and sanitation method

RacksWashed	= Number of racks washed per day

= Custom or if unknown, use value from table within the electric energy savings characterization as determined by machine type and sanitation method

Days		= Annual days of dishwasher operation

= Custom or if unknown, use 365 days per year

Tin		= Inlet water temperature increase (°F)

= Custom or if unknown, use 70 °F for building water heaters and 40 °F for booster water heaters

1.0		= Specific heat of water (Btu/lb/°F)

8.2 		= Density of water (lb/gal)

EffHeater		= Efficiency of water heater

= Custom or 80% for gas building and booster water heaters

100,000		= Therms to Btu conversion factor

For example, an ENERGY STAR high-temperature, under counter dishwasher with gas building and gas booster water heating with defaults from the calculation above and the table within the electric energy savings characterization would save:

ΔTherms = ΔBuildingEnergy + ΔBoosterEnergy

Where:

ΔBuildingEnergy	= [(1.09 * 75 * 365.25)*(70 * 1.0 * 8.2 ÷ 0.80  ÷ 100,000)] - [(0.86 * 75 * 365.25)*(70 * 1.0 * 8.2 ÷ 0.80  ÷ 100,000)]

= 45 therms

ΔBoosterEnergy	= [(1.09 * 75 * 365.25)*(40 * 1.0 * 8.2 ÷ 0.80  ÷ 100,000)] - [(0.86 * 75 * 365.25)*(40 * 1.0 * 8.2 ÷ 0.80  ÷ 100,000)]

= 26 therms

ΔTherms		 = 45 + 26

= 71 therms

Savings for all water heating combinations are presented in the tables below.

Electric building and natural gas booster water heating

| Dishwasher type |  | ThermsBase | ThermsESTAR | ΔTherms |
| --- | --- | --- | --- | --- |
| Low Temp | Under Counter | NA | NA | NA |
|  | Stationary Single Tank Door | NA | NA | NA |
|  | Single Tank Conveyor | NA | NA | NA |
|  | Multi Tank Conveyor | NA | NA | NA |
| High Temp | Under Counter | 123 | 97 | 26 |
|  | Stationary Single Tank Door | 541 | 374 | 168 |
|  | Single Tank Conveyor | 522 | 420 | 102 |
|  | Stationary Single Tank Door | 872 | 486 | 387 |
|  | Pot, Pan, and Utensil | 294 | 243 | 50 |

Natural gas building and natural gas booster water heating

| Dishwasher type |  | ThermsBase | ThermsESTAR | ΔTherms |
| --- | --- | --- | --- | --- |
| Low Temp | Under Counter | 340 | 234 | 106 |
|  | Stationary Single Tank Door | 1,543 | 867 | 676 |
|  | Single Tank Conveyor | 1,375 | 829 | 546 |
|  | Multi Tank Conveyor | 1,637 | 850 | 787 |
| High Temp | Under Counter | 337 | 266 | 71 |
|  | Stationary Single Tank Door | 1,489 | 1,027 | 462 |
|  | Single Tank Conveyor | 1,435 | 1,154 | 280 |
|  | Multi Tank Conveyor | 2,399 | 1,336 | 1,064 |
|  | Pot, Pan, and Utensil | 808 | 669 | 139 |

Natural gas building and electric booster water heating

| Dishwasher type |  | ThermsBase | ThermsESTAR | ΔTherms |
| --- | --- | --- | --- | --- |
| Low Temp | Under Counter | 340 | 234 | 106 |
|  | Stationary Single Tank Door | 1,543 | 867 | 676 |
|  | Single Tank Conveyor | 1,375 | 829 | 546 |
|  | Multi Tank Conveyor | 1,637 | 850 | 787 |
| High Temp | Under Counter | 214 | 169 | 45 |
|  | Stationary Single Tank Door | 948 | 654 | 294 |
|  | Single Tank Conveyor | 913 | 735 | 178 |
|  | Multi Tank Conveyor | 1,527 | 850 | 677 |
|  | Pot, Pan, and Utensil | 514 | 426 | 88 |

###### Water Impact Descriptions and Calculation

∆Water=(WaterUseBase*RacksWashed*Days)- (WaterUseESTAR*RacksWashed*                                      Days)

Where:

WaterUseBase	= Water use per rack (gal) of baseline dishwasher

= Custom or if unknown, use value from table within the electric energy savings characterization as determined by machine type and sanitation method

WaterUseESTAR	= Water use per rack (gal) of ENERGY STAR dishwasher

= Custom or if unknown, use value from table within the electric energy savings characterization as determined by machine type and sanitation method

RacksWashed	= Number of racks washed per day

= Custom or if unknown, use value from table within the electric energy savings characterization as determined by machine type and sanitation method

Days		= Annual days of dishwasher operation

= Custom or if unknown, use 365 days per year

For example, an ENERGY STAR low-temperature, under counter dishwasher with defaults from the calculation above and the table within the electric energy savings characterization would save:

∆Water = (WaterUseBase * RacksWashed * Days) - (WaterUseESTAR * RacksWashed * Days)

ΔWater (gallons)		 = (1.73 * 75 * 365.25) - (1.19 * 75 * 365.25)

= 14,793 gallons

Savings for all dishwasher types are presented in the table below.

|  | Annual Water Consumption (gallons) |  |  |
| --- | --- | --- | --- |
|  | Baseline | ENERGY STAR | Savings |
| Low Temperature |  |  |  |
| Under Counter | 47,391 | 32,599 | 14,793 |
| Stationary Single Tank Door | 214,767 | 120,679 | 94,088 |
| Single Tank Conveyor | 191,391 | 115,419 | 75,972 |
| Multi Tank Conveyor | 227,916 | 118,341 | 109,575 |
| High Temperature |  |  |  |
| Under Counter | 29,859 | 23,559 | 6,301 |
| Stationary Single Tank Door | 131,928 | 91,020 | 40,908 |
| Single Tank Conveyor | 127,107 | 102,270 | 24,837 |
| Multi Tank Conveyor | 212,576 | 118,341 | 94,235 |
| Pot, Pan, and Utensil | 71,589 | 59,317 | 12,272 |

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-ESDW-V06-220101

###### Review Deadline: 1/1/2026

### ENERGY STAR Fryer

###### Description

This measure applies to electric or natural gas fired ENERGY STAR certified fryers installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure, the installed equipment must be an ENERGY STAR certified fryer meeting idle energy rate (W or Btu/hr)) and cooking efficiency (%) limits, as determined by both fuel type and fryer capacity (standard versus large vat).

ENERGY STAR Requirements (Version 3.0, Effective October 1, 2016)

| Fryer Capacity | Electric Efficiency Requirements |  | Natural Gas Efficiency Requirements |  |
| --- | --- | --- | --- | --- |
|  | Idle Energy Rate | Cooking Efficiency Consumption | Idle Energy Rate | Cooking Efficiency Consumption |
| Standard Open Deep-Fat Fryer | ≤ 800 W | ≥ 83% | ≤ 9,000 Btu/hr | ≥ 50% |
| Large Vat Open Deep-Fat Fryer | ≤ 1,100 W | ≥ 80% | ≤ 12,000 Btu/hr |  |

###### Definition of Baseline Equipment

The baseline equipment is a new electric or natural gas fryer that is not ENERGY STAR certified.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

For the incremental capital costs, please see the table below:

| Fuel Source | Size | Incremental Cost |
| --- | --- | --- |
| Electric | Standard | $1,500 |
|  | Large Vat | $500 |
| Natural Gas | Standard | $1,000 |
|  | Large Vat | $2,000 |

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

Summer Peak Coincidence Factor for measure is provided below for different building type:

| Location | CF CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Custom calculation for an electric fryer below; otherwise use deemed value of 3,274.2 kWh for standard fryers and 2,697.6 kWh for large vat fryers.

ΔkWh 			= (ΔDailyIdleEnergy + ΔDailyPreheatEnergy + ΔDailyCookingEnergy) * Days /1,000

Where:

ΔDailyIdleEnergy 	= (ElecIdleBase* ((HOURS – (PreheatTime/60)) – LB/ElecPCBase)) – (ElecIdleESTAR * ((HOURS – (PreheatTime/60)) – LB/ElecPCESTAR))

ΔDailyPreheatEnergy	= (ElecPreheatBase – ElecPreheatESTAR) * 1,000

ΔDailyCookingEnergy 	= (LB * EFOODElec/ ElecEffBase) – (LB * EFOODElec/ElecEffESTAR)

Where:

ΔDailyIdleEnergy		= Difference in idle energy between baseline and efficient fryer

ΔDailyCookingEnergy	= Difference in cooking energy between baseline and efficient fryer

Days 			= Annual days of operation

= Custom, or if unknown, use 365.25 days per year

1,000			= Wh to kWh conversion factor

ElecIdleBase		= Idle energy rate of baseline electric fryer

= 1,200 W for standard fryers and 1,350 W for large vat fryers

ElecIdleESTAR		= Idle energy rate of ENERGY STAR electric fryer

= Custom or if unknown, use 800 W for standard fryers and 1,100 for large vat fryers

HOURS			= Average daily hours of operation

= Custom or if unknown, use 16 hours per day for a standard fryer and 12 hours per day for a large vat fryer

PreheatTime		= Time required to preheat the fryer

= 15 minutes per day

60			= minutes to hours conversion factor

LB 			= Food cooked per day

= Custom or if unknown, use 150 pounds

ElecPCBase 		= Production capacity of baseline electric fryer

= 65 lb/hr for standard fryers and 100 lb/hr for large vat fryers

ElecPCESTAR 		= Production capacity of ENERGY STAR electric fryer

= Custom or if unknown, use 70 lb/hr for standard fryers and 110 lb/hr for	 large vat fryers

ElecPreheatBase		= Preheat energy rate of baseline electric fryer

= 2.4 kWh

ElecPreheatESTAR		= Preheat energy rate of ENERGY STAR electric fryer

= 1.9 kWh

EFOODElec		= ASTM energy to food for electric fryers

= 167 Wh/lb

ElecEffBase		= Cooking efficiency of baseline electric fryer

= 75% for standard fryers and 70% for large vat fryers

ElecEffESTAR		= Cooking efficiency of ENERGY STAR electric fryer

= Custom or if unknown, use 83% for standard fryers and 80% for large vat fryers

For example, an ENERGY STAR standard-sized electric fryer, using default values from the calculation above, would save:

ΔkWh	 = (ΔDailyIdleEnergy + ΔDailyPreheatEnergy + ΔDailyCookingEnergy) * Days /1,000

Where:

ΔDailyIdleEnergy 		= (1,200 * ((16 – 15/60) – 150 / 65)) - (800 * ((16 – 15/60) – 150 / 70))

= 5,245 Wh

ΔDailyPreheatEnergy	= (2.4 - 1.9) * 1,000

= 500 Wh

ΔDailyCookingEnergy 	= (150 * 167/ 0.75) - (150 * 167/ 0.83)

= 3,219 Wh

ΔkWh 		 	= (5,245 + 500 + 3,219) * 365.25 / 1,000

= 3,274.2 kWh

###### Summer Coincident Peak Demand Savings

ΔkW 		= ΔkWh/(HOURS * Days) * CF

Where:

ΔkWh 	= Electric energy savings, calculated above

Other variables as defined above.

For example, an ENERGY STAR standard-sized electric fryer in a cafeteria, using default values from the calculation above, would save:

ΔkW 	= ΔkWh/(HOURS * Days) * CF

= 3,274.2 / (16 * 365.25) * 0.36

= 0.2017 kW

###### Natural Gas Energy Savings

Custom calculation for a gas fryer below, otherwise use deemed value of 512.5 therms for standard fryers and  420.6 therms for large vat fryers.

ΔTherms 	= (ΔDailyIdle Energy + ΔDailyPreheatEnergy +ΔDailyCooking Energy) * Days /100,000

Where:

ΔDailyIdleEnergy 	= (GasIdleBase* ((HOURS – (PreheatTime/60)) – LB/GasPCBase)) – (GasIdleESTAR * ((HOURS – (PreheatTime/60)) – LB/GasPCESTAR))

ΔDailyPreheatEnergy	= GasPreheatBase – GasPreheatESTAR

ΔDailyCookingEnergy 	= (LB * EFOODGas/ GasEffBase) – (LB * EFOODGas/GasEffESTAR)

Where:

100,000		= Btu to therms conversion factor

GasIdleBase	= Idle energy rate of baseline gas fryer

= 14,000 Btu/hr for standard fryers and 16,000 Btu/hr for large vat fryers

GasIdleESTAR	= Idle energy rate of ENERGY STAR gas fryer

= Custom or if unknown, use 9,000 Btu/hr for standard fryers and 12,000 Btu/hr for large vat fryers

GasPCBase 	= Production capacity of baseline gas fryer

= 60 lb/hr for standard fryers and 100 lb/hr for large vat fryers

GasPCESTAR 	= Production capacity of ENERGY STAR gas fryer

= Custom or if unknown, use 65 lb/hr for standard fryers and 110 lb/hr for large vat fryers

GasPreheatBase	= Preheat energy rate of baseline gas fryer

= 18,500 Btu

GasPreheatESTAR	= Preheat energy rate of ENERGY STAR gas fryer

= 16,000 Btu

EFOODGas 	= ASTM energy to food

= 570 Btu/lb

GasEffBase	= Cooking efficiency of baseline gas fryer

= 35% for both standard and large vat fryers

GasEffESTAR	= Cooking efficiency of ENERGY STAR gas fryer

= Custom or if unknown, use 50% for both standard and large vat fryers

Other variables as defined above.

For example, an ENERGY STAR standard-sized electric fryer, using default values from the calculation above, would save:

ΔTherms	 	= (ΔDailyIdleEnergy + ΔDailyPreheatEnergy + ΔDailyCookingEnergy) * Days /100,000

Where:

ΔDailyIdleEnergy 		= (14,000 * ((16 – 15/60) – 150 / 60)) - (9,000 * ((16  – 15/60) – 150 / 65))

= 64,519 Btu/day

ΔDailyPreheatEnergy	= 18,500 – 16,000

= 2,500 Btu/day

ΔDailyCookingEnergy 	= (150 * 570/ 0.35) - (150 * 570/ 0.50)

=73,286 Btu/day

ΔTherms	 	= (64,519 + 2,500 + 73,286) * 365.25 / 100,000

= 512.5 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-ESFR-V03-220101

###### Review Deadline: 1/1/2026

### ENERGY STAR Griddle

###### Description

This measure applies to single or double-sided electric, natural gas fired, or dual fuel ENERGY STAR griddles installed in a commercial kitchen.  For dual fuel griddles, savings should be divided between electric and gas as described in the Natural Gas Energy Savings section of this measure.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a single or double-sided natural gas, electric, or dual fuel ENERGY STAR griddle with a tested heavy load cooking energy efficiency of 70 percent (electric) 38 percent (gas) or greater and an idle energy rate of 2,650 Btu/hr per square foot of cooking surface or less, utilizing ASTM F1275. The griddle must have an Idle Energy Consumption Rate < 2,600 Btu/hr per square foot of cooking surface.

###### Definition of Baseline Equipment

The baseline equipment is an existing natural gas or electric griddle that’s not ENERGY STAR certified and is at end of use.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $0 for and electric griddle and $60 for a gas griddle.

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

Summer Peak Coincidence Factor for measure is provided below for different building type:

| Location | CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Custom calculation for single or double-sided electric griddles below, otherwise use deemed value of 2,597 kWh.

ΔkWh = (ΔIdle Energy + ΔPreheat Energy + ΔCooking Energy) * Days /1000

Where:

ΔDailyIdleEnergy 	=[(IdleBase * Width * Depth * (HOURSday – (LB/(PCBase * Width * Depth)) – (PreheatNumberBase* PreheatTimeBase/60)]- [(IdleENERGYSTAR * Width * Depth * (HOURSday – (LB/(PCENERGYSTAR * Width * Depth)) – (PreheatNumberENERGYSTAR* PreheatTimeENERGYSTAR/60]

ΔDailyPreheatEnergy 	= (PreHeatNumberBase * PreheatTimeBase / 60 * PreheatRateBase * Width * Depth) – (PreheatNumberENERGYSTAR* PreheatTimeENERGYSTAR/60 * PreheatRateENERGYSTAR * Width * Depth)

ΔDailyCookingEnergy 	= (LB * EFOOD/ EffBase) - (LB * EFOOD/ EffENERGYSTAR)

Where:

HOURSday 		= Average Daily Operation

= custom or if unknown, use 12 hours

Days 			= Annual days of operation

= custom or if unknown, use 365.25 days a year

LB 			= Food cooked per day

= custom or if unknown, use 100 pounds

Width			 = Griddle Width

= custom or if unknown, use 3 feet

Depth			= Griddle Depth

= custom or if unknown, use 2 feet

EffENERGYSTAR 		= Cooking Efficiency ENERGY STAR

= custom or if unknown, use 70%

EffBase 			= Cooking Efficiency Baseline

= custom or if unknown, use 65%

PCENERGYSTAR	 	= Production Capacity ENERGY STAR

= custom or if unknown, use 40/6 = 6.67 pounds/hr/sq ft

PCBase 			= Production Capacity base

= custom or if unknown, use 35/6 = 5.83 pounds/hr/sq ft

PreheatNumberENERGYSTAR	= Number of preheats per day

= custom or if unknown, use 1

PreheatNumberBase 	= Number of preheats per day

= custom or if unknown, use 1

PreheatTimeENERGYSTAR 	= preheat length

= custom or if unknown, use 15 minutes

PreheatTimeBase 	= preheat length

= custom or if unknown, use 15 minutes

PreheatRateENERGYSTAR = preheat energy rate high efficiency

= custom or if unknown, use 8000/6 = 1333 W/sq ft

PreheatRateBase		 = preheat energy rate baseline

= custom or if unknown, use 16000/6 = 2667 W/sq ft

IdleENERGYSTAR 		= Idle energy rate

= custom or if unknown, use 320 W/sq ft

IdleBase			 = Idle energy rate

= custom or if unknown, use 400 W/sq ft

EFOOD 			= ASTM energy to food

= 139 w/pound

For example, an ENERGY STAR griddle with a tested heavy load cooking energy efficiency of 70 percent or greater and an idle energy rate of 320 W per square foot of cooking surface or less would save.

ΔDailyIdleEnergy 	=[400 * 3 * 2 * (12 – (100/(35/6 * 3 * 2)) – (1 *15/60)]- [320 * 3 * 2 * (12 – (100/(40/6 * 3 * 2)) – (1* 15/60]

= 3583 W

ΔDailyPreheatEnergy 	= (1* 15 / 60 * 16000/6 * 3 * 2) – (1* 15/60 * 8000/6 * 3 * 2)

= 2000W

ΔDailyCookingEnergy 	= (100 * 139 / 0.65) - (100 * 139 / 0.70)

= 1527 W

ΔkWh 			= (2000+1527+3583) * 365.25 /1000

= 2597 kWh

###### Summer Coincident Peak Demand Savings

kW 		= ΔkWh/Hours * CF

For example, an ENERGY STAR griddle in a cafeteria with a tested heavy load cooking energy efficiency of 70 percent or greater and an idle energy rate of 320 W per square foot of cooking surface or less would save

=2597 kWh/4308 * 0.39

= 0.24 kW

###### Natural Gas Energy Savings

Custom calculation for single or double-sided gas griddles or dual fuel griddles below, otherwise use deemed value of 149 therms.

ΔTherms 	= (ΔIdle Energy + ΔPreheat Energy + ΔCooking Energy) * Days /100000

Where:

ΔDailyIdleEnergy 	=[(IdleBase * Width * Depth * (HOURSday - LB/(PCBase * Width * Depth)) – (PreheatNumberBase* PreheatTimeBase/60)]- [(IdleENERGYSTAR * Width * Depth * (HOURSday – (LB/(PCENERGYSTAR * Width * Depth)) – (PreheatNumberENERGYSTAR* PreheatTimeENERGYSTAR/60]

ΔDailyPreheatEnergy 	= (PreHeatNumberBase * PreheatTimeBase / 60 * PreheatRateBase * Width * Depth) – (PreheatNumberENERGYSTAR* PreheatTimeENERGYSTAR/60 * PreheatRateENERGYSTAR * Width * Depth)

ΔDailyCookingEnergy 	= (LB * EFOOD/ EffBase) - (LB * EFOOD/ EffENERGYSTAR)

Where (new variables only):

EffENERGYSTAR 		= Cooking Efficiency ENERGY STAR

= custom or if unknown, use 38%

EffBase 			= Cooking Efficiency Baseline

= custom or if unknown, use 32%

PCENERGYSTAR	 	= Production Capacity ENERGY STAR

= custom or if unknown, use 45/6 = 7.5 pounds/hr/sq ft

PCBase 			= Production Capacity base

= custom or if unknown, use 25/6 = 4.17 pounds/hr/sq ft

PreheatRateENERGYSTAR = preheat energy rate high efficiency

= custom or if unknown, use 60000/6 = 10000 btu/h/sq ft

PreheatRateBase		 = preheat energy rate baseline

= custom or if unknown, use 84000/6 = 14000 btu/h/sq ft

IdleENERGYSTAR 		= Idle energy rate

= custom or if unknown, use 15900/6 = 2650 btu/h/sq ft

IdleBase			 = Idle energy rate

= custom or if unknown, use 21000/6 = 3500 btu/h/sq ft

EFOOD 			= ASTM energy to food

= 475 btu/pound

For dual fuel griddles, assume that half of the therms savings calculated according to the algorithm above are gas savings and half are electric savings.  Electric savings for dual griddles should be calculated as ∆kWh = (∆Therms * 0.50) * 29.3.

For example, an ENERGY STAR griddle with a tested heavy load cooking energy efficiency of 38 percent or greater and an idle energy rate of 2,650 Btu/h per square foot of cooking surface or less and  an Idle Energy Consumption Rate < 2,600 Btu/h per square foot of cooking surface would save.

ΔDailyIdleEnergy 	=[3500 * 3 * 2 * (12 - 100/(25/6* 3 * 2)) – (1* 15/60))]- [(2650 * 3 * 2 * (12 -  (100/(45/6 * 3 * 2)) – (1* 15/60)))]

= 11258 Btu

ΔDailyPreheatEnergy 	= (1 * 15 / 60 * 14,000 * 3 * 2) – (1* 15/60 * 10000 * 3 * 2)

= 6000 btu

ΔDailyCookingEnergy 	= (100 * 475/ 0.32) -  (100 * 475/ 0.38)

=23438 btu

ΔTherms 		= (11258 + 6000 + 23438) * 365.25 /100000

=149 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-ESGR-V04-200101

###### Review Deadline: 1/1/2023

### ENERGY STAR Hot Food Holding Cabinets

###### Description

This measure applies to electric ENERGY STAR hot food holding cabinets (HFHC) installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be an ENERGY STAR certified HFHC.

###### Definition of Baseline Equipment

The baseline equipment is an electric HFHC that’s not ENERGY STAR certified and at end of life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is:

| HFHC Size | Incremental Cost |
| --- | --- |
| Full Size (20 cubic feet) | $1200 |
| ¾ Size (12 cubic feet) | $1800 |
| ½ Size (8 cubic feet) | $1500 |

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

Summer Peak Coincidence Factor for measure is provided below for different building type:

| Location | CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Custom calculation below, otherwise use deemed values depending on HFHC size:

| Cabinet Size | Savings (kWh) |
| --- | --- |
| Full Size HFHC | 9308 |
| ¾ Size HFHC | 3942 |
| ½ Size HFHC | 2628 |

ΔkWh = HFHCBaselinekWh – HFHCENERGYSTARkWh

Where:

HFHCBaselinekWh = PowerBaseline* HOURSday * Days/1000

PowerBaseline	= Custom, otherwise

| Cabinet Size | Power (W) |
| --- | --- |
| Full Size HFHC | 2500 |
| ¾ Size HFHC | 1200 |
| ½ Size HFHC | 800 |

HOURSday 		= Average Daily Operation

= custom or if unknown, use 15 hours

Days 			= Annual days of operation

= custom or if unknown, use 365.25 days a year

HFHCENERGYSTARkWh 	= PowerENERGYSTAR* HOURSday * Days/1000

PowerENERGYSTAR	= Custom, otherwise

| Cabinet Size | Power (W) |
| --- | --- |
| Full Size HFHC | 800 |
| ¾ Size HFHC | 480 |
| ½ Size HFHC | 320 |

HOURSday 		= Average Daily Operation

= custom or if unknown, use 15 hours

Days 			= Annual days of operation

= custom or if unknown, use 365.25 days a year

For example, if a full size HFHC is installed the measure would save:

ΔkWh 	= (PowerBaseline* HOURSday * Days)/1000 – (PowerENERGYSTAR* HOURSday * Days)/1000

= (2500*15*365.25)/1000 – (800*15*365.25)/1000

= 9,314 kWh

###### Summer Coincident Peak Demand Savings

ΔkW 		= ΔkWh/Hours * CF

Where:  Hours = Hoursday *Days

For example, if a full size HFHC is installed in a cafeteria the measure would save:

= 9,314 kWh / (15*365.25)* .39

=0 .66 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-ESHH-V03-190101

###### Review Deadline: 1/1/2023

### Ice Maker

###### Description

This measure relates to the installation of a new ENERGY STAR qualified commercial ice machine. The ENERGY STAR label applied to air-cooled, cube-type machines including ice-making head, self-contained, and remote-condensing units. This measure could relate to the replacing of an existing unit at the end of its useful life, or the installation of a new system in a new or existing building.

This measure was developed to be applicable to the following program types: TOS and NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be a new commercial ice machine meeting the minimum ENERGY STAR efficiency level standards.

ENERGY STAR Requirements (Version 3.0, Effective January 28, 2018)

| ENERGY STAR Requirements for Air-Cooled Batch-Type Ice Makers |  |  |  |  |
| --- | --- | --- | --- | --- |
| Equipment Type | Applicable Ice Harvest Rate Range (lbs of ice/24 hrs) | ENERGY STAR Energy Consumption Rate (kWh/100 lbs ice) |  | Potable Water Use (gal/100 lbs ice) |
| IMH | H < 300 | ≤ 9.20 - 0.01134H |  | ≤ 20.0 |
|  | 300 ≤ H < 800 | ≤ 6.49 - 0.0023H |  |  |
|  | 800 ≤ H < 1500 | ≤ 5.11 - 0.00058H |  |  |
|  | 1500 ≤ H ≤ 4000 | ≤ 4.24 |  |  |
| RCU | H < 988 | ≤ 7.17 – 0.00308H |  | ≤ 20.0 |
|  | 988 ≤ H ≤ 4000 | ≤ 4.13 |  |  |
| SCU | H < 110 | ≤ 12.57 - 0.0399H |  | ≤ 25.0 |
|  | 110 ≤ H < 200 | ≤ 10.56 - 0.0215H |  |  |
|  | 200 ≤ H ≤ 4000 | ≤ 6.25 |  |  |
| ENERGY STAR Requirements for Air-Cooled Continuous-Type Ice Makers |  |  |  |  |
| Equipment Type | Applicable Ice Harvest Rate Range (lbs of ice/24 hrs) |  | ENERGY STAR Energy Consumption Rate (kWh/100 lbs ice) | Potable Water Use (gal/100 lbs ice) |
| IMH | H < 310 |  | ≤ 7.90 – 0.005409H | ≤ 15.0 |
|  | 310 ≤ H < 820 |  | ≤ 7.08 – 0.002752H |  |
|  | 820 ≤ H ≤ 4000 |  | ≤ 4.82 |  |
| RCU | H < 800 |  | ≤ 7.76 – 0.00464H | ≤ 15.0 |
|  | 800 ≤ H ≤ 4000 |  | ≤ 4.05 |  |
| SCU | H < 200 |  | ≤ 12.37 – 0.0261H | ≤ 15.0 |
|  | 200 ≤ H < 700 |  | ≤ 8.24 – 0.005429H |  |
|  | 700 ≤ H ≤ 4000 |  | ≤ 4.44 |  |

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to be a commercial ice machine meeting federal equipment standards established January 28, 2018.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 9 years.

###### Deemed Measure Cost

When available, the actual cost of the measure installation and equipment shall be used. The incremental capital cost for this measure is $0 for Batch-Type and Continuous-Type.

###### Loadshape

Loadshape C23 - Commercial Refrigeration

###### Coincidence Factor

The Summer Peak Coincidence Factor is assumed to equal 0.937.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWH	= [(kWhbase – kWhee) / 100] * (DC * H) * 365.25

Where:

kWhbase	 = maximum kWh consumption per 100 pounds of ice for the baseline equipment

= calculated as shown in the table below using the actual Harvest Rate (H) of the efficient equipment.

kWhee 	= maximum kWh consumption per 100 pounds of ice for the efficient equipment

= calculated as shown in the table below using the actual Harvest Rate (H) of the efficient equipment.

| Energy Consumption of Air-Cooled Batch-Type Ice Makers |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Ice Maker Type | Applicable Ice Harvest Rate Range (lbs of ice/24 hrs) |  | kWhBase |  | kWhESTAR |
| IMH | H < 300 | 10-0.01233H |  | ≤ 9.20 - 0.01134H |  |
|  | 300 ≤ H < 800 | 7.05-0.0025H |  | ≤ 6.49 - 0.0023H |  |
|  | 800 ≤ H < 1500 | 5.55-0.00063H |  | ≤ 5.11 - 0.00058H |  |
|  | 1500 ≤ H ≤ 4000 | 4.61 |  | ≤ 4.24 |  |
| RCU | H < 988 | 7.97-0.00342H |  | ≤ 7.17 – 0.00308H |  |
|  | 988 ≤ H ≤ 4000 | 4.59 |  | ≤ 4.13 |  |
| SCU | H < 110 | 14.79-0.0469H |  | ≤ 12.57 - 0.0399H |  |
|  | 110 ≤ H < 200 | 12.42-0.02533H |  | ≤ 10.56 - 0.0215H |  |
|  | 200 ≤ H ≤ 4000 | 7.35 |  | ≤ 6.25 |  |
| Energy Consumption of Air-Cooled Continuous-Type Ice Makers |  |  |  |  |  |
| Equipment Type | Applicable Ice Harvest Rate Range (lbs of ice/24 hrs) |  | kWhBase |  | kWhESTAR |
| IMH | H < 310 | 9.19-0.00629H |  | ≤ 7.90 – 0.005409H |  |
|  | 310 ≤ H < 820 | 8.23-0.0032H |  | ≤ 7.08 – 0.002752H |  |
|  | 820 ≤ H ≤ 4000 | 5.61 |  | ≤ 4.82 |  |
| RCU | H < 800 | 9.7-0.0058H |  | ≤ 7.76 – 0.00464H |  |
|  | 800 ≤ H ≤ 4000 | 5.06 |  | ≤ 4.05 |  |
| SCU | H < 200 | 14.22-0.03H |  | ≤ 12.37 – 0.0261H |  |
|  | 200 ≤ H < 700 | 9.47-0.00624H |  | ≤ 8.24 – 0.005429H |  |
|  | 700 ≤ H ≤ 4000 | 5.1 |  | ≤ 4.44 |  |

100 	= conversion factor to convert kWhbase and kWhee into maximum kWh consumption per pound of ice.

DC	= Duty Cycle of the ice machine

= 0.57

H	= Harvest Rate (pounds of ice made per day)

= Actual installed

365.35	= days per year

For example, a batch ice machine with an ice making head producing 450 pounds of ice would save

ΔkWH	= [(5.9 – 5.5) / 100] * (0.57 * 450) * 365.25

= 440 kWh

###### Summer Coincident Peak Demand Savings

ΔkW 	= ΔkWh / (HOURS * DC) * CF

Where:

HOURS	= annual operating hours

= 8766

CF 	= 0.937

For example, an ice machine with an ice making head producing 450 pounds of ice would save

ΔkW 	= 440/(8766 * 0.57) * .937

= 0.083 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

While the ENERGY STAR labeling criteria require that certified commercial ice machines meet certain “maximum potable water use per 100 pounds of ice made” requirements, such requirements are intended to prevent equipment manufacturers from gaining energy efficiency at the cost of water consumptions. A review of the AHRI Certification Directory indicates that approximately 81% of air-cooled, cube-type machines meet the ENERGY STAR potable water use requirement. Therefore, there are no assumed water impacts for this measure.

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-ESIM-V05-220101

###### Review Deadline: 1/1/2023

### High Efficiency Pre-Rinse Spray Valve

###### Description

Pre-rinse spray valves use a spray of water to remove food waste from dishes prior to cleaning in a dishwasher.  More efficient spray valves use less water thereby reducing water consumption, water heating cost, and waste water (sewer) charges. Pre-rinse spray valves include a nozzle, squeeze lever, and dish guard bumper.  Pre-rinse spray valves are manually operated, and the frequency of use depends on the volume of dirty dishes washed at a facility.  The primary impacts of this measure are water savings.  Reduced hot water consumption saves either natural gas or electricity, depending on the type of energy the hot water heater uses.

This measure was developed to be applicable to the following program types: TOS, EREP, KITS and DI.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure, the new or replacement pre-rinse spray nozzle must have a maximum flow rate that meets program requirements.

###### Definition of Baseline Equipment

The baseline equipment flow rate depends on program type. For TOS, the baseline equipment is a new pre-rinse spray valve with a maximum flow rate of 1.23 gpm or less.  For EREP and DI, the baseline equipment is an existing pre-rinse spray valve with an assumed flow rate of 2.14 gpm or less.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 5 years.

###### Deemed Measure Cost

When available, the actual cost of the measure (including labor where applicable) should be used. If unknown, the incremental cost of this measure for TOS programs is assumed to be $0.  For EREP, KITS and DI programs, the total installed cost is assumed to be $54.

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings (note water savings must first be calculated)

ΔkWH = ΔWater (gallons) * 8.33 * 1 * (Tout - Tin) * (1/EFF_Elec) /3,412 * FLAG

Where:

ΔWater (gallons)		= amount of water saved as calculated below

8.33		= specific mass in pounds of one gallon of water (lbm/gal)

1		= Specific heat of water: 1 Btu/lbm/°F

Tout		= Water Heater Outlet Water Temperature

= custom, otherwise assume Tin + 70°F temperature rise from Tin

Tin		= Inlet Water Temperature

= custom, otherwise assume 50.7°F

EFF_Elec  		= Efficiency of electric water heater supplying hot water to pre-rinse spray valve

=custom, otherwise assume 98%

Flag 		= 1 if electric or 0 if gas

Time of Sale: For example, a new spray nozzle with 0.98 gal/min flow replacing a nozzle with 1.23 gal/min flow at a large institutional establishments with a cafeteria with 70 degree temperature rise of water used by the pre-rinse spray valve that is heated by electric hot water saves annually :

ΔkWH 	= 14,040 * 8.33 * 1 * ((70+50.7) – 50.7) * (1/.98) /3,412 * 1

= 2,448kWh

Retrofit:  For example, a new spray nozzle with 0.98 gal/min flow replacing a nozzle with 2.14 gal/min flow at a large institutional establishments with a cafeteria with 70 degree temperature rise of water used by the pre-rinse spray valve that is heated by electric hot water equals:

ΔkWH 	= 65,146 * 8.33 * 1 * ((70+ 50.7) – 50.7) * (1/.98) /3,412 * 1

=11,360 kWh

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure, but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater total

Where:

Ewater total		= IL Total Water Energy Factor (kWh/Million Gallons)

=5,010

Time of Sale:  For example, a new spray nozzle with 0.98 gal/min flow replacing a nozzle with 1.23 gal/min flow at a large institutional establishment with a cafeteria equals

ΔWater (gallons) 	= (1.23 – 0.98) * 60 * 3 * 312

= 14,040 gal/yr

ΔkWhwater 	= 14,040/1,000,000*5,010

= 70 kWh

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms 	= ΔWater (gallons) * 8.33 * 1 * (Tout - Tin) * (1/EFF_Gas) /100,000 * (1 – FLAG)

Where (new variables only):

EFF_Gas = 	Efficiency of gas water heater supplying hot water to pre-rinse spray valve

= custom, otherwise assume 80%

Time of Sale:  For example, a new spray nozzle with 0.98 gal/min flow replacing a nozzle with 1.23 gal/min flow at a large institutional establishments with a cafeteria with 70 degree temperature of water used by the pre-rinse spray valve that is heated by fossil fuel hot water saves annually:

ΔTherms	= 14,040 * 8.33 * 1 * ((70+50.7) - 50.7) * (1/0.80)/100,000 * (1-0)

= 102 Therms

Retrofit:  For example, a new spray nozzle with 0.98 gal/min flow replacing a nozzle with 2.14 gal/min flow at a busy large institutional establishments with a cafeteria with 70 degree temperature rise of water used by the pre-rinse spray valve that is heated by fossil fuel hot water saves annually:

ΔTherms	= 65,146 * 8.33 * 1 * ((70+50.7) - 50.7) * (1/0.80)/100,000 * (1-0)

=475 Therms

###### Water Impact Calculation

ΔWater (gallons) = (FLObase - FLOeff) * 60 * HOURSday * DAYSyear * ISR

Where:

FLObase 	= Base case flow in gallons per minute, or custom (Gal/min)

| Time of Sale | Direct Install |
| --- | --- |
| 1.23 gal/min | 2.14 gal/min |

FLOeff 		= Efficient case flow in gallons per minute or custom (Gal/min)

= 0.98 gal/min

60	= Minutes per hour

HOURSday	= Hours per day that the pre-rinse spray valve is used at the site, custom, otherwise:

| Application | Hours/day |
| --- | --- |
| Small, quick- service restaurants | 1 |
| Medium-sized casual dining restaurants | 1.5 |
| Large institutional establishments with cafeteria | 3 |

DAYSyear	= Days per year pre-rinse spray valve is used at the site, custom, otherwise 312 days/yr based on assumed 6 days/wk x 52 wk/yr = 312 day/yr.

ISR	= in-service-rate, the percentage of units actually installed. For kits programs, if survey  data is unavailable, use 0.466. For all other programs use 1.0.

Time of Sale:  For example, a new spray nozzle with 0.98 gal/min flow replacing a nozzle with 1.23 gal/min flow at a large institutional establishment with a cafeteria equals

= (1.23 – 0.98) * 60 * 3 * 312

= 14,040 gal/yr

Retrofit:  For example, a new spray nozzle with 0.98 gal/min flow replacing a nozzle with 2.14 gal/min flow at a large institutional establishments with a cafeteria equals

= (2.14 – 0.98) * 60 * 3 * 312

= 65,146 gal/yr

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-SPRY-V08-220101

###### Review Deadline: 1/1/2026

### Infrared Charbroiler

###### Description

This measure applies to natural gas fired charbroilers that utilize infrared burners installed in a commercial kitchen

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a new natural gas charbroiler with infrared burners.

###### Definition of Baseline Equipment

The baseline equipment is an existing natural gas charbroiler without infrared burners.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $2173.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

Custom calculation below, otherwise use deemed value of 707 therms based on default values.

∆Therms=∆PreheatEnergy+ ∆CookingEnergy*Days100,000

∆PreheatEnergy= PreheatRateBase-PreheatRateEE*Preheats*PreheatTime60

∆CookingEnergy= InputRateBase-InputRateEE*(Duty*Hours)

Where:

Days 		= Annual days of operation

= Custom or if unknown, use 312 days per year

100,000		= Btu to therms conversion factor

PreheatRateBase 	= Preheat energy rate of baseline charbroiler

= 64,000 Btu/hr

PreheatRateEE	= Preheat energy rate of infrared charbroiler

= Custom or if unknown, use 54,000 Btu/hr

Preheats		= Number of preheats per day

= Custom or if unknown, use 1 preheat per day

PreheatTime	= Length of one preheat

= Custom or if unknown, use 15 minutes per preheat

60 		= Minutes to hours conversion factor

InputRateBase 	= Input energy rate of baseline charbroiler

= 140,000 Btu/hr

InputRateEE	= Input energy rate of infrared charbroiler

= Custom or if unknown, use 105,000 Btu/hr

Duty 	= Duty cycle of charbroiler (%)

= Custom or if unknown, use 80%

Hours 		= Average daily hours of operation

= Custom or if unknown, use 8 hours per day

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-IRCB-V02-180101

###### Review Deadline: 1/1/2024

### Rotisserie Oven

###### Description

This measure applies to efficient natural gas fired high efficiency rotisserie ovens utilizing infrared burners or design approaches that combine radiative heat exchangers and convection heating and installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a new highly efficient natural gas rotisserie oven as defined by the program.

###### Definition of Baseline Equipment

The baseline equipment is a new standard natural gas rotisserie oven.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $2665.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

Custom calculation below based on Food Service Technology Center calculator, otherwise use deemed value of 599 therms, based on default values.

∆Therms=(InputRateBase- InputRateEE) * (Duty * Hours)100,000

Where:

InputRateBase	= Energy input rate of baseline rotisserie oven (Btu/hr)

= Custom of if unknown, use 90,000 Btu/hr

InputRateEE 	= Energy input rate of efficient rotisserie oven (Btu/hr)

= Custom of if unknown, use 50,000 Btu/hr

Duty 	= Duty cycle of rotisserie oven (%)

= Custom or if unknown, use 60%

Hours	= Typical operating hours of rotisserie oven

= Custom or if unknown, use 2,496 hours

100,000	= Btu to therms conversion factor

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-IROV-V03-220101

###### Review Deadline: 1/1/2024

### Infrared Salamander Broiler

###### Description

This measure applies to natural gas fired high efficiency salamander broilers utilizing infrared burners installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a new natural gas salamander broiler with infrared burners

###### Definition of Baseline Equipment

The baseline equipment is an existing natural gas salamander broiler without infrared burners

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $1,000.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

Custom calculation below based on Food Service Technology Center calculator, otherwise use deemed value of 240 therms, based on defaults.

∆Therms=(InputRateBase- InputRateEE) * (Duty * Hours)100,000

Where:

InputRateBase	= Rated energy input rate of baseline salamander broiler (Btu/hr)

= 38,500 Btu/hr

InputRateEE 	= Rated energy input rate of infrared salamander broiler (Btu/hr)

= Custom; or if unknown, use 24,750 Btu/hr

Duty 	= Duty cycle of salamander broiler (%)

= Custom; or if unknown, use 70%

Hours	= Typical operating hours of salamander broiler

= Custom; or if unknown, use 2,496 hours

100,000	= Btu to therms conversion factor

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-IRBL-V02-180101

###### Review Deadline: 1/1/2024

### Infrared Upright Broiler

###### Description

This measure applies to natural gas fired high efficiency upright broilers utilizing infrared burners and installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a new natural gas upright broiler with infrared burners.

###### Definition of Baseline Equipment

The baseline equipment is an existing natural gas upright broiler without infrared burners.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $4,400.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

Custom calculation below based on Food Service Technology Center calculator, otherwise use deemed value of 943 therms based on default values.

∆Therms=(InputRateBase- InputRateEE) * (Duty * Hours)100,000

Where:

InputRateBase	= Rated energy input rate of baseline upright broiler (Btu/hr)

= 144,000 Btu/hr

InputRateEE 	= Rated energy input rate of infrared upright broiler (Btu/hr)

= Custom; or if unknown, use 90,000 Btu/hr

Duty 	= Duty cycle of upright broiler (%)

= Custom; or if unknown, use 70%

Hours	= Typical operating hours of upright broiler

= Custom; or if unknown, use 2,496 hours

100,000	= Btu to therms conversion factor

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-IRUB-V02-180101

###### Review Deadline: 1/1/2024

### Kitchen Demand Ventilation Controls

###### Description

Installation of commercial kitchen demand ventilation controls that vary the ventilation based on cooking load and/or time of day.

IECC 2018 specifies that Kitchen Demand Control Ventilation is a mandatory compliance pathway for systems over 5,000 CFM of exhaust airflow. As stated, each kitchen exhaust hood shall comply with one of the following:

- Not < 50% of all replacement air shall be transfer air that would otherwise be exhausted.

- Demand ventilation systems on not < 75% of the exhaust air that are configured to provide not less than 50% reduction in exhaust and replacement air system airflow rates including controls necessary to modulate airflow in response to appliance operation and maintain full capture and containment of smoke, effluent, and combustion products during cooking and idle.

- Listed energy recovery devices with a sensible heat recovery effectiveness not < 40% on not < 50% of the total exhaust airflow.

If one of these alternate compliance options is met, kitchen demand ventilation controls would not be required by code; however, in these situations the demand ventilation controls would be considered redundant and the energy savings would likely be reduced. As a result, this measure is only applicable to new kitchens/systems under 5,000 CFM of exhaust airflow.

This measure was developed to be applicable to the following program types: NC, RF, TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a  control system that varies the exhaust rate of kitchen ventilation (exhaust and/or makeup air fans) based on the energy and effluent output from the cooking appliances (i.e., the more heat and smoke/vapors generated, the more ventilation needed). There are three main demand control ventilation systems available that can achieve this type of modulation:

- Temperature sensors only. These systems ramp ventilation up and down based solely on the temperature from the cooking activity as measured in the ductwork or capture tank of the hood.

- Temperature and optical sensors. These systems offer the same functionality as systems with only temperature sensors plus the ability to change the ventilation rate based on the presence of smoke or steam.

- Temperature and infrared cooking sensors. These systems offer the same functionality as systems with only temperature sensors plus the ability to measure ventilation up and down based on when cooking starts.

###### Definition of Baseline Equipment

The baseline equipment is kitchen ventilation that has constant speed ventilation motor.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 20 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is:

| Measure Category | Incremental Cost $/HP of fan |
| --- | --- |
| DVC Control Retrofit | $1,992 |
| DVC Control New | $1,180 |

###### Loadshape

Loadshape C23 - Commercial Ventilation

###### Coincidence Factor

The measure has deemed peak kW savings therefore a coincidence factor does not apply.

Algorithm

###### Calculation of Savings

Annual energy use was based on monitoring results from five different types of sites, as summarized in PG&E Food Service Equipment work paper.

###### Electric Energy Savings

kWh savings are assumed to be 4966 kWh per horsepower of the fan.

###### Summer Coincident Peak Demand Savings

kW savings are assumed to be 0.68 kW per horsepower of the fan.

###### Natural Gas Energy Savings

ΔTherms = CFM * HP* Annual Heating Load /(Eff(heat) * 100,000)

Where:

CFM 	=  the average airflow reduction with ventilation controls per hood

= 430 cfm/HP

HP 	= actual if known, otherwise assume 7.75 HP

Annual Heating Load 	= Annual heating energy required to heat fan exhaust make-up air, Btu/cfm dependent on location:

| Zone | Annual Heating Load, Btu/cfm |
| --- | --- |
| 1 (Rockford) | 154,000 |
| 2-(Chicago) | 144,000 |
| 3 (Springfield) | 132,000 |
| 4-(Belleville) | 102,000 |
| 5-(Marion) | 104,000 |

Eff(heat) 	= Heating Efficiency

= actual if known, otherwise assume 80%

100,000		= conversion from Btu to Therm

For example, a kitchen hood in Rockford, IL with a 7.75 HP ventilation motor

ΔTherms 	= 430 * 7.75*154,000 / (0.80 * 100,000)

= 6,415 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-VENT-V04-210101

###### Review Deadline: 1/1/2025

### Pasta Cooker

###### Description

This measure applies to natural gas fired dedicated pasta cookers as determined by the manufacturer and installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a new natural gas fired pasta cooker.

###### Definition of Baseline Equipment

The baseline equipment is an existing natural gas fired stove where pasta is cooked in a pan.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12.

###### Deemed Measure Cost

The incremental capital cost for this measure is $2,400.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

The annual natural gas energy savings from this measure is a deemed value equaling 1380 Therms.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-PCOK-V02-180101

###### Review Deadline: 1/1/2024

### Rack Oven - Double Oven

###### Description

This measure applies to natural gas fired high efficiency rack oven - double oven installed in a commercial kitchen.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a new natural gas rack oven - double oven with a baking efficiency ≥ 50% utilizing ASTM standard 2093.

###### Definition of Baseline Equipment

The baseline equipment is an existing natural gas rack oven – double oven with a baking efficiency < 50%.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $3,000.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

Custom calculation below, otherwise use deemed value of 1930 therms based on default values.

∆Therms=InputRate*BakingEfficiencyEE-BakingEfficiencyBase*Duty*Hours*1100,000

Where:

InputRate		= Input energy rate of rack oven – double oven

= Custom; or if unknown, 275,000 Btu/hr

BakingEfficiencyEE	= Baking efficiency of energy efficiency rack oven – double oven

= Custom; or if unknown, use 55%

BakingEfficiencyBase 	= Baking efficiency of baseline rack oven – double oven

= Custom; or if unknown, 30%

Duty 		= Duty cycle of double rack oven (%)

= Custom; or if unknown, use 75%

Hours 			= Average daily hours of operation

= Custom; or if unknown, use 3,744 hours

100,000		= Btu to therms conversion factor

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code CI-FSE-RKOV-VO2-180101

###### Review Deadline: 1/1/2024

### ENERGY STAR Electric Convection Oven

###### Description

Commercial convection ovens that are ENERGY STAR certified have higher heavy load cooking efficiencies, and lower idle energy rates, making them up to 20 percent more efficient than standard models.  Energy savings estimates are for ovens using full size (18” x 36”) sheet pans.

This measure was developed to be applicable to the following program types; TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is assumed to be an ENERGY STAR qualified electric convection oven.

###### Definition of Baseline Equipment

The baseline equipment is assumed to be a standard convection oven with a heavy load efficiency of 65%.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental cost for this measure is assumed to be $350 for half size units and $500 for full size.

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

Summer Peak Coincidence Factor for measure is provided below for different building type:

| Location | CF CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.39 |
| Unknown | 0.41 |

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh	= kWHbase - kWheff

kWh 		= [(LB * EFOOD/EFF) + (IDLE * (HOURSDAY – LB/PC – PRETIME/60)) + PREENERGY] * DAYS

Where:

kWHbase		= the annual energy usage of the baseline equipment calculated using baseline values

kWHeff		= the annual energy usage of the efficient equipment calculated using efficient values

HOURSDAY	= daily operating hours

= Actual, defaults:

| Type of Food Service | HOURSDAY |
| --- | --- |
| Fast Food, limited menu | 4 |
| Fast Food, expanded menu | 5 |
| Pizza | 8 |
| Full Service, limited menu | 8 |
| Full Service, expanded menu | 7 |
| Cafeteria | 6 |
| Unknown | 6 |
| Custom | Varies |

DAYS		= Days per year of operation

= Actual, default = 365

PRETIME	= Preheat time (min/day), the amount of time it takes a steamer to reach operating temperature when turned on

= 15 min/day

EFOOD	= ASTM Energy to Food (kWh/lb); the amount of energy absorbed by the food during cooking, per pound of food

= 0.0732

LB	= pounds of food cooked per day (lb/day)

= Actual, defaults:

= 61 lbs for half sized oven

= 122 lbs for full-sized oven

EFF	= Heavy load cooking energy efficiency (%).  See table below. If known, use Actual for Energy Efficient model.

IDLE	= Idle energy rate.  See table below. If known, use Actual for Energy Efficient model.

PC	= Production capacity (lbs/hr).  See table below. If known, use Actual for Energy Efficient model.

PREENERGY	= Preheat energy (kWh/day).  See table below. If known, use Actual for Energy Efficient model.

Table: Performance Metrics: Baseline and Efficient Values

| Metric | Size | Baseline | Energy Efficient |
| --- | --- | --- | --- |
| PREENERGY (kWh) |  | Half |  | 0.89 |  |  | 0.70 |
|  |  | Full |  | 1.56 |  |  | 1.39 |
| IDLE (kW) |  | Half |  | 1.15 |  |  | 0.81 |
|  |  | Full |  | 1.41 |  |  | 0.92 |
| EFF |  | Half |  | 70% |  |  | 75% |
|  |  | Full |  | 77% |  |  | 80% |
| PC (lb/hr) |  | Half |  | 45 |  |  | 53 |
|  |  | Full |  | 70 |  |  | 82 |

For example, using defaults provided above, the savings for a full-sized ENERGY STAR Electric Convection Oven in unknown location are:

kWHbase 		= [(122 * 0.0732/0.77) + (1.4 * (6 – 122/70 – 8.8/60)) + 1.6] * 365

= 6,919 kWh

kWheff		= [(122 * 0.0732/0.80) + (0.917 * (6 – 122/82 – 8.55/60)) + 1.4] * 365

= 6,044 kWh

ΔkWh		= kWHbase - kWheff

= 6,919 – 6,044

= 875 kWh

###### Summer Coincident Peak Demand Savings

ΔkW  = (ΔkWh / (HOURSDAY * DAYS)) * CF

Where:

ΔkWh 		= Annual energy savings (kWh), calculated above

CF	 = Summer Peak Coincidence Factor, as defined above

For example, using defaults provided above, the savings for a full-sized ENERGY STAR Electric Convection Oven in unknown location are:

ΔkW  	= (875 / (6 * 365)) * 0.41

= 0.16 kW

###### Fossil Fuel Impact Descriptions and Calculation

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code CI-FSE-ECON-V03-220101

###### Review Deadline: 1/1/2026

### Efficient Dipper Wells

###### Description

Various commercial food establishments utilize dipper wells that continuously run fresh water over utensils. One example is an ice cream shop that places the ice cream scooper in the dipper well, in order to keep them clean and avoid cross-mixing of flavors. Some restaurants may utilize a dipper well to store potato slicers and butter-ball scoopers. Coffee shops often utilize a dipper well for storage of drink thermometers and mixing spoons. Bars may utilize a dipper well for storage of mixing spoons, strainers, ice tongs, and other utensils. Dipper wells may also be found in grocery stores, school cafeterias, and other institutional kitchens.

Commercial kitchen equipment vendors have developed water-efficient dipper well designs which eliminate the continuous water flow. The efficient design recirculates the water in the well rather than continuously adding fresh water. For bacteriological control some designs utilize a chemical disinfectant (i.e., bleach) and some utilize ozone.

The calculated water savings (in gallons/year) will, in turn, be used to calculate electricity savings (in kWh/year) after applying the appropriate energy factor.

Heated dipper wells are not included in this characterization as the electric penalty associated with the electric resistance heating removes all potential electric savings due to water characterization.

This measure was developed to be applicable to the following program types; EREP and TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is assumed to be a dipper well that does not continuously run. One type of water-efficient dipper well design recirculates the water in the basin, rather than continuously adding fresh water. The efficient design will employ chemical or ozone sanitation.

Other types of water-efficient dipper well utilize a spatula or shower, where water is only applied to the surface of the utensil when a pressure switch is activated. The dimensions of water-efficient dipper wells will vary, depending on the number of utensils that need to be handled. The flow rate of the spigot is similar between the baseline equipment and the efficient equipment. However, that flow rate only occurs when the well initially fills up or the pressure switch is activated.

###### Definition of Baseline Equipment

The baseline equipment is assumed to be a dipper well providing continuously running fresh water to the utensils in the basin. As a result, there is a concurrent stream of wastewater that is continuously sent to the sewer. The dipper well typically will run during the hours of operation for the restaurant or bar. Some dipper wells will also be left on during the night when the establishment is closed.

Many dipper wells consist of two concentric tanks. Water flows into the inner tank and overflows through the perforations at the top to the outer tank, which is connected to the sewer drain. Other designs utilize just one tank, with some other means of overflow drainage to the sewer.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

###### Deemed Measure Cost

The cost for this measure is assumed to be $450 for Early Replacement or $300 for Time of Sale. The typical material cost for an efficient dipper well system is approximately $150 to $350. The typical material cost for a baseline dipper well system is approximately $100 to $200.  Full installation costs, including plumbing materials, labor, and any associated controls, should be used for screening purposes.

###### Loadshape

###### Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

Energy savings from the efficient dipper well systems are the result of reduced water consumption. There are indirect electric energy savings from reduced potable water treatment and wastewater treatment energy inputs.

###### Electric Energy Savings

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure, but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

The electric energy savings are based indirectly on the reduced electricity usage used to provide the potable water and treat the wastewater. By applying an “Energy Factor”, the water savings (in gallons/year) can be converted to electricity savings (in kWh/year). This “Energy Factor” considers the electric energy requirements of potable water treatment plants, potable water distribution, wastewater treatment plants, and wastewater distribution.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater total

Where:

Ewater total	= IL Total Water Energy Factor (kWh/Million Gallons)

=5,010

For example,

BAWU =  (DWOH * AO) / (TFOG x 1 hour/60 min)

= [16 hours/day] * [365 day/year]

[0.5 gal/min] * [1 hour/60 min]

= 175,200 gal/year

ECAWU = 3,650 gal/year

ΔWater = BAWU – ECAWU

= 175,200 gal/year – 3,650 gal/year

= 171,550 gal/year

ΔkWhwater = ΔWater / 1,000,000 * Ewater total

= (171,500 gal. of water/year) / 1,000,000 * 5,010 kWh/million gallons

= 859 kWh/year

###### Summer Coincident Peak Demand Savings

N/A

###### Fossil Fuel Impact Descriptions and Calculation

N/A

###### Water Impact Descriptions and Calculation

The methodology for quantifying the water savings involves a direct comparison of the baseline equipment to the efficient equipment. The baseline flow rate will typically be between 0.2 gpm to 1.0 gpm. The actual flow rate of the baseline equipment should be directly measured. This can be accomplished by recording the time required to fill a 1-gallon container (minutes per gallon); taking the inverse of that value will give the water flow rate (gallons per minute). The number of hours per day that the spigot remains flowing should be determined. This is typically coincident with the operating hours of the establishment, but the spigot could remain flowing during off hours too.

The equation for calculating the baseline annual water usage is as follows:

BAWU =  [DWOH * AO) / [TFOG x (1 hour/60 min)]

Where:

BAWU 		= Baseline Annual Water Usage (gal/year)

DWOH 		= Dipper Well Operating Hours (hours/day)

AO 		= Annual Operations (days/year)

TFOG 		= Time to Fill One Gallon (min/gal)

Estimating the efficient-case water consumption will require an understanding of how the dipper well will be used. If the efficient-case equipment utilizes a constantly circulating pool of chemically treated water, then the only water consumption is that required to fill the basin. Depending on the number of times that the basin is filled and emptied in a day, the annual water consumption for the efficient case can be calculated as follows:

ECAWU = BV * BFPD * AO

Where:

ECAWU 		= Efficient Case Annual Water Usage (gal/year)

BV 		= Basin Volume (gal)

BFPD 		= Basin Fills Per Day (days-1)

AO 		= Annual Operations (days/year)

If the efficient-case equipment utilizes a ‘shower’ that only dispenses water when the pressure switch is activated, the amount of water consumption is dependent on the number of times the ‘shower’ is actuated and the length of each ‘shower’. The Spigot Flow Rate should be similar to that of the baseline equipment (0.2 gal/min to 1.0 gal/min). However, that flow rate is only in effect for the duration that the pressure switch is pressed. This is referred to as the Time of Actuation, and it can generally be estimated as a few seconds per push.  Furthermore, the number of times the shower is actuated in a day can be estimated by considering the customer sales volume of the establishment.

The annual water consumption for the efficient case can also be calculated as follows:

ECAWU = (SFR x TA x NAPD) / (60 sec/min x AO)

Where:

ECAWU 		= Efficient Case Annual Water Usage (gal/year)

SFR 		= Spigot Flow Rate (gal/min)

TA 		= Time of Actuation (sec/push)

NAPD 		= Number of Actuations per Day (push/day)

AO 		= Annual Operations (days/year)

For the purposes of this measure, the Efficient Case daily water usage of 10 gal/day will be used . At 365 days/year of usage, the ECAWU will be 3,650 gal/year.

Finally, the annual water savings per year can be calculated as follows:

ΔWater = BAWU – ECAWU

Where:

ΔWater 		= Total Water Savings (gal/year)

BAWU 		= Baseline Annual Water Usage (gal/year)

ECAWU 		= Efficient Case Annual Water Usage (gal/year)

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code CI-FSE-EDIP-V02-220101

###### Review Deadline: 1/1/2023

### 4.2.21 On-Demand Package Sealers – Provisional Measure

###### Description

This measure consists of the replacement of standard electric package sealers with new on-demand package sealers in a retail grocery store. The sealers are used for heat-sealing plastic-wrapped packages for retail sale. The typical baseline unit uses a 550-Watt heating element and 50 Watt heat sealing bar at about 280°F or greater and maintains that temperature unless the unit is turned off when not in use. In practice, the units are frequently left on to avoid waiting for the bar to reach operating temperature. Qualifying units use on-demand heat bars or automatic controls that turn off the unit between uses. Different configurations and brands were tested for the baseline at two grocery store chains that included a total of 199 stores.   This measure applies to grocery store, convenience store, deli, bakery, butcher, and other commercial with a demonstrated business need.

This measure was developed to be applicable to the following program types: TOS, EREP.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The on-demand package sealer uses controls to turn the equipment off when it is not in use.  The functionality of the baseline and on-demand system is similar. The on-demand package sealer operates similarly to the baseline but has a larger heating element.  The on-demand package sealer utilizes an automatic control or pressure momentary switch control to power off the heating elements when the equipment is not in use.  Controls for the on-demand unit allow the heating element to turn on only when the heating element is pushed down, or the product crosses the automatic controls. By applying pressure to the heating element or activating the automatic controls the on-demand unit engages a switch, which activates the 2,000-Watt heating element until the switch is disengaged, or for a maximum of 3 seconds. The efficient sealers use less energy overall by reducing standby electrical energy use. These machines come in stand-alone or table-top styles.

###### Definition of Baseline Equipment

The baseline package sealer consists of a heating bar and a larger heating element and is rated at approximately 550 Watts and 0.50 kW, respectively. The heating bar is used to cut the wrapping film as it contacts the heating bar. The larger heating element is used to heat up the wrapping film. When the wrapping film is heated, the film sticks to a package to seal the product. With the conventional package sealer, both heating elements are controlled to keep a constant temperature of 280°F. The units are manually turned on and off. The baseline package sealers come in two styles, a stand-alone unit and a table-top unit.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

###### Deemed Measure Cost

The deemed measure cost for this measure varies based on unit size and type. Please see the table below for typical costs:

| Equipment Category | Tabletop Unit | Floor Unit |
| --- | --- | --- |
| Baseline |  | $825 |  | $2,349 |  |
| Efficient |  | $1,215 |  | $4,304 |  |

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = ((Wattsbase*HOU)/1,000) - ((Wattsefficient*HOU)/1,000) * (1-ESF)((Wattsefficient*HOU)/1,000) * (1-ESF)

Where:

Wattsbase        	= Wattage of Existing Equipment’s heating element

= If not known, use 600 W

Wattsefficient 	= Wattage of Proposed Efficient Equipment sealing element

= If not known, use 2,000 W

HOU 		= Use known Hours of Use

= If hours not known, hours are selected from the fixture hours column of the Reference Table in Section 4.5 for each building type.

ESF		= Energy Savings Factor

= If ESF not known, use 90%

For example, a new on-demand package sealer replacing a baseline package sealer with unknown hours at a grocery store saves:

ΔkWh	= 	((600 * 5,468) / 1,000) – (((2,000 * 5,468) / 1,000) * (1 - 0.9))

=	2,187.2 kWh

###### Summer Coincident Peak Demand Savings

ΔkW = ΔkWhHOU*CF

Where:

CF 		= Coincident Factor, use 1.0.

For example, a new on-demand package sealer replacing a baseline package sealer with unknown hours at a grocery store saves:

ΔkWh	=	2,187.2 / 5,468 * 1.0

=	0.40 kW

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-FSE-ODPS-V01-220101

###### Review Deadline: 1/1/2025

## Hot Water

### Water Heater

###### Description

This measure is for upgrading from minimum code to a high efficiency water heater. Storage water heaters are used to supply hot water for a variety of commercial building types. Storage capacities vary greatly depending on the application. Large consumers of hot water include (but not limited to) industries, hotels/motels and restaurants.

Tankless water heaters function similar to standard hot water heaters except they do not have a storage tank.  When there is a call for hot water, the water is heated instantaneously as it passes through the heating element and then proceeds to the user or appliance calling for hot water.  Tankless water heaters achieve savings by eliminating the standby losses that occur in stand-alone or tank-type water heaters and by being more efficient than the baseline storage hot water heater.

Heat pump water heaters use electricity to move heat from one place to another instead of generating heat directly and can allow for additional energy savings. Savings are presented dependent on the heating system installed in the home due to the impact of the heat pump water heater on the heating loads.

This measure was developed to be applicable to the following program types: TOS, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The minimum specifications of the high efficiency equipment should be defined by the programs.

###### Definition of Baseline Equipment

Time of Sale: The baseline condition is assumed to be a new standard water heater of same type as the existing unit being replaced, meeting the Federal Standard for ≤75,000 Btuh units and IECC 2018 for all others. If existing type is unknown, assume same water heater type as the efficient unit.

For Residential-sized >55 gallon HPWH tanks, the baseline should assume the same capacity and use the appropriate standard listed below, unless it can be confirmed that the existing tank being replaced was <55 gallon (and the larger tank is only being used to achieve greater efficiency of the heat pump cycle and prevent the unit from going in to resistance mode), in which case the existing unit capacity and the  <55 gallon algorithms should be used.

New Construction: The baseline condition is a new standard water heater of the same type as the efficient, meeting the IECC code level in place at the time the building permit was issued. Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

Note the same draw pattern (very small, low, medium and high draw) should be used for both baseline and efficient units. Definitions of draw pattern are provided below.

| Equipment Type | Sub Category | Draw Pattern | Federal Standard – Uniform Energy Factor |
| --- | --- | --- | --- |
| Residential Gas Storage Water Heaters ≤75,000 Btu/h | ≤55 gallon tanks | Very small | UEF = 0.3456 – (0.0020 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.5982 – (0.0019 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.6483 – (0.0017 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.6920 – (0.0013 * Rated Storage Volume in Gallons) |
|  | >55 gallon and ≤100 gallon tanks | Very small | UEF = 0.6470 – (0.0006 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.7689 – (0.0005 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.7897 – (0.0004 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.8072 – (0.0003 * Rated Storage Volume in Gallons) |
| Residential-duty Commercial High Capacity Storage Gas-Fired Storage Water Heaters > 75,000 Btu/h | ≤120 gallon tanks | Very small | UEF = 0.2674 – (0.0009 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.5362 – (0.0012 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.6002 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.6597 – (0.0009 * Rated Storage Volume in Gallons) |
| Commercial Gas Storage Water Heaters >75,000 Btu/h and ≤155,000 Btu/h | >120 gallon tanks | All | 80% Ethermal, Standby Losses = (Q /800 + 110√Rated Storage Volume in Gallons) |
| Commercial Gas Storage Water Heaters >155,000 Btu/h |  |  |  |
| Residential Gas Instantaneous Water Heaters ≤ 200,000 Btu/h | ≤2 gal | Very low | UEF = 0.80 |
|  |  | All other | UEF = 0.81 |
| Commercial Gas Instantaneous Water Heaters > 200,000 Btu/h | <10 gal | All | 80% Ethermal |
|  | ≥10 gal | All | 80% Ethermal |
| Residential Electric Storage Water Heaters ≤ 75,000 Btu/h | ≤55 gallon tanks | Very small | UEF = 0.8808 – (0.0008 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.9254 – (0.0003 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.9307 – (0.0002 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.9349 – (0.0001 * Rated Storage Volume in Gallons) |
|  | >55 gallon and ≤120 gallon tanks | Very small | UEF = 1.9236 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 2.0440 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 2.1171 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 2.2418 – (0.0011 * Rated Storage Volume in Gallons) |
| Residential Electric Instantaneous Water Heaters | ≤12kW and ≤2 gal | All other | UEF = 0.91 |
|  |  | High | UEF = 0.92 |
| Residential-duty Commercial Electric Instantaneous Water Heaters | > 12kW and ≤58.6 kW and ≤2 gal | All | UEF = 0.80 |

Residential-duty Commercial Water Heaters meet the following criteria:

- Is not designed to provide outlet hot water at temperatures greater than 180 °F; and

- If electric, must use a single-phase external power supply; and

- Gas-fired Storage Water Heater with a rated input no greater than 105 kBtu/h and a DOE Rated Storage volume no greater than 120 gallons.

- Electric Instantaneous with a rated input no greater than 58.6 kW and a DOE Rated Storage volume no greater than 2 gallons.

Draw patterns are based on first hour rating (gallons) for storage tanks and maximum flow (GPM) for instantaneous as shown below:

| Storage Water Heater Draw Pattern |  |
| --- | --- |
| Draw Pattern | First Hour Rating (gallons) |
| Very Small | ≥ 0 and < 18 |
| Low | ≥ 18 and < 51 |
| Medium | ≥ 51 and < 75 |
| High | ≥ 75 |

| Instantaneous Water Heater Draw Pattern |  |
| --- | --- |
| Draw Pattern | Max GPM |
| Very Small | ≥ 0 and < 1.7 |
| Low | ≥ 1.7 and < 2.8 |
| Medium | ≥ 2.8 and < 4 |
| High | ≥ 4 |

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years for storage and heat pump units, 5 years for electric tankless, and 20 years for gas tankless.

###### Deemed Measure Cost

The full install cost and incremental cost assumptions are provided below. Actual costs should be used where available:

Gas storage water heaters:

| Equipment Type | Category | Install Cost | Incremental Cost |
| --- | --- | --- | --- |
| Gas Storage Water Heaters ≤ 75,000 Btu/h, ≤55 Gallons | Baseline | $616 | N/A |
|  | Efficient | $1,055 | $440 |
| Gas Storage Water Heaters > 75,000 Btu/h | 0.80 Et | $4,886 | N/A |
|  | 0.83 Et | $5,106 | $220 |
|  | 0.84 Et | $5,299 | $413 |
|  | 0.85 Et | $5,415 | $529 |
|  | 0.86 Et | $5,532 | $646 |
|  | 0.87 Et | $5,648 | $762 |
|  | 0.88 Et | $5,765 | $879 |
|  | 0.89 Et | $5,882 | $996 |
|  | 0.90 Et | $6,021 | $1,135 |

For electric water heaters, the incremental capital cost for this measure is assumed to be:

| Tank Size | Incremental Cost |
| --- | --- |
| 50 gallons | $1050 |
| 80 gallons | $1050 |
| 100 gallons | $1950 |

The incremental capital cost for an electric tankless heater this measure is assumed to be:

| Output (gpm) at delta T 70 | Incremental Cost |
| --- | --- |
| 5 | $1050 |
| 10 | $1050 |
| 15 | $1950 |

The incremental capital cost for a gas fired tankless heater is assumed to be $2,526.

For a heat pump water heater, the incremental installation cost (including labor) should be used. Defaults are provided below. Actual efficient costs can also be used although care should be taken as installation costs can vary significantly due to complexities of a particular site.

| Capacity | Efficiency Range | Baseline Installed Cost | Efficient Installed Cost | Incremental Installed Cost |
| --- | --- | --- | --- | --- |
| ≤55 gallons | <2.6 UEF | $1,032 | $2,062 | $1,030 |
|  | ≥2.6 UEF | $1,032 | $2,231 | $1,199 |
| >55 gallons | <2.6 UEF | $1,319 | $2,432 | $1,113 |
|  | ≥2.6 UEF | $1,319 | $3,116 | $1,797 |

###### Loadshape

For electric hot water heaters, use Loadshape C02 - Commercial Electric DHW.

###### Coincidence Factor

The coincidence factor is assumed to be 0.925.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Electric energy savings are calculated for electric water heaters per the equations given below.

Electric units ≤12 kW:

∆kWh= Tout-Tin * HotWaterUseGallon*γWater*1* 1UEFelecbase- 1UEFEff3412+HPWHWasteHeatcool- HPWHWasteHeatheat

Where:

Tout		= Tank temperature

= 125°F

Tin		= Incoming water temperature from well or municiple system

= 50.7°F

HotWaterUseGallon	= Estimated annual hot water consumption (gallons)

= Actual if possible to provide reasonable custom estimate. If not, two methodologies are provided to develop an estimate:

- Consumption per usable storage tank capacity

= Capacity * Consumption/cap

Where:

Capacity		= Usable capacity of hot water storage tank in gallons

= Actual

Consumption/cap = Estimate of consumption per gallon of usable tank    capacity, based on building type:

| Building Type | Consumption/Cap |
| --- | --- |
| Convenience | 528 |
| Education | 568 |
| Grocery | 528 |
| Health | 788 |
| Large Office | 511 |
| Large Retail | 528 |
| Lodging | 715 |
| Other Commercial | 341 |
| Restaurant | 622 |
| Small Office | 511 |
| Small Retail | 528 |
| Warehouse | 341 |
| Nursing | 672 |
| Multi-Family | 894 |

- Consumption per unit area by building type

= (Area/1000) * Consumption/1,000 sq.ft.

Where:

Area  	= Area in sq.ft that is served by DHW boiler

= Actual

Consumption/1,000 sq.ft. = Estimate of DHW consumption per 1,000 sq.ft. based on building type:

| Building Type | Consumption/1,000 sq.ft. |
| --- | --- |
| Convenience | 4,594 |
| Education | 7,285 |
| Grocery | 697 |
| Health | 24,540 |
| Large Office | 1,818 |
| Large Retail | 1,354 |
| Lodging | 29,548 |
| Other Commercial | 3,941 |
| Restaurant | 44,439 |
| Small Office | 1,540 |
| Small Retail | 6,111 |
| Warehouse | 1,239 |
| Nursing | 30,503 |
| Multi-Family | 15,434 |

γWater		= Specific weight capacity of water (lb/gal)

= 8.33 lbs/gal

1	= Specific heat of water (Btu/lb.°F)

UEFelecbase  	= Rated efficiency of baseline water heater expressed as Uniform Energy Factor (UEF);

Note the same draw pattern (very small, low, medium and high draw) should be used for both baseline and efficient units.

| Equipment Type | Sub Category | Draw Pattern | Federal Standard – Uniform Energy Factor |
| --- | --- | --- | --- |
| Residential Electric Storage Water Heaters ≤ 75,000 Btu/h | ≤55 gallon tanks | Very small | UEF = 0.8808 – (0.0008 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.9254 – (0.0003 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.9307 – (0.0002 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.9349 – (0.0001 * Rated Storage Volume in Gallons) |
|  | >55 gallon and ≤120 gallon tanks | Very small | UEF = 1.9236 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 2.0440 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 2.1171 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 2.2418 – (0.0011 * Rated Storage Volume in Gallons) |
| Residential Electric Instantaneous Water Heaters | ≤12kW and ≤2 gal | All other | UEF = 0.91 |
|  |  | High | UEF = 0.92 |
| Residential-duty Commercial Electric Instantaneous Water Heaters | > 12kW and ≤58.6 kW and ≤2 gal | All | UEF = 0.80 |

Draw patterns are based on first hour rating (gallons) for storage tanks and maximum flow (GPM) for instantaneous as shown below:

| Storage Water Heater Draw Pattern |  |
| --- | --- |
| Draw Pattern | First Hour Rating (gallons) |
| Very Small | ≥ 0 and < 18 |
| Low | ≥ 18 and < 51 |
| Medium | ≥ 51 and < 75 |
| High | ≥ 75 |

| Instantaneous Water Heater Draw Pattern |  |
| --- | --- |
| Draw Pattern | Max GPM |
| Very Small | ≥ 0 and < 1.7 |
| Low | ≥ 1.7 and < 2.8 |
| Medium | ≥ 2.8 and < 4 |
| High | ≥ 4 |

UEFeff 	= Rated efficiency of efficient water heater expressed as Uniform Energy Factor (UEF)

= Actual

3412		= Converts Btu to kWh

HPWHWasteheatcool	= Heat Pump Water Heater Only - Cooling savings from conversion of heat in building to water heat

=TOUT – TIN* HotWaterUseGallon*γWater*1* 1 - 1UEFEff * LF * 25% *LMCOPCOOL*3412*Cool

Where:

LF		= Location Factor

= 1.0 for HPWH installation in a conditioned space

= 0.5 for HPWH installation in an unknown location

= 0.0 for installation in an unconditioned space

25%		= Portion of reduced waste heat that results in cooling savings

COPCOOL		= COP of Central Air Conditioner

= Actual - If unknown, assume 3.08 (10.5 SEER / 3.412)

LM		= Latent multiplier to account for latent cooling demand

= 1.33

Cool		= 1 if building has central cooling, 0 if not cooled

HPWHWasteheatHeat	= Heat Pump Water Heater Only - Heating cost from conversion of heat in building to water heat (dependent on heating fuel)

=TOUT – TIN* HotWaterUseGallon*γWater*1* 1 - 1UEFEff * LF * 35%COPHEAT*3412*ElectricHeat0ctricHeattl

Where:

35%	= Portion of reduced waste heat that results in increased heating load

COPHEAT		= COP of electric heating system

= Actual system efficiency including duct loss - If not available, use:

| System Type | Age of Equipment | HSPF Estimate | ηHeat (Effective COP Estimate) (HSPF/3.412)*0.85 |
| --- | --- | --- | --- |
| Heat Pump | Before 2006 | 6.8 | 1.7 |
|  | 2006 - 2014 | 7.7 | 1.92 |
|  | 2015 on | 8.2 | 2.04 |
| Resistance | N/A | N/A | 1 |

ElectricHeat	= 1 if building is electrically heated, 0 if not

For example, for a 50 gallon, 95% UEF storage unit installed in a 1500 ft2 restaurant:

ΔkWh		= ((125 – 50.7) * ((1,500/1,000) * 44,439) * 8.33 * 1 * (1/0.88 - 1/0.95))/3412 + 0 + 0

= 1012 kWh

Electric units > 12kW:

∆kWh=Tout-Tair*V*γWater*1*SLelecbase- SLeff100SLelecbase- SLeff*87663412

Tair		= Ambient Air Temperature

= 70°F

V		= Rated tank volume in gallons

= Actual

SLelecbase		= Standby loss of electric baseline unit (%/hr)

= 0.30 + 27/V

SLeff		= Nameplate standby loss of new water heater, in BTU/h

8766		= Hours per year

For example, >12kW, 100 gallon storage unit with rated standby loss of 0.5 %/hr:

SLbase	= 0.3 + (27 / 100)

= 0.57%/hr

ΔkWh		= (((125 – 70) * 100 * 8.33 * 1 * (0.57- 0.5)/100) * 8766)/3412

= 82.4 kWh

###### Summer Coincident Peak Demand Savings

∆kW=∆kWhHours*CF

Where:

Hours		= Full load hours of water heater

= 6461

CF 		= Summer Peak Coincidence Factor for measure

= 0.925

For example, >12kW, 100 gallon storage unit with rated standby loss of 0.5 %/hr:

ΔkW		= 82.4 / 6,461 * 0.925

= 0.0118 kW

###### Natural Gas Energy Savings

Natural gas  energy savings are calculated for natural gas storage water heaters per the equations given below.

∆Therms=Tout-Tin * HotWaterUseGallon*γWater*1*1UEFgasbase- 1UEFEff100,000- HPWHWasteHeatGasHeat

Where:

100,000		= Converts Btu to Therms

EFgasbase  	= Rated efficiency of baseline water heater (expressed as Uniform Energy Factor (UEF) or Thermal Efficiency as provided below).

Note the same draw pattern (very small, low, medium and high draw) should be used for both baseline and efficient units.

| Equipment Type | Sub Category | Draw Pattern | Federal Standard – Uniform Energy Factor |
| --- | --- | --- | --- |
| Residential Gas Storage Water Heaters ≤75,000 Btu/h | ≤55 gallon tanks | Very small | UEF = 0.3456 – (0.0020 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.5982 – (0.0019 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.6483 – (0.0017 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.6920 – (0.0013 * Rated Storage Volume in Gallons) |
|  | >55 gallon and ≤100 gallon tanks | Very small | UEF = 0.6470 – (0.0006 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.7689 – (0.0005 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.7897 – (0.0004 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.8072 – (0.0003 * Rated Storage Volume in Gallons) |
| Residential-duty Commercial High Capacity Storage Gas-Fired Storage Water Heaters > 75,000 Btu/h | ≤120 gallon tanks | Very small | UEF = 0.2674 – (0.0009 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.5362 – (0.0012 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.6002 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.6597 – (0.0009 * Rated Storage Volume in Gallons) |
| Commercial Gas Storage Water Heaters >75,000 Btu/h and ≤155,000 Btu/h | >120 gallon tanks | All | 80% Ethermal, Standby Losses = (Q /800 + 110√Rated Storage Volume in Gallons) |
| Commercial Gas Storage Water Heaters >155,000 Btu/h |  |  |  |
| Residential Gas Instantaneous Water Heaters ≤ 200,000 Btu/h | ≤2 gal | Very low | UEF = 0.80 |
|  |  | All other | UEF = 0.81 |
| Commercial Gas Instantaneous Water Heaters > 200,000 Btu/h | <10 gal | All | 80% Ethermal |
|  | ≥10 gal | All | 78% Ethermal |

Draw patterns are based on first hour rating (gallons) for storage tanks and maximum flow (GPM) for instantaneous as shown below:

| Storage Water Heater Draw Pattern |  |
| --- | --- |
| Draw Pattern | First Hour Rating (gallons) |
| Very Small | ≥ 0 and < 18 |
| Low | ≥ 18 and < 51 |
| Medium | ≥ 51 and < 75 |
| High | ≥ 75 |

| Instantaneous Water Heater Draw Pattern |  |
| --- | --- |
| Draw Pattern | Max GPM |
| Very Small | ≥ 0 and < 1.7 |
| Low | ≥ 1.7 and < 2.8 |
| Medium | ≥ 2.8 and < 4 |

HPWHWasteHeatGasHeat	 = Heat Pump Water Heater Only - Heating cost from conversion of heat in building to water heat (dependent on heating fuel)

=TOUT – TIN* HotWaterUseGallon*γWater*1* 1 - 1UEFEff * LF * 35%100,000* ηHeat*(1-ElectricHeat)0ctricHeattl

ηHeat		= Heating system efficiency including duct loss

= Actual

Additional Standby Loss Savings

Gas Storage Water Heaters >75,000 Btu/h can claim additional savings due to lower standby losses.

∆ThermsStandby=(SLgasbase-SLeff)*8766100,000

Where:

SLgasbase		= Standby loss of gas baseline unit (Btu/h)

= Q/800 + 110√V

Q 	= Nameplate input rating in Btu/h

V	= Rated volume in gallons

SLeff		= Nameplate standby loss of new water heater, in Btu/h

8766		= Hours per year

For example, for a 200,000 Btu/h, 150 gallon, 90% UEF storage unit with rated standby loss of 1029 BTU/h installed in a 1500 ft2 restaurant:

ΔTherms		= ((125 – 50.7) * ((1,500/1,000) * 44,439) * 8.33 * 1 * (1/0.8 - 1/0.9))/100,000

= 57.3 Therms

ΔThermsStandby	= (((200000/800 + 110 * √150) – 1029) * 8766)/100,000

= 49.8 Therms

ΔThermsTotal 	= 57.3 + 49.8

= 107.1 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

The deemed O&M cost adjustment for a tankless heaters is $100.

###### Measure Code: CI-HWE-STWH-V08-220101

###### Review Deadline: 1/1/2024

### Low Flow Faucet Aerators

###### Description

This measure relates to the direct installation of a low flow faucet aerator in a commercial building. Expected applications include small business, office, restaurant, or motel. Health care-specific inputs are defined for Laminar Flow Restrictor (LFR) devices.  For multifamily or senior housing, the residential low flow faucet aerator should be used.

This measure was developed to be applicable to the following program types, DI, KITS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be an energy efficient faucet aerator, for bathrooms rated at 1.5 gallons per minute (GPM) or less, or for kitchens rated at 2.2 GPM or less. For LFR devices, the installed equipment must be a device rated at 2.2 GPM or less. Savings are calculated on an average savings per faucet fixture basis.

###### Definition of Baseline Equipment

The baseline condition is assumed to be a standard bathroom faucet aerator rated at 2.25 GPM or more, or a standard kitchen faucet aerator rated at 2.75 GPM or more. For LFR devices, the baseline condition is assumed to be no aerator at all, due to the contamination risk caused by faucet aerators in health care facilities and the baseline flow rate is assumed to be 3.74 GPM.  Note if flow rates are measured, for example through a Direct Install program, then actual baseline flow rates should be used as opposed to the deemed values.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

###### Deemed Measure Cost

The actual full install cost (including labor) for this measure should be used. If unknown assume $8 for faucet aerators and $14.27 for LFR devices.

###### Loadshape

Loadshape C02 - Commercial Electric DHW

###### Coincidence Factor

The coincidence factor for this measure is dependent on building type as presented below.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Note these savings are per faucet retrofitted.

ΔkWh  = %ElectricDHW * ((GPM_base - GPM_low)/GPM_base) * Usage *  EPG_electric * ISR

Where:

%ElectricDHW 	= proportion of water heating supplied by electric resistance heating

| DHW fuel | %Electric_DHW |
| --- | --- |
| Electric | 100% |
| Fossil Fuel | 0% |
| Unknown | 16% |

GPM_base	= Average flow rate, in gallons per minute, of the baseline faucet “as-used”

= 1.39, or custom based on metering studies, or, if measured during DI:

= Measured full throttle flow * 0.83 throttling factor

Baseline for LFRs	= 3.74 * 0.83 = 3.10

GPM_low	= Average flow rate, in gallons per minute, of the low-flow faucet aerator “as-used”

= 0.94, or custom based on metering studies, or, if measured during DI:

= Rated full throttle flow * 0.95 throttling factor

For LFRs	= 2.2 * 0.95 = 2.09

Usage	= Estimated usage of mixed water (mixture of hot water from water heater line and cold water line) per faucet (gallons per year)

= If data is available to provide a reasonable custom estimate it should be used; if not, use the following defaults (or substitute custom information in to the calculation):

| Building Type | Gallons hot water per unit per day (A) | Unit | Estimated % hot water from Faucets (B) | Multiplier (C) | Unit | Days per year (D) | Annual gallons mixed water per faucet (A*B*C*D) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Small Office | 1 | person | 100% | 10 | employees per faucet | 250 | 2,500 |
| Large Office | 1 | person | 100% | 45 | employees per faucet | 250 | 11,250 |
| Fast Food Rest | 0.7 | meal/day | 50% | 75 | meals per faucet | 365 | 9,581 |
| Sit-Down Rest | 2.4 | meal/day | 50% | 36 | meals per faucet | 365 | 15,768 |
| Retail | 2 | employee | 100% | 5 | employees per faucet | 365 | 3,650 |
| Grocery | 2 | employee | 100% | 5 | employees per faucet | 365 | 3,650 |
| Warehouse | 2 | employee | 100% | 5 | employees per faucet | 250 | 2,500 |
| Elementary School | 0.6 | person | 50% | 50 | students per faucet | 200 | 3,000 |
| Jr High/High School | 1.8 | person | 50% | 50 | students per faucet | 200 | 9,000 |
| Health | 90 | patient | 25% | 2 | Patients per faucet | 365 | 16,425 |
| Motel | 20 | room | 25% | 1 | faucet per room | 365 | 1,825 |
| Hotel | 14 | room | 25% | 1 | faucet per room | 365 | 1,278 |
| Other | 1 | employee | 100% | 20 | employees per faucet | 250 | 5,000 |

EPG_electric	= Energy per gallon of mixed water used by faucet (electric water heater)

= (8.33 * 1.0 * (WaterTemp - SupplyTemp)) / (RE_electric * 3412)

= 0.0879 kWh/gal for Bath, 0.1054 kWh/gal for Kitchen, 0.1477 kWh/gal for LFRs, 0.1004 kWh/gal for unknown

8.33		= Specific weight of water (lbs/gallon)

1.0		= Heat Capacity of water (btu/lb-°F)

WaterTemp	= Assumed temperature of mixed water

= 86F for Bath, 93F for Kitchen, 91F for Unknown, 110F for health care facilities

SupplyTemp	= Assumed temperature of water entering building

= 50.7°F

RE_electric	= Recovery efficiency of electric water heater

= 98%

3412		= Converts Btu to kWh (Btu/kWh)

ISR	= In service rate of faucet aerators dependant on install method as listed in table below:

| Selection | ISR |
| --- | --- |
| Direct Install - Deemed | 0.95 |
| Efficiency Kits - Default | 0.50 |
| Leave-Behind Kit | 0.91 |

For example, a direct installed kitchen faucet in a large office with electric DHW:

ΔkWh  	= 1 * ((1.39 – 0.94)/1.39) * 11,250 * 0.1054 * 0.95

= 364.7 kWh

For example, a direct installed bathroom faucet in an Elementary School with electric DHW:

ΔkWh  	= 1 * ((1.39 – 0.94)/1.39) * 3,000 * 0.0879 * 0.95

= 81.1 kWh

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure, but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater total

Where

Ewater total		= IL Total Water Energy Factor (kWh/Million Gallons)

=5,010

For example, a direct installed faucet in a large office:

ΔWater (gallons)	= ((1.39 – 0.94)/1.39) * 11,250 * 0.95

= 3,640 gallons

ΔkWhwater 	= 3,640/1,000,000*5,010

= 18 kWh

###### Summer Coincident Peak Demand Savings

ΔkW  = (ΔkWh / Hours) * CF

Where:

ΔkWh	= calculated value above on a per faucet basis. Note do not include the secondary savings in this calculation.

Hours 	= Annual electric DHW recovery hours for faucet use

= (Usage  * 0.44  )/GPH

= Calculate if usage is custom, if using default usage use:

| Building Type | Annual Recovery Hours |
| --- | --- |
| Small Office | 20 |
| Large Office | 92 |
| Fast Food Rest | 78 |
| Sit-Down Rest | 129 |
| Retail | 30 |
| Grocery | 30 |
| Warehouse | 20 |
| Elementary School | 24 |
| Jr High/High School | 73 |
| Health | 134 |
| Motel | 15 |
| Hotel | 10 |
| Other | 41 |

Where:

GPH	= Gallons per hour recovery of electric water heater calculated for 89.3F temp rise (140-50.7), 98% recovery efficiency, and typical 12kW electric resistance storage tank.

= 53.9

CF	= Coincidence Factor for electric load reduction

= Dependent on building type

| Building Type | Coincidence Factor |
| --- | --- |
| Small Office | 0.0064 |
| Large Office | 0.0288 |
| Fast Food Rest | 0.0084 |
| Sit-Down Rest | 0.0184 |
| Retail | 0.0043 |
| Grocery | 0.0043 |
| Warehouse | 0.0064 |
| Elementary School | 0.0096 |
| Jr High/High School | 0.0288 |
| Health | 0.0144 |
| Motel | 0.0006 |
| Hotel | 0.0004 |
| Other | 0.0128 |

For example, a direct installed kitchen faucet in a large office with electric DHW:

ΔkW  	= 364.7/92 * 0.0288

= 0.1142 kW

For example, a direct installed bathroom faucet in an Elementary School with electric DHW:

ΔkW  	= 81.1/24 * 0.0096

= 0.0324 kW

###### Fossil Fuel Impact Descriptions and Calculation

ΔTherms 	= %FossilDHW * ((GPM_base - GPM_low)/GPM_base) * Usage * EPG_gas * ISR

Where:

%FossilDHW 	= proportion of water heating supplied by fossil fuel heating

| DHW fuel | %Fossil_DHW |
| --- | --- |
| Electric | 0% |
| Fossil Fuel | 100% |
| Unknown | 86% |

EPG_gas		= Energy per gallon of mixed water used by faucet (gas water heater)

= (8.33 * 1.0 * (WaterTemp - SupplyTemp)) / (RE_gas * 100,000)

= 0.0044 Therm/gal for Bath, 0.0053 Therm/gal for Kitchen, 0.0074 Therm/gal for LFRs, 0.0050 Therm/gal for unknown

Where:

RE_gas		= Recovery efficiency of gas water heater

= 67%

100,000		= Converts Btus to Therms (Btu/Therm)

Other variables as defined above.

For example, a direct installed kitchen faucet in a large office with gas DHW:

ΔTherms	= 1 * ((1.39 – 0.94)/1.39) * 11,250 * 0.0053 * 0.95

= 18.3 Therms

For example, a direct installed bathroom faucet in an Elementary School with gas DHW:

ΔTherms	= 1 * ((1.39 – 0.94)/1.39) * 3,000 * 0.0044 * 0.95

= 4.06 Therms

###### Water Impact Descriptions and Calculation

ΔWater (gallons) = ((GPM_base - GPM_low)/GPM_base) * Usage * ISR

Variables as defined above.

For example, a direct installed faucet in a large office:

ΔWater (gallons)	= ((1.39 – 0.94)/1.39) * 11,250 * 0.95

= 3,640 gallons

For example, a direct installed faucet in an Elementary School:

ΔWater (gallons)	= ((1.39 – 0.94)/1.39) * 3,000 * 0.95

= 971 gallons

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Sources used for GPM assumptions

| Source ID | Reference |
| --- | --- |
| 1 | 2011, DeOreo, William. California Single Family Water Use Efficiency Study. April 20, 2011. |
| 2 | 2000, Mayer, Peter, William DeOreo, and David Lewis. Seattle Home Water Conservation Study. December 2000. |
| 3 | 1999, Mayer, Peter, William DeOreo. Residential End Uses of Water. Published by AWWA Research Foundation and American Water Works Association. 1999. |
| 4 | 2003, Mayer, Peter, William DeOreo. Residential Indoor Water Conservation Study. Aquacraft, Inc. Water Engineering and Management. Prepared for East Bay Municipal Utility District and the US EPA. July 2003. |
| 5 | 2011, DeOreo, William. Analysis of Water Use in New Single Family Homes. By Aquacraft. For Salt Lake City Corporation and US EPA. July 20, 2011. |
| 6 | 2011, Aquacraft. Albuquerque Single Family Water Use Efficiency and Retrofit Study. For Albuquerque Bernalillo County Water Utility Authority. December 1, 2011. |
| 7 | 2008, Schultdt, Marc, and Debra Tachibana. Energy related Water Fixture Measurements: Securing the Baseline for Northwest Single Family Homes. 2008 ACEEE Summer Study on Energy Efficiency in Buildings. |

###### Measure Code: CI-HWE-LFFA-V10-220101

###### Review Deadline: 1/1/2024

### Low Flow Showerheads

###### Description

This measure relates to the direct installation of a low flow showerhead in a commercial building. Expected applications include small business, office, restaurant, or small motel. For multifamily or senior housing, the residential low flow showerhead should be used.

This measure was developed to be applicable to the following program types:  DI. If applied to other program types, the measure savings should be verified

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be an energy efficient showerhead rated at 2.0 gallons per minute (GPM) or less. Savings are calculated on a per showerhead fixture basis.

###### Definition of Baseline Equipment

The baseline condition is assumed to be a standard showerhead rated at 2.5 GPM.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

###### Deemed Measure Cost

The actual full install cost (including labor) should be used. If unknown, assume $12 per showerhead.

###### Loadshape

Loadshape C02 - Commercial Electric DHW

###### Coincidence Factor

The coincidence factor for this measure is assumed to be 2.78%.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Note these savings are per showerhead fixture

ΔkWh  =

%ElectricDHW  * ((GPM_base * L_base - GPM_low * L_low) * NSPD * 365.25) * EPG_electric * ISR

Where:

%ElectricDHW 	= proportion of water heating supplied by electric resistance heating

= 1 if electric DHW; 0 if fuel DHW; if unknown, assume 16%

GPM_base	= Flow rate of the baseline showerhead

= 2.67 for Direct-install programs

GPM_low	= As-used flow rate of the low-flow showerhead, which may, as a result of measurements of program evaulations deviate from rated flows, see table below:

Rated Flow

2.0 GPM

1.75 GPM

1.5 GPM

Custom or Actual

L_base		= Shower length in minutes with baseline showerhead

= 8.20 min

L_low		= Shower length in minutes with low-flow showerhead

= 8.20 min

365.25		= Days per year, on average.

NSPD		= Estimated number of showers taken per day for one showerhead

EPG_electric	= Energy per gallon of hot water supplied by electric

= (8.33 * 1.0 * (ShowerTemp - SupplyTemp)) / (RE_electric * 3412)

= (8.33 * 1.0 * (101 – 50.7)) / (0.98 * 3412)

= 0.125 kWh/gal

8.33		= Specific weight of water (lbs/gallon)

1.0		= Heat Capacity of water (btu/lb-°F)

ShowerTemp	= Assumed temperature of water

= 101°F

SupplyTemp	= Assumed temperature of water entering house

= 50.7°F

RE_electric	= Recovery efficiency of electric water heater

= 98%

3412		= Converts Btu to kWh (btu/kWh)

ISR	= In service rate of showerhead

= Dependant on program delivery method as listed in table below

| Selection | ISR |
| --- | --- |
| Direct Install or Guided Self-Install | 0.98 |
| Leave-Behind Kit | 0.94 |

For example, a direct-installed 1.5 GPM showerhead in an office with electric DHW where the number of showers is estimated at 3 per day:

ΔkWh  	= 1 * ((2.67*8.20)- (1.5*8.20)) * 3*365.25) *0.125 * 0.98

= 1288 kWh

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater total

Where

Ewater total		= IL Total Water Energy Factor (kWh/Million Gallons)

=5,010

For example, a direct-installed 1.5 GPM showerhead in an office with where the number of showers is estimated at 3 per day:

ΔWater (gallons) 	= ((2.67 * 8.20)-(1.5 * 8.20)) * 3 * 365.25 * 0.98

= 10,302 gallons

ΔkWhwater 	= 10,302/1,000,000*5,010

= 52 kWh

###### Summer Coincident Peak Demand Savings

ΔkW  = ΔkWh/Hours * CF

Where:

ΔkWh	= calculated value above. Note do not include the secondary savings in this calculation.

Hours 	= Annual electric DHW recovery hours for showerhead use

= ((GPM_base * L_base) *NSPD * 365.25 ) * 0.608  / GPH

Where:

GPH	= Gallons per hour recovery of electric water heater calculated for 89.3F temp rise (140-50.7), 98% recovery efficiency, and typical 12kW electric resistance storage tank.

= 53.9

CF	= Coincidence Factor for electric load reduction

= 0.0278

For example, a direct-installed 1.5 GPM showerhead in an office with electric DHW where the number of showers is estimated at 3 per day:

ΔkW 	= (1288 / 271)*0.0278

= 0.132 kW

###### Fossil Fuel Impact Descriptions and Calculation

ΔTherms 	= %FossilDHW * ((GPM_base * L_base - GPM_low * L_low) * NSPD* 365.25) * EPG_gas * ISR

Where:

%FossilDHW 	= proportion of water heating supplied by fossil fuel heating

| DHW fuel | %Fossil_DHW |
| --- | --- |
| Electric | 0% |
| Fossil Fuel | 100% |
| Unknown | 84% |

EPG_gas		= Energy per gallon of Hot water supplied by gas

= (8.33 * 1.0 * (ShowerTemp - SupplyTemp)) / (RE_gas * 100,000)

= 0.0063 Therm/gal

Where:

RE_gas		= Recovery efficiency of gas water heater

= 67%

100,000		= Converts Btus to Therms (btu/Therm)

Other variables as defined above.

For example, a direct-installed 1.5 GPM showerhead in an office with gas DHW where the number of showers is estimated at 3 per day:

ΔTherms 	= 1.0 * (( 2.67 *8.2) – (1.5 * 8.2)) * 3 * 365.25 * 0.0063 * 0.98

= 64.9 therms

###### Water Impact Descriptions and Calculation

ΔWater (gallons) = ((GPM_base * L_base - GPM_low * L_low) * NSPD * 365.25  * ISR

Variables as defined above

For example, a direct-installed 1.5 GPM showerhead in an office with where the number of showers is estimated at 3 per day:

ΔWater (gallons) 	= ((2.67 * 8.20)-(1.5 * 8.20)) * 3 * 365.25 * 0.98

= 10,302 gallons

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Sources

| Source ID | Reference |
| --- | --- |
| 1 | 2011, DeOreo, William. California Single Family Water Use Efficiency Study. April 20, 2011. |
| 2 | 2000, Mayer, Peter, William DeOreo, and David Lewis. Seattle Home Water Conservation Study. December 2000. |
| 3 | 1999, Mayer, Peter, William DeOreo. Residential End Uses of Water. Published by AWWA Research Foundation and American Water Works Association. 1999. |
| 4 | 2003, Mayer, Peter, William DeOreo. Residential Indoor Water Conservation Study. Aquacraft, Inc. Water Engineering and Management. Prepared for East Bay Municipal Utility District and the US EPA. July 2003. |
| 5 | 2011, DeOreo, William. Analysis of Water Use in New Single Family Homes. By Aquacraft. For Salt Lake City Corporation and US EPA. July 20, 2011. |
| 6 | 2011, Aquacraft. Albuquerque Single Family Water Use Efficiency and Retrofit Study. For Albuquerque Bernalillo County Water Utility Authority. December 1, 2011. |
| 7 | 2008, Schultdt, Marc, and Debra Tachibana. Energy related Water Fixture Measurements: Securing the Baseline for Northwest Single Family Homes. 2008 ACEEE Summer Study on Energy Efficiency in Buildings. |

###### Measure Code: CI-HWE-LFSH-V08-220101

###### Review Deadline: 1/1/2023

### Commercial Pool Covers

###### Description

This measure refers to the installation of covers on commercial use pools that are heated with gas-fired equipment located either indoors or outdoors. By installing pool covers, the heating load on the pool boiler will be reduced by reducing the heat loss from the water to the environment and the amount of actual water lost due to evaporation (which then requires additional heated water to make up for it). An additional benefit to pool covers are the electricity savings from the reduced fresh water required to replace the evaporated water.

The main source of energy loss in pools is through evaporation. This is particularly true of outdoor pools where wind plays a larger role. The point of installing pool covers is threefold. First, it will reduce convective losses due to the wind by shielding the water surface. Second, it will insulate the water from the colder surrounding air. And third, it will reduce radiative losses to the night sky. In doing so, evaporative losses will also be minimized, and the boiler will not need to work as hard in replenishing the pool with hot water to keep the desired temperature.

This measure can be used for pools that (1) currently do not have pool covers, (2) have pool covers that are past the useful life of the existing cover, or (3) have pool covers that are past their warranty period and have failed.

###### Definition of Efficient Equipment

For indoor pools, the efficient case is the installation of an indoor pool cover with a 5 year warranty on an indoor pool that operates all year.

For outdoor pools, the efficient case is the installation of an outdoor pool cover with a 5 year warranty on an outdoor pool that is open through the summer season.

###### Definition of Baseline Equipment

For indoor pools, the base case is an uncovered indoor pool that operates all year.

For outdoor pools, the base case is an outdoor pool that is uncovered and is open through the summer season.

###### Deemed Lifetime of Efficient Equipment

The useful life of this measure is assumed to be 6 years.

###### Deemed Measure Cost

The table below shows the costs for the various options and cover sizes. Since this measure covers a mix of various sizes, the average cost of these options is taken to be the incremental measure cost. Costs are per square foot.

| Cover Size | Edge Style |  |
| --- | --- | --- |
|  | Hemmed (indoor) | Weighted (outdoor) |
| 1000-1,999 sq. ft. | $2.19 | $2.24 |
| 2,000-2,999 sq. ft. | $2.01 | $2.06 |
| 3,000+ sq. ft. | $1.80 | $1.83 |
| Average | $2.00 | $2.04 |

###### Loadshape

Loadshape R15 – Residential Pool Pumps

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater supply

Where

Ewater supply	= Water Supply Energy Factor (kWh/Million Gallons)

= 2,571

For example,

2400ft2 Indoor Swimming Pool:

ΔWater 	= WaterSavingFactor x Size of Pool

= 15.28 gal./ft2/year x 2400 ft2

= 36,672 gal./year

ΔkWhwater = ΔWater / 1,000,000 * Ewater supply

= 36,672 gal./year / 1,000,000 * 2,571 kWh/million gallons

= 96.3 kWh/year

2400ft2 Outdoor Swimming Pool:

ΔWater = WaterSavingFactor x Size of Pool

= 8.94 gal./ft2/year x 2400 ft2

= 21,456 gal./year

ΔkWhwater = ΔWater / 1,000,000 * Ewater supply

= 21,456 gal./year / 1,000,000 * 2,571 kWh/million gallons

= 55.2 kWh/year

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

The calculations are based on modeling runs using RSPEC! Energy Smart Pools Software that was created by the U.S. Department of Energy.

ΔTherms = SavingFactor x Size of Pool

Where

Savings factor 	= dependant on pool location and listed in table below:

| Location | Therm / sq-ft |
| --- | --- |
| Indoor | 2.61 |
| Outdoor | 1.01 |

Size of Pool 	= custom input

###### Water Impact Descriptions and Calculation

ΔWater (gallons) = WaterSavingFactor x Size of Pool

Where

WaterSavingFactor = Water savings for this measure dependant on pool location and listed in table below:

| Location | Annual Savings Gal / sq-ft |
| --- | --- |
| Indoor | 15.28 |
| Outdoor | 8.94 |

Size of Pool 	= Custom input

###### Deemed O&M Cost Adjustment Calculation

There are no O&M cost adjustments for this measure.

###### Measure code: CI-HWE-PLCV-V03-200101

###### Review Deadline: 1/1/2025

### Tankless Water Heater – Measure combined with 4.3.1 Water Heater in Version 8

### Ozone Laundry

###### Description

A new ozone laundry system(s) is added-on to new or existing commercial washing machine(s) using hot water heated with natural gas. The system generates ozone (O3), a naturally occurring molecule, which helps clean fabrics by chemically reacting with soils in cold water. Adding an ozone laundry system(s) will reduce the amount of chemicals, detergents, and hot water needed to wash linens. Using ozone also reduces the total amount of water consumed, saving even more in energy.

Natural gas energy savings will be achieved at the hot water heater/boiler as they will be required to produce less hot water to wash each load of laundry. The decrease in hot water usage will increase cold water usage, but overall water usage at the facility will decrease.

Electric savings can be realized through reduced washer cycle length and reduced pumping load at the boiler feeding the commercial washers.  The increased usage associated with operating the ozone system should also be accounted for when determining total kWh impact. Data reviewed for this measure characterization indicated that pumping savings should be accounted for, but washer savings and ozone generator consumption are comparatively so small that they can be ignored.

The reduced washer cycle length may decrease the dampness of the clothes when they move to the dryer. This can result in shorter runtimes which result in gas and electrical savings. However, at this time, there is inconclusive evidence that energy savings are achieved from reduced dryer runtimes so the resulting dryer effects are not included in this analysis. Additionally, there would be challenges verifying that dryer savings will be achieved throughout the life of the equipment.

This incentive only applies to the following facilities with on-premise laundry operations:

  - Hotels/motels

  - Fitness and recreational sports centers.

  - Healthcare (excluding hospitals)

  - Assisted living facilities

  - Laundromats

Ozone laundry system(s) could create significant energy savings opportunities at other larger facility types with on-premise laundry operations (such as correctional facilities, universities, and staff laundries), however, the results included in this analysis are based heavily on past project data for the applicable facility types listed above and may not apply to facilities outside of this list due to variances in number of loads and average pound (lbs.)-capacity per project site.  Projects at these facilities should continue to be evaluated through custom programs and the applicable facility types and the resulting analysis should be updated based on new information.

Laundromats are the only application where number of washing units needs to be used to calculate total site energy savings. All other applications use site assumptions to calculate total site savings.

This measure was developed to be applicable to the following program types:  TOS, RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

A new ozone laundry system(s) is added-on to new or existing commercial washing machine(s) using hot water heated with natural gas. The ozone laundry system(s) must transfer ozone into the water through:

- Venturi Injection

- Bubble Diffusion

- Additional applications may be considered upon program review and approval on a case by case basis

- For laundromats, the ozone laundry system(s) must be connected to both the hot and cold water inlets of the clothes washing machine(s) so that hot water is no longer provided to the clothes washer.

###### Definition of Baseline Equipment

The base case equipment is a conventional washing machine system with no ozone generator installed. The washing machines are provided hot water from a gas-fired boiler.

###### Deemed Lifetime of Efficient Equipment

The measure equipment effective useful life (EUL) is estimated at 10 years based on typical lifetime of the ozone generator’s corona discharge unit.

###### Deemed Measure Cost

The actual measure costs should be used if available. If not, the following deemed values should be used:

| Application | Deemed Measure Cost |
| --- | --- |
| Laundromat | $25.53 / lbs capacity |
| Hotel/Motel | $79.84 / lbs capacity |
| Fitness and Recreation |  |
| Healthcare |  |
| Assisted Living |  |

###### Loadshape

Loadshape C53 – Flat

###### Coincidence Factor

Past project documentation and data collection is not sufficient to determine a coincidence factor for this measure. Value should continue to be studied and monitored through additional studies due to limited data points used for this determination.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Electric savings can be realized through reduced washer cycle length and reduced pumping load at the boiler feeding the commercial washers. There is also an increased usage associated with operating the ozone system. Data reviewed for this measure characterization indicated that while pumping savings is significant and should be accounted for, washer savings and ozone generator consumption are negligible, counter each other out and are well within the margin of error so these are not included to simplify the characterization.

∆kWhPUMP = HP * HPCONVERSION * Hours * %water_savings

Where:

∆kWhPUMP	= Electric savings from reduced pumping load

HP 		= Brake horsepower of boiler feed water pump;

= Actual, or use 5 HP if unknown

HPCONVERSION	= Conversion from Horsepower to Kilowatt

= 0.746

Hours 		= Actual associated boiler feed water pump hours

= Must be a custom calculation for laundromats, but 800 hours can be used for other applications if unknown

%water_savings 	= water reduction factor: how much more efficient an ozone injection washing machine is compared to a typical conventional washing machine as a rate of hot and cold water reduction.

| Application | %water_savings |
| --- | --- |
| Laundromat | 10% |
| Hotel/Motel | 25% |
| Fitness and Recreation |  |
| Healthcare |  |
| Assisted Living |  |

Using defaults above:

∆kWhPUMP_LAUNDROMAT	= 5 * 0.746 * Hours * 0.10

= 0.373 kWh * Hours

∆kWhPUMP_All OTHER  	= 5 * 0.746 * 800 * 0.25

= 746 kWh

Default per pound:		= ∆kWhPUMP  / Lbs-Capacity

Where:

Lbs-Capacity 	= Total washer capacity measured in pounds of laundry

| Application | Lbs-Capacity |
| --- | --- |
| Laundromat | Actual combined capacity of ozone connected washers |
| Hotel/Motel | 254.38 lbs per site |
| Fitness and Recreation |  |
| Healthcare |  |
| Assisted Living |  |

∆kWhPUMPALL OTHERS per pound 	= 746/254.38

= 2.93 kWh/lb

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure, but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater total

Where:

ΔWater (gallons)LAUNDROMAT	  	= 239 * Lbs_Capacity

ΔWater (gallons)ALL OTHERS		= 464,946

Ewater total		= IL Total Water Energy Factor (kWh/Million Gallons)

=5,010

Deemed savings using defaults:

ΔkWhwater_LAUNDROMAT 	= (239 * Lbs-Cpacity)/1,000,000 * 5,010

ΔkWhwater_ALL OTHERS 	= 464,946/1,000,000 * 5,010

= 2,329 kWh

###### Summer Coincident Peak Demand Savings

Past project documentation and data collection is not sufficient to determine summer coincident peak demand savings for this measure. Value should continue to be studied and monitored through additional studies due to limited data points used for this determination.  In absence of site-specific data, the summer coincident peak demand savings should be assumed to be zero.

∆kW 	= 0

###### Natural Gas Savings

∆Therm 	= 	ThermBaseline * %hot_water_savings

Where:

∆Therm 		= Gas savings resulting from a reduction in hot water use, in therm.

ThermBaseline 	= Annual Baseline Gas Consumption

= WHE * WUtiliz * WUsage_hot

Where:

WHE 	= water heating energy: energy required to heat the hot water used

= 0.00885 therm/gallon

WUtiliz 	= washer utilitzation factor: the annual pounds of clothes washed per year

= actual, if unknown the values below:

| Application | WUtiliz |
| --- | --- |
| Laundromat | 2,190 cycles per year * Lbs-Capacity |
| Hotel/Motel | 916,150 lbs (Approx. 4,745 cycles per year) per site |
| Fitness and Recreation |  |
| Healthcare |  |
| Assisted Living |  |

WUsage_hot	= hot water usage factor: how much hot water a typical conventional washing machine utilizes, normalized per pounds of clothes washed

| Application | WUsage_hot |
| --- | --- |
| Laundromat | 0.64 gallons/lb |
| Hotel/Motel | 1.19 gallons/lb |
| Fitness and Recreation |  |
| Healthcare |  |
| Assisted Living |  |

Using defaults above:

ThermBaseline_LAUNDROMAT	= 0.00885 * (2,190 cycles per year * Lbs-Capacity) * 0.64

= 12.4 therms * Lbs-Capacity

ThermBaseline_ALL OTHERS	= 0.00885 * 916,150 * 1.19

= 9648 therms

%hot_water_savings 	= hot water reduction factor: how much more efficient an ozone injection washing machine is, compared to a typical conventional washing machine, as a rate of hot water reduction

| Application | %hot_water_savings |
| --- | --- |
| Laundromat | 100% |
| Hotel/Motel | 81% |
| Fitness and Recreation |  |
| Healthcare |  |
| Assisted Living |  |

Savings using defaults above:

∆Therm 			= ThermBaseline * %hot_water_savings

∆ThermLAUNDROMAT		= 12.4 * Lbs-Capacity * 100%

= 12.4 therms * Lbs-Capacity

∆ThermALL OTHER 		= 9648 * 81%

= 7815 therms per site

Default per lb capacity:

∆ThermLAUNDROMAT / lb		= 12.4 * Lbs-Capacity / lb capacity

= 12.4 therms / lb

∆Therm ALL OTHER / lb		= 7815 / 254.38

= 30.7 therms / lb

###### Water Impact Descriptions and Calculation

The water savings calculations listed here account for the combination of hot and cold water used. Savings calculations for this measure were based on the reduction in total water use from implementing an ozone washing system to the base case. There are three main components in obtaining this value:

ΔWater (gallons) = WUsage * WUtiliz * %water_savings

Where:

ΔWater (gallons)	= reduction in total water use from implementing an ozone washing system to the base case

WUsage	= water usage factor: amount of total water used by a conventional washing machine normalized per unit of clothes washed

WUsageLAUNDROMATS = 1.09 gallons / lbs laundry

WUsageALL OTHERS = 2.03  gallons/lbs laundry

WUtiliz 	= washer utilization factor: the annual pounds of clothes washed per year

= actual, if unknown use the values below:

| Application | WUtiliz |
| --- | --- |
| Laundromat | 2,190 cycles per year * Lbs-Capacity |
| Hotel/Motel | 916,150 lbs (Approx. 4,745 cycles per year) per site |
| Fitness and Recreation |  |
| Healthcare |  |
| Assisted Living |  |

%water_savings 	= water reduction factor: how much more efficient an ozone injection washing machine is compared to a typical conventional washing machine as a rate of hot and cold water reduction.

| Application | %water_savings |
| --- | --- |
| Laundromat | 10% |
| Hotel/Motel | 25% |
| Fitness and Recreation |  |
| Healthcare |  |
| Assisted Living |  |

Savings using defaults above:

∆Water		= WUsage * WUtiliz * %water_savings

∆Water LAUNDROMATS	= 1.09 * WUtiliz * 0.1

= 1.09 * (2,190 * Lbs-Capacity) * 0.1

= 239 * Lbs-Capacity

∆Water ALL OTHERS		= 2.03 * 916,150 * 0.25

= 464,946 gallons per site

Default per pound:

∆WaterLAUNDROMATS / lb capacity 	= (239 * Lbs-Capacity) / lb-capacity

= 239 gallons/lb

∆ Water ALL OTHERS / lb-capacity 	= 464,946 / 254.38

= 1,828 gallons / lb

###### Deemed O&M Cost Adjustment Calculation

Maintenance is required for the following components annually:

- Ozone Generator: filter replacement, check valve replacement, fuse replacement, reaction chamber inspection/cleaning, reaction chamber o-ring replacement

- Air Preparation – Heat Regenerative: replacement of two medias

- Air Preparation – Oxygen Concentrators: filter replacement, pressure relief valve replacement, compressor rebuild

- Venturi Injector: check valve replacement

Maintenance is expected to cost $0.79 / lbs capacity.

###### Sources

1   "Lodging Report", December 2008, California Travel & Tourism Commission, http://tourism.visitcalifornia.com/media/uploads/files/editor/Research/CaliforniaTourism_200812.pdf

2   "Health, United States, 2008" Table 120, U.S. Department of Health & Human Services, Centers for Disease Control & Prevention, National Center for Health Statistics, http://www.cdc.gov/nchs/data/hus/hus08.pdf#120

3   Fourth Quarter 2008 Facts and Fictures, California Department of Corrections & Rehabilitation (CDCR), http://www.cdcr.ca.gov/Divisions_Boards/Adult_Operations/docs/Fourth_Quarter_2008_Facts_and_Figures.pdf

4   Jail Profile Survey (2008), California Department of Corrections & Rehabilitation (CDCR), http://www.cdcr.ca.gov/Divisions_Boards/CSA/FSO/Docs/2008_4th_Qtr_JPS_full_report.pdf

5      DEER2011_NTGR_2012-05-16.xls from  DEER Database for Energy-Efficient Resources; Version 2011 4.01

Under: DEER2011 Update Documentation linked at: DEER2011 Update Net-To-Gross table Cells: T56 and U56

6   The Benefits of Ozone in Hospitality On-Premise Laundry Operations, PG&E Emerging Technologies Program, Application Assessment Report #0802, April 2009.

7   Federal Register, Vol. 52, No. 166

8  2009 ASHRAE Handbook – Fundamentals, Thermodynamic Properties of Water at Saturation, Section 1.1 (Table 3), 2009

9 Table 2 through 6: Excel file summarizing data collected from existing ozone laundry projects that received incentives under the NRR-DR program

10 DOE Technical Support Document Chapter 6, 2010 https://www.regulations.gov/contentStreamer?documentId=EERE-2006-STD-0127-0118&attachmentNumber=8&disposition=attachment&contentType=pdf

11 GTI Residential Ozone Laundry Field Demonstration (May 2018)

###### Measure Code CI-HWE-OZLD-V06-220101

###### Review Deadline: 1/1/2023

### Multifamily Central Domestic Hot Water Plants

###### Description

This measure covers multifamily central domestic hot water (DHW) plants with thermal efficiencies greater than or equal to 88%. This measure is applicable to any combination of boilers and storage tanks provided the thermal efficiency of the boilers is greater than 88%. Plants providing other than solely DHW are not applicable to this measure.

This measure was developed to be applicable to the following program types:  TOS, NC, ER.

If applied to other program types, the measure savings should be verified.

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

###### Definition of Efficient Equipment

To qualify the boiler(s) must have a Thermal Efficiency of 88% or greater and supply domestic hot water to multi-family buildings.

###### Definition of Baseline Equipment

For TOS the baseline boiler is assumed to have a Thermal Efficiency of 80%.

For Early Replacement the savings are calculated between existing unit and efficient unit consumption during the remaining life of the existing unit, and between new baseline unit as above and efficient unit consumption for the remainder of the measure life.

###### Deemed Lifetime of Efficient Equipment

The measure life for the domestic hot water boilers is 15 years.

###### Deemed Measure Cost

TOS: The actual install cost should be used for the efficient case, minus the baseline cost assumption provided below:

| Capacity Range | Baseline Installed Cost per kBtuh |
| --- | --- |
| <300kBtuh | $65 per kBTUh |
| 300 – 2500 kBtuh | $38 per kBTUh |
| >2500 kBtuh | $32 per kBTUh |

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

There are no anticipated electrical savings from this measure.

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

Time of Sale:

ΔTherms		= Hot Water Savings + Standby Loss Savings

= [(MFHH * #Units * GPD * Days/yr * עWater * (Tout – Tin) * (1/Eff_base – 1/Eff_ee)) / 100,000] + [((SL * Hours/yr * (1/Eff_base – 1/Eff_ee)) / 100,000]

Early Replacment:

ΔTherms for remaining life of existing unit (1st 5 years):

= [(MFHH * #Units * GPD * Days/yr * עWater * (Tout – Tin) * (1/Eff_exist – 1/Eff_ee)) / 100,000] + [((SL * Hours/yr * (1/Eff_exist – 1/Eff_ee)) / 100,000]

ΔTherms for remaining measure life (next 10 years):

= [(MFHH * #Units * GPD * Days/yr * עWater * (Tout – Tin) * (1/Eff_base – 1/Eff_ee)) / 100,000] + [((SL * Hours/yr * (1/Eff_base – 1/Eff_ee)) / 100,000]

Where:

MFHH 		= number of people in Multi-Family household

= Actual. If unknown assume 2.1 persons/unit

#Units 		= Number of units served by hot water boiler

= Actual

GPD 		= Gallons of hot water used per person per day

= Actual. If unknown assume 17.6 gallons per person per day

Days/yr 		= 365.25

עWater 		= Specific Weight of Water

= 8.33 gal/lb

Tout 		= tank temperature of hot water

= 125°F or custom

Tin 		= Incoming water temperature from well or municiple system

= 50.7°F

Eff_base 	= thermal efficiency of base unit

= 80%

Eff_ee 		= thermal efficiency of efficient unit complying with this measure

= Actual. If unknown assume 88%

Eff_exist		= thermal efficiency of existing unit

= Actual. If unknown assume 73%

SL 		= Standby Loss

= (Input rating / 800) + (110 * √Tank Volume).

Input rating 	= Name plate input capacity in Btuh

Tank Volume 	= Rated volume of the tank in gallons

Hours / yr  	= 8766 hours

100,000 		= btu/therm

Time of Sale:

For example, an 88% 1000 gallon boiler with 150,000 Btuh input rating installed serving 50 units.

ΔTherms	= Hot Water Savings + Standby Loss Savings

= [(MFHH * #Units * GPD * Days/yr * עWater * (Tout – Tin) * (1/Eff_base – 1/Eff_ee)) / 100,000] + [((SL * Hours/yr * (1/Eff_base – 1/Eff_ee)) / 100,000]

=[(2.1 * 50 * 17.6 * 8.33 * 365.25 * 1.0 * (125-50.7) * (1/0.8 – 1/0.88)) / 100000] + [((150000/800 + (110 * √1000)) * 8766 * (1/0.8 – 1/0.88)) / 100000]

= 475 + 37

= 512 therms

Early Replacement:

For example, an 88% 1000 gallon boiler with 150,000 Btuh input rating installed serving 50 units replaces a working unit with unknown efficiency.

ΔTherms for remaining life of existing unit (1st 5 years):

=[(2.1 * 50 * 17.6 * 8.33 * 365.25 * 1.0 * (125-50.7) * (1/0.73 – 1/0.88)) / 100000] + [((150000/800 + (110 * √1000)) * 8766 * (1/0.73 – 1/0.88)) / 100000]

= 975 + 75

= 1050 therms

ΔTherms for remaining measure life (next 10 years):

= 475 + 37 (as above)

= 512 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure code: CI-HWE-MDHW-V05-220101

###### Review Deadline: 1/1/2023

### Controls for Central Domestic Hot Water

###### Description

Demand control recirculation pumps seek to reduce inefficiency by combining control via temperature and demand inputs, whereby the controller will not activate the recirculation pump unless both (a) the recirculation loop return water has dropped below a prescribed temperature (e.g. 100°F) and (b) a CDHW demand is sensed as water flow through the CDHW system.

This measure was developed to be applicable to the following program types: TOS, RF, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Re-circulating pump shall cycle on based on (a) the recirculation loop return water dropping below a prescribed temperature (e.g. 100°F) and (b) a CDHW demand is sensed as water flow through the CDHW system.

###### Definition of Baseline Equipment

The base case for this measure category are existing, un-controlled Recirculation Pumps on gas-fired Central Domestic Hot Water Systems.

###### Deemed Lifetime of Efficient Equipment

The effective useful life is 15 years.

###### Deemed Measure Cost

The average cost of the demand controller circulation kit is $1,442 with an installation cost of $768 for a total measure cost of $2,210.

###### Loadshape

###### Loadshape C02 - Non-Residential Electric DHW

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Deemed at 1,103 kWh.

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

Gas savings for this measure can be calculated by using site specific boiler size and boiler usage information or deemed values are provided based on number of rooms for Dormitories and number of apartments for Multi-Family buildings.

∆Therms 	= Boiler Input Capacity * (tnormal occ * Rnormal occ + tlow occ * Rlow occ) / 100,000

Where:

Boiler Input Capacity	= Input capacity of the Domestic Hot Water boiler in BTU/hr.

= If the facility uses the same boiler for space heat and domestic hot water, estimate the boiler input capacity for only domestic hot water loads. If this cannot be estimated, use 22.75% of total boiler input capacity for Multi-Family Buildings, 16.48% of total boiler input capacity for Dormitories , and 12.33% of total boiler input capacity for Hotels/Motels, as domestic hot water load.

= If unknown capcity use 4,938 BTU/hr per room for Dormitories, 12,493 BTU/hr per apartment for Multi-Family Buildings, and 3,696 BTU/hr per room for Hotels/Motels.

tnormal occ	= Total operating hours of domestic hot water burner, when  the facility has normal occupancy. If unknown, assume 1,688 hours for Dormitories, 2,089 hours for Multi-Family buildings, and 2,428 hours for Hotels/Motels.

tlow occ	= Total operating hours of domestic hot water burner, when the facility has low occupancy. If unknown, assume 520 hours for Dormitories, 0 hours for Multi-Family buildings, and 0 hours for Hotels/Motels.

Rnormal occ	= Reduction(%) in total operating hours of domestic hot water burner, due to installed central domestic hot water controls, during normal occupancy period.

= 22.44% for Dormitories

= 24.02% for Multi-Family Buildings

= 13.44% for Hotels/Motels

Rlow occ	= Reduction(%) in total operating hours of domestic hot water burner, due to installed central domestic hot water controls, during low occupancy period.

= 44.57% for Dormitories

= 0% for Multi-Family Buildings

= 0% for Hotels/Motels

Based on defaults above:

∆Therms 	= 30.1 * number of rooms (for Dormitories)

= 62.7 * number of apartments (for Multi-Family buildings)

= 12.06 * number of rooms (Hotels/Motels)

For example, a dormitory building has a 400,000 BTU/hr boiler whose burner operates for an estimated 580 hours during vacation months and 1,300 hours during regular occupancy months.  Savings from installing central domestic hot water controls in this building are -

∆Therms = 400,000 BTU/hr * (1,300 * 0.2244 + 580 * 0.4457) / 100,000

= 2,200.9 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HWE-CDHW-V03-220101

###### Review Deadline: 1/1/2025

### Heat Recovery Grease Trap Filter

###### Description

A heat recovery grease trap filter combines grease filters and a heat exchanger to recover heat leaving kitchen hoods. As a direct replacement for conventional hood mounted filters in commercial kitchens, they are plumbed to the domestic hot water system to provide preheating energy to incoming water.

This measure was developed to be applicable to the following program types: NC and RF. If applied to other program types, the measure savings should be verified. For NC projects, this measure may be applicable if code requirements are otherwise satisfied.

###### Definition of Efficient Equipment

Grease filters with heat exchangers carrying domestic hot water in kitchen exhaust air ducts.

###### Definition of Baseline Equipment

Kitchen exhaust air duct with constant air flow and no heat recovery.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years.

###### Deemed Measure Cost

Full installation costs, including plumbing materials, labor and any associated controls, should be used for screening purposes.

###### Loadshape

Loadshape C01 - Commercial Electric Cooking

###### Coincidence Factor

Summer Peak Coincidence Factor for measure is provided below for different building type:

| Location | CF CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.36 |
| Unknown | 0.40 |

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

For electric hot water heaters:

ΔkWh   = [(Meal/Day * HW/Meal * Days/Year) * lbs/gal * BTU/lb.°F * (ΔT/filter * Qty_Filter) * 0.00293] /(ηHeaterElec)

Where:

Meal/Day 	= Average number of meals served per day. If not directly available, see Table 1.

HW/Meal 	= Hot water required per meal

= 3 gal/meal

Days/Year 	= Number of days kitchen operates per year. If not directly available, see Table 1.

Lbs/gal		= weight of water

= 8.3 lbs/gal

BTU/lb.°F	= Specific heat of water

= 1.0

ΔT/filter		= Temperature difference of domestic water across each filter

= 5.8°F/filter

Qty_Filter 	= Number of heat recovery grease trap filters installed. If not directly available, see Table 1.

Commercial Kitchen Load based on Building Type

| Building Type | Meals/Day | Assumed days/Year | Number of Filters |
| --- | --- | --- | --- |
| Primary School | 400 | 312 | 2 |
| Secondary School | 600 | 312 | 3 |
| Quick Service Restaurant | 800 | 312 | 5 |
| Full Service Restaurant | 780 | 312 | 4 |
| Large Hotel | 780 | 356 | 4 |
| Hospital | 800 | 356 | 4 |

ηHeaterElec	= Efficiency of the Electric water heater.

= Actual. If unknown, for retrofit use the table C404.2 in IECC 2012. For new construction use the active code at time the permit was issued.

###### Summer Coincident Peak Demand Savings

ΔkW = ΔkWh/Hours * CF

Where:

Hours		= Hours of operation of kitchen exhaust air fan. If not directly available use:

| Building Type | Kitchen Exhaust Fan Annual Operating Hours |
| --- | --- |
| Primary School | 4,056 |
| Secondary School | 4,056 |
| Quick Service Restaurant | 5,616 |
| Full Service Restaurant | 5,616 |
| Large Hotel | 5,340 |
| Hospital | 3,916 |

CF	= Summer Peak Coincidence Factor for measure:

| Location | CF CF |
| --- | --- |
| Fast Food Limited Menu | 0.32 |
| Fast Food Expanded Menu | 0.41 |
| Pizza | 0.46 |
| Full Service Limited Menu | 0.51 |
| Full Service Expanded Menu | 0.36 |
| Cafeteria | 0.36 |
| Unknown | 0.40 |

###### Natural Gas Savings

For natural gas hot water heaters:

ΔTherm	= [(Meal/Day * HW/Meal * Days/Year) * lbs/gal * BTU/lb .°F * (ΔT/filter * Qty_Filter] / (ηHeaterGas * 100,000)

Where:

ηHeaterGas		= Efficiency of the Gas water heater. If not directly available, use:

= Actual. If unknown, for retrofit use the table C404.2 in IECC 2012. For new construction use the active code at time the permit was issued.

Other variables as above.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

O&M savings may result from reduced filter and hood cleaning frequencies. More research should be done to understand any potential savings and the associated value.

###### Measure Code: CI-HWE-GRTF-V02-200601

###### Review Deadline: 1/1/2024

### DHW Boiler Tune-up

###### Description

Domestic hot water (DHW) boilers provide hot water for bathrooms, kitchens, tubs and other appliances. Several commercial and industrial facilities such as multi-family buildings, lodging and restaurants have a separate hot water boiler serving DHW loads. Unlike space heating boilers, DHW boilers operate year round, which means they have a greater need to be properly maintained and tuned up.

This measure calculates savings for tuning up a DHW boiler to improve its efficiency and reduce its consumption. A boiler tune-up involves cleaning/inspecting burners, burner nozzles and combustion chambers, adjusting air flow and burner gas input to reduce stack temperatures, and checking venting and safety controls.  A pre- and post- tune up combustion efficiency ticket (from combustion analyzer) can be used to confirm the improvement in boiler efficiency.

Boilers that serve only a DHW load are eligible for this measure.

This measure was developed to be applicable to the following program types: RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the facility must, as applicable, complete the tune-up requirements listed below, by approved technician:

- Measure combustion efficiency using an electronic flue gas analyzer

- Adjust airflow and reduce excessive stack temperatures

- Adjust burner and gas input, manual or motorized draft control

- Check for proper venting

- Complete visual inspection of system piping and insulation

- Check safety controls

- Check adequacy of combustion air intake

- Clean fireside surfaces.

- Inspect all refractory. Patch and wash coat as required.

- Inspect gaskets on front and rear doors and replace as necessary.

- Seal and close front and rear doors properly.

- Clean low and auxiliary low water cut-off controls, then re-install using new gaskets.

- Clean plugs in control piping.

- Remove all hand hole and man hole plates. Flush boiler with water to remove loose scale and sediment.

- Replace all hand hole and man hole plates with new gaskets.

- Open feedwater tank manway, inspect and clean as required. Replace manway plate with new gasket.

- Clean burner and burner pilot.

- Check pilot electrode and adjust or replace.

- Clean air damper and blower assembly.

- Clean motor starter contacts and check operation.

- Make necessary adjustments to burner for proper combustion.

- Perform all flame safeguard and safety trip checks.

- Check all hand hole plates and man hole plates for leaks at normal operating temperatures and pressures.

- Troubleshoot any boiler system problems as requested by on-site personnel

###### Definition of Baseline Equipment

The baseline condition of this measure is a boiler that has not had a tune-up within the past 36 months.

###### Deemed Lifetime of Efficient Equipment

The life of this measure is 3 years.

###### Deemed Measure Cost

The cost of this measure is $0.83/MBtu/hr per tune-up.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

ΔTherms =  ((Tout - Tin) * HotWaterUseGallon * γwater * 1 * (1/Effbefore – 1/Effafter))/100,000

Where:

Tout			= Hot water storage tank temperature

= 125°F

Tin			= Incoming water temperature from well or municipal system

= 54°F

HotWaterUseGallon	= Estimated annual hot water consumption (gallons)

= Actual if possible to provide reasonable custom estimate. If not, the following

methods are provided to develop an estimate:

- Consumption per usable storage tank capacity

= Capacity * Consumption/cap

Where:

Capacity		= Usable capacity of hot water storage tank in gallons

= Actual

Consumption/cap = Estimate of consumption per gallon of usable tank    capacity, based on building type:

| Building Type | Consumption/Cap |
| --- | --- |
| Convenience | 528 |
| Education | 568 |
| Grocery | 528 |
| Health | 788 |
| Large Office | 511 |
| Large Retail | 528 |
| Lodging | 715 |
| Other Commercial | 341 |
| Restaurant | 622 |
| Small Office | 511 |
| Small Retail | 528 |
| Warehouse | 341 |
| Nursing | 672 |
| Multi-Family | 894 |

- Consumption per unit area by building type

= (Area/1000) * Consumption/1,000 sq.ft.

Where:

Area  	= Area in sq.ft that is served by DHW boiler

= Actual

Consumption/1,000 sq.ft. = Estimate of DHW consumption per 1,000 sq.ft. based on building type:

| Building Type | Consumption/1,000 sq.ft. |
| --- | --- |
| Convenience | 4,594 |
| Education | 7,285 |
| Grocery | 697 |
| Health | 24,540 |
| Large Office | 1,818 |
| Large Retail | 1,354 |
| Lodging | 29,548 |
| Other Commercial | 3,941 |
| Restaurant | 44,439 |
| Small Office | 1,540 |
| Small Retail | 6,111 |
| Warehouse | 1,239 |
| Nursing | 30,503 |
| Multi-Family | 15,434 |

γwater		= Specific weight capacity of water (lb/gal)

= 8.33 lbs/gal

1	= Specific heat of water (Btu/lb.°F)

Effbefore                    = Efficiency of the boiler before tune-up

Effafter                      = Efficiency of the boiler after tune-up

100,000                  =  Converts Btu to therms

Note: Contractors should select a mid-level firing rate that appropriately represents the average building operating condition over the course of the year and take readings at a consistent firing rate for pre and post tune-up.

For example, tune up of a DHW Boiler heating a 100 gallon storage tank in a nursing home, measuring 80% AFUE prior to tune up and 82.2% AFUE after.

∆Therms =  ((Tout - Tin) * HotWaterUseGallon * γwater * 1 * (1/Effbefore – 1/Effafter))/100,000

=  ((125 - 54) * (100 * 672) * 8.33 * 1 * (1/0.8 – 1/0.822))/100,000

= 13.3 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HWE-DBTU-V01-180101

###### Review Deadline: 1/1/2024

### Tunnel Washers

###### Description

Laundry equipment can be found at a variety of facilities, including hospitals, hotels, health clubs, penitentiaries, and others. Typically, these facilities use conventional batch washing machines for laundering their linens, towels, napkins and tablecloths, and uniforms. The uniformity of the feedstocks makes them good candidates for conversion to a continuous-batch tunnel washing machine system, which ultimately utilizes less water and detergent than conventional systems. The water savings are ultimately based on a comparison of the water efficiencies between the baseline and efficient equipment (measured in gallons of water per pound of laundry).

###### Definition of Efficient Equipment

A tunnel washing machine utilizes a porous Archimedes screw to move laundry and wash water in opposite (or counterflow) directions. The laundry travels in the upslope direction, while the wash water travels downslope through the holes in the Archimedes screw. The laundry gets progressively cleaner as it travels up the screw, while the wash water gets progressively dirtier as it travels down the screw. The screw can be programmed to intermittently change direction, to provide additional agitation. The mechanical action of the screw and travel path of the wash water through holes helps significantly with the cleaning action of the tunnel washer, allowing a reduction in the amount of detergent and rinse water required.

In contrast to the baseline equipment, the tunnel washer reuses the “rinse” water from the top section of the tunnel into the lower “wash” water sections, along with the gradual introduction of detergent. The continuous counterflow of laundry and wash water ultimately results in a more water-efficient system.

Tunnel washers also utilize automated PLC computer controls to constantly monitor water temperatures in each section of the tunnel and to automate the introduction of fresh water and detergent. The speed of the Archimedes screw can adjust for the varying dirt load of the laundry input. The computer system can typically collect performance data (gallons of water, pounds of detergent, pounds of laundry) over time to continuous evaluate system efficiency.

Tunnel washers can utilize either a hydraulic press extractor to “squeeze” water out of the linen or a more conventional centrifugal extractor that spins the linen to remove the water.

Tunnel washers can also reduce manhours required to process the laundry, as a staff is not required to manually load and unload each batch. The continuous feed of laundry in a tunnel washing machine system requires less labor and reduces the potential for injury from sticking hand and arms into a conventional washing machine drum.

Tunnel washers are quite large compared to conventional washers and require a significant footprint in the facility. In addition, they require approximately 12 feet of ceiling clearance above the top of the tunnel washer for proper installation.

###### Definition of Baseline Equipment

A traditional batch washing machine has discrete washing and rinsing cycles, wherein the water gets completely drained at the end of each cycle.

Typical top-loading washing machines used in homes and laundromats use approximately 40 gallons of water per load. This equates to 20 gallons for the wash cycle and 20 gallons for the rinse cycle. Some facilities will even utilize a second rinse cycle. The vertical axis design requires enough water in the drum to suspend the fabric in the soapy water.

The next step up in efficiency is a front-loading (or horizontal axis) washing machines. They typically use 20 to 30 gallons of water per load. This equates to 10-15 gallons for the wash cycle and 10-15 gallons for the rinse cycle.

Larger horizontal-axis washing machines can consume up to 45 gallons of water per load, equating to 22 gallons for the wash cycle and 22 gallons for the rinse cycle.

###### Deemed Lifetime of Efficient Equipment

The life of this measure is assumed to be 15 years for a new tunnel washing machine.

###### Deemed Measure Cost

The actual cost of the measure should be used.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

Energy savings from conversion from conventional washing machines to tunnel washing machines are the result of reduced water consumption and reduced natural gas consumption from heating water. There are indirect electric energy savings from reduced potable water treatment and wastewater treatment.

###### Electric Energy Savings

The electric energy savings are based indirectly on the reduced electricity usage attributed to the water savings from the tunnel washing machine. By applying an “Energy Factor”, the water savings (in gallons/year) can be converted to electricity savings (in kWh/year). This “Energy Factor” considers the electric energy requirements of water treatment plants and water distribution infrastructure, and wastewater treatment and distribution infrastructure.

The methodology for estimating water savings is as follows:

ΔWater = [BWME – TWME] x PLD x ADPY

ΔWater = 	Total Water Savings (gallons/year)

BWME = 	Baseline Washing Machine Efficiency (gal of water / lb. of laundry)

TWME =		Tunnel Washing Machine Efficiency (gal of water / lb. of laundry)

PLD = 		Pounds of Laundry Per Day (lb. laundry/day)

ADPY = 		Annual Days Per Year (days/year)

The values for BWME and TWME should be taken from actual equipment specifications or actual measurements (water flow meters and mechanical scales).

Typical values for TWME can be range from 0.75-1.0 gal. of water/lb. of laundry. Some equipment vendors have claimed TWME approaching 0.3-0.4 gal. of water/lb. of laundry. For the purposes of this measure, a TWME value of 0.87 gal. of water/lb. of laundry will be used.

Typical values for BWME can range from 1.8-3.0 gal. of water/lb. of laundry. For the purposes of this measure, a BWME value of 2.03 gal. of water/lb. of laundry will be used.

The PLD is specific to each individual facility. An occupied hotel room typically produces 11 pounds of laundry per day. An occupied hospital bed likely produces a similar amount of laundry load. The laundry loads of restaurants, health clubs, prisons, and other facilities need to be quantified using actual facility data.

The PLD can also be estimated from the Ozone Laundry Measure in the IL TRM, section 4.3.6. This measure gives a Washer Utilization Factor (Wutil) of 916,150 pounds/year of laundry for a typical facility. Assuming 365 days/year of laundry activity, this would give a PLD of 2,508 pounds of laundry per day.

The ADPY is often 365 days per year for facilities that never shut down, including hospitals, hotels, and prisons. Other facilities may have regular shutdown periods, so the ADPY value should be adjusted as necessary.

The electricity savings for this measure can be calculated by applying the energy factor to the ΔWater. This EF considers savings from both potable water treatment and wastewater treatment.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater total

Where

Ewater total = IL Total Water Energy Factor (kWh/Million Gallons)

=5,010

For example, switching from conventional washing machine technology to tunnel washing machine technology, at a facility that processes the defined 916,150 pounds/year (Wutil) and is open every day of the year.

ΔWater = [BWME – TWME] x PLD x ADPY

= [(2.03 – 0.87) gal. of water/lb. of laundry] x (916,150 lb. of laundry/year)

= 1,062,734 gal. of water/year

ΔkWhwater = ΔWater / 1,000,000 * Ewater total

= (1,062,734 gal. of water/year) / 1,000,000 * 5,010 kWh/million gallons

= 5,324 kWh/year

###### Summer Coincident Peak Demand Savings

Since the times of day from the water savings measure do not necessarily coincide with the times of day that the water treatment and distribution equipment is in use, the coincident peak demand savings cannot be determined.

###### Natural Gas Savings

With reduced water use by the installation of a tunnel washer, the DHW boiler used to heat the incoming water will  use significantly less gas. The below algorithm can be used to calculate natural gas savings for hot water heating.

ΔTherms =  ((Tout - Tin) * HotWaterReductionGallon * γwater * 1 * (1/Eff))/100,000

Where:

Tout			= Hot water storage tank temperature

= 125°F

Tin			= Incoming water temperature from well or municipal system

= 54°F

HotWaterReductionGallon	= Estimated annual hot water reduction (gallons)

= Actual custom estimate

γwater			= Specific weight capacity of water (lb/gal)

= 8.33 lbs/gal

1		= Specific heat of water (Btu/lb.°F)

Eff                   	 	= Efficiency of the boiler

= Use actual efficiency, otherwise use 80% AFUE

100,000                 		=  Converts Btu to therms

For example, a DHW Boiler with an efficiency of 80% AFUE heats a 100 gallon storage tank in a laundry facility using a tunnel washer. Use of the tunnel washer will save the original laundry site an estimated 1,062,734 gallons of water the below example savings:

∆Therms =  ((Tout - Tin) * HotWaterUseGallon * γwater * 1 * (1/Eff))/100,000

=  ((125 - 54) * 1,062,734 * 8.33 * 1 * (1/0.8))/100,000

= 7856 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

The water savings from the tunnel washing machines will help preserve water supplies, extend the life of water treatment and wastewater treatment plants. The reduction in detergent requirements will also have cost and environmental benefits.

###### Deemed O&M Cost Adjustment Calculation

Actual O&M cost adjustments should be used for this measure.

###### Measure Code: CI-HWE-TUWA-V01-200101

###### Review Deadline: 1/1/2024

### Tank Insulation

###### Description

This measure provides rebates for installation of 1” or 2” fiberglass, mineral fiber, or other types of insulation with similar properties to existing bare heated tanks for industrial and some commercial installations. Storage tanks can hold any heated material including, but not limited to, hot water, thermal oil, chemicals, and asphalt.

Default per square foot savings estimates are provided for both exposed indoor and outdoor storage tanks that are heated by heat transfer fluids including steam and thermal oil. Only systems heated with natural gas are eligible for this measure.

Indoor tanks require at least 1” of insulation and outdoor tanks must have at least 2 inches of insulation and include an all-weather protective jacket. New advanced insulating materials may be thinner and savings can be calculated with 3E Plus v4.1.

This measure was developed to be applicable to the following program types: RF (Retrofit), DI (Direct Install). If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient case is installing tank insulation to an uninsulated, heated material storage tank. Indoor tanks must have at least 1 inch of insulation (R-value of 2.1) and outdoor tanks must have at least 2” of insulation (R--value of 4.2) and include an all-weather protective jacket.

###### Definition of Baseline Equipment

The base case for savings estimates is a bare, steel tank. Other tank materials can be used to calculate savings with 3E Plus v4.1. Tanks are not required by mechanical codes to be insulated and are commonly found without any insulation.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 15 years.

###### Incremental Measure Cost

The incremental cost for this measure is $12/ft2.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

ΔTherms 	= [ESFb * Ab + ESFe * Ae] * Hours * LF * TRF / (100,000 * η)

Where:

ESFb 		= Energy savings factor from tank body defined as the difference in heat loss between an 			   insulated condition and a bare condition as found in table below [Btu/hr/ft2]

Ab 		= Area of tank body [ft2]

= Actual

ESFe 		= Energy savings factor from tank endcap(s) defined as the difference in heat loss between 			   an insulated condition and a bare condition as found in table below [Btu/hr/ft2]

Ae		= Area of endcap(s) [ft2]

= Combined area of endcaps if tank is oriented horizontally, separate areas if tank is 				   oriented vertically or only one endcap is insulated

= Actual

Hours		= Operating hours of heating system

= Actual

LF		= Load factor of heating system

= Annual gas consumption / (Hours * Nameplate Heating Capacity)

TRF		= Thermal Regain Factor for tank location and use, see table below. The Custom TRF option may be used on any tank location, including tank locations with deemed TRFs specifically listed in the table below, if supporting justification and calculations for the Custom TRF are provided.

May vary seasonally such as: TRF[summer] * summer hours + TRF[winter] * winter hours where TRF values reflecting summer and winter conditions are apportioned by the hours for those conditions. TRF may also be adjusted by building specific balance point temperature (BPT) and operating hours above and below that BPT.

| Tank Location | Assumed Regain | TRF, Thermal Regain Factor |
| --- | --- | --- |
| Outdoor | 0% | 1.0 |
| Indoor, conditioned, annual use (e.g. hot water or process loads), 55°F BPT | 45% | 0.55 |
| Indoor, semi-conditioned, annual use, 55°F BPT | 16% | 0.84 |
| Indoor, unconditioned spaces, (no heat transfer to conditioned space) | 0% | 1.0 |
| Location not specified - Commercial | 45% | 0.55 |
| Location not specified – Industrial | 16% | 0.84 |
| Custom | Custom | 1 – assumed regain |

100,000		= Conversion factor from BTUs to Therms

η 		= Efficiency of heating equipment used to heat tanks

= Actual, or if unknown assume 79%

The following table shows conductivities and maximum temperature ratings of similar insulation materials. The average value was used with 3EPlus software to generate the Energy Savings Factors used in the savings algorithm.

Table 1 – Insulation types

| Insulation Type | Conductivity (Btu.in/ hr.ft2.°F @ 300°F) | Max Temp (°F) |
| --- | --- | --- |
| Mineral Fiber Pipe and Tank Wrap | 0.48 | 650 |
| Mineral Fiber Board | 0.44 | 850 |
| Polyurethane | 0.5 | 400 |
| Average | 0.47 |  |

The tank surface temperature assumption depends on the system type. The following table should be used to select the appropriate Energy Savings Factor based on the fluid temperature:

Table 2 – Heating fluid temperatures

| System Type | Fluid Temperature Assumption (°F) |
| --- | --- |
| Low Pressure Steam (< 15 psi) | 225 |
| High Pressure Steam (> 60 psi) | 315 |
| Thermal Oil | 425 |

The energy savings factors (ESF) were developed using the 3E Plus v4.1 software program, and are derived as the difference in heat loss per square foot of a bare tank and an insulated tank. The energy savings analysis is based on adding 1” (indoor) or 2” (outdoor) thick insulation around bare tanks. Outdoor conditions are assumed to be 48.6°F with a wind speed of  5.0 mph. The thermal conductivity of tank insulation varies by material and temperature rating; to obtain a typical value, a range of materials allowed for this measure was averaged. For insulation materials not in the table above, use 3E Plus v4.1 software to calculate ESFb and ESFe.

Energy Savings Factors [Btu/hr/ft2]

|  |  | Low Pressure Steam | High Pressure Steam | Thermal Oil |
| --- | --- | --- | --- | --- |
| Vertical Tank - Body | Indoor | 290.2 | 559.0 | 991.8 |
|  | Outdoor | 373.4 | 666.0 | 1132.0 |
| Horizontal Tank - Body | Indoor | 290.2 | 559.0 | 991.8 |
|  | Outdoor | 373.4 | 666.0 | 1132.0 |
| Vertical Tank End - Top | Indoor | 336.8 | 642.8 | 783.9 |
|  | Outdoor | 426.3 | 756.2 | 1269.6 |
| Vertical Tank End - Bottom | Indoor | 189.8 | 380.0 | 712.1 |
|  | Outdoor | 288.1 | 515.7 | 897.3 |
| Horizontal Tank End | Indoor | 290.2 | 559.0 | 991.8 |
|  | Outdoor | 373.4 | 666.0 | 1132.0 |

For example, an outdoor, vertical, cylindrical tank with a  radius of 5 ft and height of 15 ft heated by a thermal oil heating system that is insulated around the body and top of the tank would save (assuming 4380 hours of operation, 70% load factor, and 78% efficient thermal oil heater):

ΔTherms 	= [ESFb * Ab + ESFe * Ae] * Hours * LF * TRF / (100,000 * η)

ESFb		= 1132.0 Btu/hr/ft2

Ab		= 2 * π * r * h

= 471.2 ft2

ESFe		= 1269.6 Btu/hr/ft2

Ae		= π * r2

= 78.5 ft2

Hours		= 4380

LF		= 0.7

TRF		= 1.0

η		= 0.78

ΔTherms	 = [1132.0 * 471.2 + 1269.6 * 78.5] * 4380 * 0.7 * 1 / (100,000 * 0.78)

= 24,884 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HWE-TKIN-V02-220101

###### Review Deadline: 1/1/2024

## HVAC End Use

Many of the commercial HVAC measures use equivalent full load hours (EFLH) to calculate heating and cooling savings.  The tables with these values are included in this section and referenced in each measure.

To calculate the updated EFLHs by building type and climate zone provided below, most of the eQuest models that were previously develop by a TAC Subcommittee utilizing building energy models originally developed for ComEd, were migrated to OpenStudio by a parametric calibration process.  The parametric runs were controlled with a genetic learning algorithm to characteristically adjust the seed models to achieve an acceptable target error against the existing eQuest model population.  The breadth of the characteristic variations were informed through a sensitivity analysis, the IL joint assessment survey, and the existing eQuest models.  The DOE prototypical models served as the initial seed model for most instances of calibration except were a direct map to available prototypes was unavailable.

The building characteristics of the eQuest models can be found in the reference table named “EFLH Building Descriptions Updated 2014-11-21.xlsx”. The OpenStudio models are based upon the DOE Prototypes described in NREL’s “U.S. Department of Energy Commercial Reference Building Models of the National Building Stock” and a calibration log file that documents all of the variations made to each model to get them calibrated is provided in “IL-Calibration-Log_2019-08-27.xlsx”. These documents and all the models are all available on the SharePoint site.

Note, for greenhouse boiler control measures, like Modulating Boiler Controls and/or Boiler Oxygen Trim Controls it is recommended to use methodology detailed in 4.4.21 Linkageless Boiler Controls for Space Heating and 4.4.22 Oxygen Trim Controls for Space Heating Boilers, respectively.

Note where a measure installation is within a building or application that does not fit with any of the defined building types below, the user should apply custom assumptions where it is reasonable to estimate them, else the building of best fit should be utilized.

Equivalent Full Load Hours for Heating (EFLHHeating) for Existing Buildings:

| Building Type | Heating EFLH Existing Buildings |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Assembly | 1,787 | 1,831 | 1,635 | 1,089 | 1,669 | eQuest |
| Assisted Living | 1,683 | 1,646 | 1,446 | 1,063 | 1,277 | eQuest |
| Auto Dealership | 2,981 | 2,950 | 2,694 | 2,368 | 2,437 | OpenStudio |
| College | 1,256 | 1,293 | 1,138 | 1,116 | 1,131 | OpenStudio |
| Convenience Store | 1,481 | 1,368 | 1,214 | 871 | 973 | eQuest |
| Drug Store | 2,848 | 2,947 | 2,568 | 2,362 | 2,516 | OpenStudio |
| Elementary School | 1,614 | 1,603 | 1,409 | 1,209 | 1,269 | OpenStudio |
| Emergency Services | 2,757 | 2,670 | 2,383 | 2,149 | 2,186 | OpenStudio |
| Garage | 985 | 969 | 852 | 680 | 752 | eQuest |
| Greenhouse – w/ Curtains | 4,320 | 4,059 | 3,493 | 2,996 | 2,933 | Virtual Grower 3.1 |
| Greenhouse – w/o Curtains | 4,344 | 4,081 | 3,513 | 3,012 | 2,949 | Virtual Grower 3.1 |
| Grocery | 1,467 | 1,551 | 1,364 | 1,367 | 1,375 | OpenStudio |
| Healthcare Clinic | 1,446 | 1,526 | 1,452 | 1,553 | 1,574 | OpenStudio |
| High School | 1,807 | 1,855 | 1,649 | 1,591 | 1,622 | OpenStudio |
| Hospital - CAV no econ | 1,216 | 1,220 | 1,072 | 1,001 | 1,028 | OpenStudio |
| Hospital - CAV econ | 1,387 | 1,398 | 1,252 | 1,222 | 1,269 | OpenStudio |
| Hospital - VAV econ | 665 | 697 | 628 | 646 | 615 | OpenStudio |
| Hospital - FCU | 1,622 | 1,571 | 1,374 | 1,220 | 1,281 | OpenStudio |
| Hotel/Motel | 1,597 | 1,634 | 1,468 | 1,376 | 1,451 | OpenStudio |
| Hotel/Motel - Common | 1,670 | 1,733 | 1,549 | 1,496 | 1,557 | OpenStudio |
| Hotel/Motel - Guest | 1,555 | 1,597 | 1,433 | 1,316 | 1,400 | OpenStudio |
| Manufacturing Facility | 1,048 | 1,013 | 939 | 567 | 634 | eQuest |
| MF - High Rise | 1,565 | 1,540 | 1,448 | 1,089 | 1,125 | OpenStudio |
| MF - High Rise - Common | 537 | 558 | 501 | 480 | 499 | OpenStudio |
| MF - High Rise - Residential | 1,665 | 1,666 | 1,512 | 1,145 | 1,207 | OpenStudio |
| MF - Mid Rise | 1,730 | 1,782 | 1,589 | 1,538 | 1,560 | OpenStudio |
| Movie Theater | 1,916 | 1,905 | 1,718 | 1,288 | 1,538 | eQuest |
| Office - High Rise - CAV no econ | 995 | 1,036 | 933 | 786 | 832 | OpenStudio |
| Office - High Rise - CAV econ | 1,001 | 1,051 | 929 | 803 | 851 | OpenStudio |
| Office - High Rise - VAV econ | 1,552 | 1,432 | 1,239 | 1,077 | 1,098 | OpenStudio |
| Office - High Rise - FCU | 1,015 | 993 | 899 | 773 | 809 | OpenStudio |
| Office - Low Rise | 2,825 | 2,625 | 2,365 | 2,007 | 2,040 | OpenStudio |
| Office - Mid Rise | 1,672 | 1,629 | 1,454 | 1,356 | 1,399 | OpenStudio |
| Religious Building | 1,603 | 1,504 | 1,440 | 1,054 | 1,205 | eQuest |
| Restaurant | 1,326 | 1,328 | 1,179 | 1,091 | 1,122 | OpenStudio |
| Retail - Department Store | 1,365 | 1,322 | 1,193 | 1,034 | 1,088 | OpenStudio |
| Retail - Strip Mall | 1,347 | 1,325 | 1,183 | 1,064 | 1,096 | OpenStudio |
| Warehouse | 1,285 | 1,286 | 1,180 | 1,147 | 1,224 | OpenStudio |
| Unknown | 1,709 | 1,678 | 1,508 | 1,287 | 1,411 | n/a |

Equivalent Full Load Hours for Heating (EFLHHeating) for New Construction:

| Building Type | Heating EFLH New Construction |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Auto Dealership | 1,286 | 1,185 | 1,279 | 1,138 | 1,078 | OpenStudio |
| College | 942 | 834 | 906 | 831 | 818 | OpenStudio |
| Drug Store | 1,023 | 930 | 1,017 | 889 | 822 | OpenStudio |
| Elementary School | 949 | 878 | 943 | 861 | 859 | OpenStudio |
| Emergency Services | 480 | 352 | 501 | 407 | 347 | OpenStudio |
| Grocery | 2,795 | 2,788 | 2,549 | 2,380 | 2,597 | OpenStudio |
| Healthcare Clinic | 1,534 | 1,417 | 1,555 | 1,395 | 1,371 | OpenStudio |
| High School | 1,502 | 1,549 | 1,368 | 1,283 | 1,299 | OpenStudio |
| Hospital - CAV no econ | 2,345 | 2,207 | 2,318 | 2,110 | 2,195 | OpenStudio |
| Hospital - CAV econ | 2,345 | 2,207 | 2,318 | 2,110 | 2,195 | OpenStudio |
| Hospital - VAV econ | 2,345 | 2,207 | 2,318 | 2,110 | 2,195 | OpenStudio |
| Hospital - FCU | 2,345 | 2,207 | 2,318 | 2,110 | 2,195 | OpenStudio |
| Hotel/Motel - Residential | 1,412 | 1,243 | 1,439 | 1,405 | 1,146 | OpenStudio |
| Hotel_Motel_Common | 1,554 | 1,415 | 1,519 | 1,410 | 1,361 | OpenStudio |
| Hotel_Motel_Guest | 1,538 | 1,083 | 1,554 | 1,381 | 987 | OpenStudio |
| MF - High Rise | 1,308 | 884 | 1,361 | 1,125 | 865 | OpenStudio |
| MF - High Rise - Common | 1,581 | 1,280 | 1,590 | 1,349 | 1,220 | OpenStudio |
| MF - High Rise - Residential | 1,352 | 946 | 1,413 | 1,174 | 917 | OpenStudio |
| MF - Mid Rise | 1,637 | 1,385 | 1,637 | 1,434 | 1,322 | OpenStudio |
| Office - High Rise - FCU | 987 | 870 | 1,001 | 893 | 837 | OpenStudio |
| Office - High Rise - VAV econ | 987 | 870 | 1,001 | 893 | 837 | OpenStudio |
| Office - Mid Rise | 867 | 759 | 892 | 792 | 701 | OpenStudio |
| Office - High Rise - CAV no econ | 967 | 854 | 971 | 876 | 804 | OpenStudio |
| Office Low Rise | 954 | 916 | 826 | 667 | 664 | OpenStudio |
| Restaurant | 787 | 797 | 671 | 811 | 820 | OpenStudio |
| Retail - Department Store | 1,286 | 1,185 | 1,279 | 1,138 | 1,078 | OpenStudio |
| Retail - Strip Mall | 973 | 867 | 972 | 857 | 777 | OpenStudio |
| Warehouse | 1,413 | 1,390 | 1,398 | 1,298 | 1,290 | OpenStudio |
| Unknown | 1,133 | 1,064 | 1,091 | 982 | 960 | n/a |

Equivalent Full Load Hours for Cooling (EFLHcooling) for Existing Buildings:

| Building Type | Cooling EFLH Existing Buildings |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Assembly | 725 | 796 | 937 | 1,183 | 932 | eQuest |
| Assisted Living | 1,475 | 1,457 | 1,773 | 2,110 | 1,811 | eQuest |
| Auto Dealership | 996 | 1,051 | 1,343 | 1,582 | 1,414 | OpenStudio |
| College | 572 | 564 | 676 | 776 | 613 | OpenStudio |
| Convenience Store | 1,088 | 1,067 | 1,368 | 1,541 | 1,371 | eQuest |
| Drug Store | 858 | 943 | 1,133 | 1,279 | 1,092 | OpenStudio |
| Elementary School | 834 | 837 | 999 | 1264 | 967 | OpenStudio |
| Emergency Services | 2,983 | 3,009 | 3,762 | 4,030 | 3,740 | OpenStudio |
| Garage | 934 | 974 | 1,226 | 1,582 | 1,383 | eQuest |
| Grocery | 826 | 914 | 1,151 | 1,329 | 1,240 | OpenStudio |
| Healthcare Clinic | 1,220 | 1,294 | 1,505 | 1,658 | 1,534 | OpenStudio |
| High School | 892 | 883 | 1,066 | 1,397 | 1,018 | OpenStudio |
| Hospital - CAV no econ | 1,719 | 1,799 | 2,068 | 2,238 | 2,066 | OpenStudio |
| Hospital - CAV econ | 1,267 | 1,302 | 1,604 | 1,798 | 1,592 | OpenStudio |
| Hospital - VAV econ | 3,313 | 3,332 | 3,458 | 3,546 | 3,311 | OpenStudio |
| Hospital - FCU | 1,575 | 1,562 | 1,921 | 1,979 | 1,812 | OpenStudio |
| Hotel/Motel | 1,106 | 1,148 | 1,453 | 1,605 | 1,435 | OpenStudio |
| Hotel/Motel - Common | 1,108 | 1,168 | 1,430 | 1,574 | 1,406 | OpenStudio |
| Hotel/Motel - Guest | 1,061 | 1,106 | 1,391 | 1,509 | 1,401 | OpenStudio |
| Manufacturing Facility | 1,010 | 1,055 | 1,209 | 1,453 | 1,273 | eQuest |
| MF - High Rise | 928 | 920 | 1,059 | 1,360 | 1,205 | OpenStudio |
| MF - High Rise - Common | 1,405 | 1,383 | 1,479 | 1,527 | 1,466 | OpenStudio |
| MF - High Rise - Residential | 764 | 807 | 976 | 1,216 | 1,147 | OpenStudio |
| MF - Mid Rise | 787 | 855 | 1,099 | 1,198 | 1,082 | OpenStudio |
| Movie Theater | 876 | 745 | 1,036 | 1,178 | 1,010 | eQuest |
| Office - High Rise - CAV no econ | 1,357 | 1,404 | 1,587 | 1,753 | 1,468 | OpenStudio |
| Office - High Rise - CAV econ | 922 | 937 | 1,138 | 1,274 | 1,000 | OpenStudio |
| Office - High Rise - VAV econ | 847 | 887 | 991 | 1,092 | 893 | OpenStudio |
| Office - High Rise - FCU | 1,083 | 1,116 | 1,269 | 1,348 | 1,266 | OpenStudio |
| Office - Low Rise | 1,796 | 1,790 | 2,233 | 2,342 | 2,219 | OpenStudio |
| Office - Mid Rise | 1,128 | 1,153 | 1,360 | 1,461 | 1,356 | OpenStudio |
| Religious Building | 861 | 817 | 967 | 1,159 | 1,067 | eQuest |
| Restaurant | 990 | 1,021 | 1,273 | 1,411 | 1,290 | OpenStudio |
| Retail - Department Store | 639 | 640 | 775 | 936 | 812 | OpenStudio |
| Retail - Strip Mall | 697 | 720 | 915 | 998 | 930 | OpenStudio |
| Warehouse | 252 | 265 | 363 | 377 | 379 | OpenStudio |
| Unknown | 1,003 | 1,019 | 1,230 | 1,403 | 1,236 | n/a |

Equivalent Full Load Hours for Cooling (EFLHcooling) for New Construction:

| Building Type | Cooling EFLH New Construction |  |  |  |  | Model Source |
| --- | --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  |
| Auto Dealership | 806 | 923 | 792 | 938 | 1,028 | OpenStudio |
| College | 925 | 990 | 994 | 1,156 | 1,217 | OpenStudio |
| Drug Store | 813 | 931 | 744 | 836 | 1,083 | OpenStudio |
| Elementary School | 724 | 821 | 732 | 753 | 999 | OpenStudio |
| Emergency Services | 379 | 429 | 371 | 423 | 576 | OpenStudio |
| Grocery | 643 | 568 | 569 | 562 | 511 | OpenStudio |
| Healthcare Clinic | 1,964 | 2,093 | 1,932 | 2,055 | 2,221 | OpenStudio |
| High School | 1,807 | 1,642 | 2,093 | 2,292 | 1,830 | OpenStudio |
| Hospital - CAV no econ | 2,627 | 2,751 | 2,662 | 2,782 | 2,962 | OpenStudio |
| Hospital - CAV econ | 2,627 | 2,751 | 2,662 | 2,782 | 2,962 | OpenStudio |
| Hospital - VAV econ | 2,627 | 2,751 | 2,662 | 2,782 | 2,962 | OpenStudio |
| Hospital - FCU | 2,627 | 2,751 | 2,662 | 2,782 | 2,962 | OpenStudio |
| Hotel/Motel - Residential | 1,639 | 1,836 | 1,712 | 1,851 | 1,983 | OpenStudio |
| Hotel_Motel_Common | 2,343 | 2,472 | 2,286 | 2,400 | 2,590 | OpenStudio |
| Hotel_Motel_Guest | 788 | 1,024 | 846 | 1,073 | 1,164 | OpenStudio |
| MF - High Rise | 1,338 | 1,705 | 1,287 | 1,500 | 1,932 | OpenStudio |
| MF - High Rise - Common | 773 | 912 | 751 | 878 | 972 | OpenStudio |
| MF - High Rise - Residential | 1,299 | 1,663 | 1,245 | 1,451 | 1,882 | OpenStudio |
| MF - Mid Rise | 1,341 | 1,633 | 1,245 | 1,492 | 1,818 | OpenStudio |
| Office - High Rise - FCU | 1,296 | 1,465 | 1,281 | 1,477 | 1,574 | OpenStudio |
| Office - High Rise - VAV econ | 1,296 | 1,465 | 1,281 | 1,477 | 1,574 | OpenStudio |
| Office - High Rise - CAV no econ | 1,433 | 1,644 | 1,411 | 1,632 | 1,793 | OpenStudio |
| Office - High Rise - CAV econ | 1,361 | 1,375 | 1,604 | 1,715 | 1,617 | OpenStudio |
| Office - Mid Rise | 957 | 1,149 | 958 | 1,122 | 1,270 | OpenStudio |
| Office Low Rise | 947 | 989 | 1,090 | 1,302 | 1,076 | OpenStudio |
| Restaurant | 768 | 761 | 1,034 | 1,110 | 994 | OpenStudio |
| Retail - Department Store | 806 | 924 | 796 | 939 | 1,027 | OpenStudio |
| Retail - Strip Mall | 722 | 789 | 667 | 834 | 911 | OpenStudio |
| Warehouse | 389 | 522 | 408 | 527 | 567 | OpenStudio |
| Unknown | 984 | 1,045 | 1,047 | 1,177 | 1,176 | n/a |

### Air Conditioner Tune-up

###### Description

An air conditioning system that is operating as designed saves energy and provides adequate cooling and comfort to the conditioned space

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be a unitary or split system air conditioner at least 3 tons and preapproved by program. The measure requires that a certified technician performs the following items:

- Check refrigerant charge

- Identify and repair leaks if refrigerant charge is low

- Measure and record refrigerant pressures

- Measure and record temperature drop at indoor coil

- Clean condensate drain line

- Clean outdoor coil and straighten fins

- Clean indoor and outdoor fan blades

- Clean indoor coil with spray-on cleaner and straighten fins

- Repair damaged insulation – suction line

- Change air filter

- Measure and record blower amp draw

A copy of contractor invoices that detail the work performed to identify tune-up items, as well as additional labor and parts to improve/repair air conditioner performance must be submitted to the program.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline condition is assumed to be an AC system that that does not have a standing maintenance contract or a tune up within in the past 36 months.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 3 years.

###### Deemed Measure Cost

Tune-up costs can vary considerably, particularly if regrigerant leak detection, remediation and recharge is necessary. Actual invoiced tune-up costs should be used.

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWH	= (kBtu/hr) * [(1/EERbefore) – (1/EERafter)] * EFLH

Where:

kBtu/hr 	= capacity of the cooling equipment actually installed in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr).

=Actual

EERbefore	= Energy Efficiency Ratio of the baseline equipment prior to tune-up

=Actual

EERafter 	= Energy Efficiency Ratio of the baseline equipment after to tune-up

=Actual

EFLH 	= Equivalent Full Load Hours for cooling in Existing Buildings are provided in section 4.4 HVAC End Use

Where it is not possible or appropriate to perform Test in and Test out of the equipment, the following deemed methdology can be used:

ΔkWh	= (kBtu/hr) / EERbefore * EFLH * %Savings

Where:

%Savings	= Deemed percent savings per Tune-Up component. These are additive if condenser cleaning, evaporator cleaning and refrigerant charge correction are performed (totals provided below)

| Tune-Up Component | % savings |
| --- | --- |
| Condenser Cleaning | 6.10% |
| Evaporator Cleaning | 0.22% |
| Refrig. Charge Off. <=20% | 0.68% |
| Refrig. Charge Off. >20% | 8.44% |
| Combined (Refrig. Charge Off. <=20%) | 7.00% |
| Combined (Refrig. Charge Off. >20%) | 14.76% |

For example, a 12 EER 5-ton rooftop air conditioner on a department store in Rockford receives a tune-up that includes both condenser and evaporator cleaning:

ΔkWh 	= (5*12) / 12 * 1,392 * 6.32%

= 440 kWh

###### Summer Coincident Peak Demand Savings

ΔkWSSP 	= (kBtu/hr * (1/EERbefore - 1/EERafter)) * CFSSP

ΔkWPJM 	= (kBtu/hr * (1/ EERbefore - 1/EERafter)) * CFPJM

Where:

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Where it is not possible or appropriate to perform Test in and Test out of the equipment, the following deemed methdology can be used:

ΔkW	= (kBtu/hr) / EERbefore * %Savings * CF

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-ACTU-V06-210101

###### Review Deadline: 1/1/2025

### Space Heating Boiler Tune-up

###### Description

This measure is for a non-residential boiler that provides space heating.  The tune-up will improve boiler efficiency by cleaning and/or inspecting burners, combustion chamber, and burner nozzles.  Adjust air flow and reduce excessive stack temperatures, adjust burner and gas input.  Check venting, safety controls, and adequacy of combustion air intake.  Combustion efficiency should be measured before and after tune-up using an electronic flue gas analyzer.

###### Definition of Efficient Equipment

To qualify for this measure the facility must, as applicable, complete the tune-up requirements listed below by approved technician:

- Measure combustion efficiency using an electronic flue gas analyzer

- Adjust airflow and reduce excessive stack temperatures

- Adjust burner and gas input, manual or motorized draft control

- Check for proper venting

- Complete visual inspection of system piping and insulation

- Check safety controls

- Check adequacy of combustion air intake

- Clean fireside surfaces.

- Inspect all refractory. Patch and wash coat as required.*

- Inspect gaskets on front and rear doors and replace as necessary.*

- Seal and close front and rear doors properly.*

- Clean low and auxiliary low water cut-off controls, then re-install using new gaskets.*

- Clean plugs in control piping.*

- Remove all hand hole and manhole plates. Flush boiler with water to remove loose scale and sediment.*

- Replace all hand hole and manhole plates with new gaskets.*

- Open feedwater tank manway, inspect and clean as required. Replace manway plate with new gasket.*

- Clean burner and burner pilot.

- Check pilot electrode and adjust or replace.

- Clean air damper and blower assembly.

- Clean motor starter contacts and check operation.*

- Make necessary adjustments to burner for proper combustion.

- Perform all flame safeguard and safety trip checks.

- Check all hand hole plates and manhole plates for leaks at normal operating temperatures and pressures.

- Troubleshoot any boiler system problems as requested by on-site personnel

Note: Tune-up activities marked with an asterisk (*) are eligible to be performed by internal maintenance staff at periods of boiler shutdown.

###### Definition of Baseline Equipment

The baseline condition of this measure is a boiler that has not had a tune-up within the past 36 months.

###### Deemed Lifetime of Efficient Equipment

The life of this measure is 3 years.

###### Deemed Measure Cost

The cost of this measure is $0.83/MBtu/hr per tune-up

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms	=(Capacity * EFLH * (((Effbefore + Ei)/ Effbefore) – 1)) / 100,000

Where:

Capacity		= Boiler gas input size (Btu/hr)

= Custom

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings are provided in section 4.4 HVAC End Use

Effbefore		= Efficiency of the boiler before the tune-up

= Actual. Default value is 81.5%

Note: Contractors should select a mid-level firing rate that appropriately represents the average building operating condition over the course of the heating season and take readings at a consistent firing rate for pre and post tune-up.

Ei		= Efficiency improvement of the boiler tune-up measure

= Actual. Default value is 2.3%

100,000		= Converts Btu to therms

For example, a 1050 kBtu boiler in a Chicago high rise office records an efficiency prior to tune up of 81.5% AFUE and a 2.3% improvement in efficiency after tune up:

Δtherms = (1,050,000 * 2050 * ((0.815 + 0.023)/ 0.815 – 1)) /100,000

= 607 Therms

###### Summer Coincident Peak Demand Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-BLRT-V07-210101

###### Review Deadline: 1/1/2025

### Process Boiler Tune-up

###### Description

This measure is for a non-residential boiler for process loads.  For space heating, see measure 4.4.2. The tune-up will improve boiler efficiency by cleaning and/or inspecting burners, combustion chamber, and burner nozzles.  Adjust air flow and reduce excessive stack temperatures, adjust burner and gas input.  Check venting, safety controls, and adequacy of combustion air intake.  Combustion efficiency should be measured before and after tune-up using an electronic flue gas analyzer.

###### Definition of Efficient Equipment

To qualify for this measure the facility must, as applicable, complete the tune-up requirements by approved technician as specified below:

- Measure combustion efficiency using an electronic flue gas analyzer

- Adjust airflow and reduce excessive stack temperatures

- Adjust burner and gas input, manual or motorized draft control

- Check for proper venting

- Complete visual inspection of system piping and insulation

- Check safety controls

- Check adequacy of combustion air intake

- Clean fireside surfaces

- Inspect all refractory. Patch and wash coat as required.*

- Inspect gaskets on front and rear doors and replace as necessary.*

- Seal and close front and rear doors properly.*

- Clean low and auxiliary low water cut-off controls, then re-install using new gaskets.*

- Clean plugs in control piping.*

- Remove all hand hole and man hole plates. Flush boiler with water to remove loose scale and sediment.*

- Replace all hand hole and man hole plates with new gaskets.*

- Open feedwater tank manway, inspect and clean as required. Replace manway plate with new gasket.*

- Clean burner and burner pilot.

- Check pilot electrode and adjust or replace.

- Clean air damper and blower assembly.

- Clean motor starter contacts and check operation.*

- Make necessary adjustments to burner for proper combustion.

- Perform all flame safeguard and safety trip checks.

- Check all hand hole plates and man hole plates for leaks at normal operating temperatures and pressures.

- Troubleshoot any boiler system problems as reQuested by on-site personnel

Note: Tune-up activities marked with an asterisk (*) are eligible to be performed by internal maintenance staff at periods of boiler shutdown.

###### Definition of Baseline Equipment

The baseline condition of this measure is a boiler that has not had a tune-up within the past 36 months.

###### Deemed Lifetime of Efficient Equipment

The life of this measure is 3 years.

###### Deemed Measure Cost

The cost of this measure is $0.83/MBtu/hr per tune-up

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms	=((Capacity * 8766 * UF) / 100) * (1 - (Effpre / Effmeasured))

Where:

Capacity	= Boiler gas input size (kBtu/hr)

=Custom

UF 	= Utilization Factor

= 41.9%, or custom

Effpre 	= Boiler Combustion Efficiency Before Tune-Up

= Actual. Default value is 80.3%

Note: Contractors should select afiring rate that appropriately represents the average operating condition and take readings at a consistent firing rate for pre and post tune-up.

Effmeasured 	= Boiler Combustion Efficiency After Tune-Up

= Actual. Default value is 82.6%

100	=converstion from kBtu to therms

8766	= hours a year

For example, a 80.3% 1050 kBtu boiler is tuned-up resulting in final efficiency of 82.6%:

Δtherms		=((1050 * 8766 * 0.419) / 100) * (1 - (0.80.3 / 0.826))

= 1074 therms

###### Summer Coincident Peak Demand Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-PBTU-V06-210101

###### Review Deadline: 1/1/2025

### Boiler Lockout/Reset Controls

###### Description

This measure relates to improving combustion efficiency by adding controls to non-residential space heating boilers to vary the boiler entering water temperature relative to heating load as a function of the outdoor air temperature to save energy. Energy is saved by increasing the temperature difference between the water temperature entering the boiler in the boiler's heat exchanger and the boiler's burner flame temperature. The flame temperature remains the same while the water temperature leaving the boiler decreases with the decrease in heating load due to an increase in outside air temperature.  A lockout temperature is also set to prevent the boiler from turning on when it is above a certain temperature outdoors.

This measure was developed to be applicable to the following program types: RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Natural gas customer adding boiler reset controls capable of resetting the boiler supply water temperature in an inverse linear fashion with outdoor air temperature. Boiler lockout temperatures should be set to 55 °F at this time as well, to turn the boiler off when the temperature goes above a certain setpoint.

###### Definition of Baseline Equipment

Existing boiler without boiler reset controls, any size with constant hot water flow.

###### Deemed Lifetime of Efficient Equipment

The life of this measure is 16 years.

###### Deemed Measure Cost

The cost of this measure is $612.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms = Capacityinput * SF * EFLH / 100

Where:

Capacityinput 	= Boiler Input Capacity (kBtu/hr)

= custom

SF 	= Savings factor

= 8%, or custom

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings are provided in section 4.4 HVAC End Use

100	= conversion from kBtu to therms

For example, reset controls were installed on an 800 kBtu/hr boiler at a restaurant in Rockford, IL

ΔTherms = 800 * 0.08 * 1,350 / 100

= 864 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-BLRC-V04-210101

###### Review Deadline: 1/1/2024

### Condensing Unit Heaters

###### Description

This measure applies to a gas fired condensing unit heater installed in a commercial application.

This measure was developed to be applicable to the following program types: TOS, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be a condensing unit heater up to 300 MBH with a Thermal Efficiency > 90% and the heater must be vented, and condensate drained per manufacturer specifications. The unit must be replacing existing natural gas equipment.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline condition is assumed to be a non-condensing natural gas unit heater at end of life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental capital cost for a unit heater is equal to the input capacity in kBtu/h multiplied by $15.56

Incremental cost = Capacity * $15.56

Where:

Capacity		= Nominal rating of the input capacity of the new condensing unit heater in kBtu/hr

$15.56		= Incremental cost per kBtu/h of input capacity of a new condensing unit heater

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms	=((Capacity * EFLH * UF) / 100) * (1 / EffBase – 1 / EffEE)

Where:

Capacity	= Nominal rating of the input capacity of the new condensing unit heater in kBtu/hr

= Actual

UF 	= Utilization Factor

= 72.5%, or custom

EffBase 	= Combustion Efficiency of the baseline unit heater

= Default value is 80%

EffEE 	= Combustion Efficiency of the installed unit heater

= Actual. Default value is 90%

100	=converstion from kBtu to therms

EFLH	= Equivalent Full Load Hours for in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

For example, a 150 kBtu condensing unit heater with a combustion efficiency of 90% is installed in a garage in Rockford:

Δtherms		=((150 * 985 * 0.725) / 100) * (1 / 0.80 – 1 / 0.90)

= 149 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-CUHT-V02-220101

###### Review Deadline: 1/1/2027

### Electric Chiller

###### Description

This measure relates to the installation of a new electric chiller meeting the efficiency standards presented below. This measure could relate to the replacement of an existing unit at the end of its useful life, or the installation of a new system in an existing building (i.e. time of sale). Only single-chiller applications should be assessed with this methodology. The characterization is not suited for multiple chillers projects or chillers equipped with variable speed drives (VSDs).

This measure was developed to be applicable to the following program types: TOS, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to exceed the efficiency requirements defined by the program.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit (if unknown assume IECC 2015).

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 23 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is provided below:

| Air-Cooled Chiller Incremental Costs ($/Ton) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Capacity (Tons) | Efficient EER |  |  |  |
|  | 9.9 | 10.2 | 10.52 | 10.7 |
| 50 | $226 | $453 | $694 | $830 |
| 100 | $113 | $226 | $347 | $415 |
| 150 | $75 | $151 | $231 | $277 |
| 200 | $46 | $92 | $141 | $169 |
| 400 | $23 | $46 | $71 | $85 |

| Water-Cooled Scroll/Screw Chiller Incremental Costs ($/Ton) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Capacity (Tons) | Efficient kW/ton |  |  |  |  |  |  |
|  | 0.72 |  | 0.68 |  | 0.64 |  | 0.6 |
| 50 | $114 |  | $164 |  | N/a |  | N/a |
| 100 | $52 |  | $77 |  | N/a |  | N/a |
| 150 | N/a |  | N/a |  | N/a |  | N/a |
| 200 | N/a |  | N/a |  | $61 |  | $122 |
| 400 | N/a |  | N/a |  | N/a |  | $16 |
| Water-Cooled Centrifugal Chiller Incremental Costs ($/Ton) |  |  |  |  |  |  |  |
| Capacity (Tons) |  | Efficient kW/ton |  |  |  |  |  |
|  |  | 0.6 |  | 0.58 |  | 0.54 |  |
| 100 |  | $62 |  | $99 |  | $172 |  |
| 150 |  | $42 |  | $66 |  | $115 |  |
| 200 |  | $31 |  | $49 |  | $86 |  |
| 300 |  | N/a |  | N/a |  | $55 |  |
| 600 |  | N/a |  | N/a |  | $22 |  |

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.  Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWH	= TONS * ((IPLVbase) – (IPLVee)) * EFLH

Where:

TONS 	= chiller nominal cooling capacity in tons (note: 1 ton = 12,000 Btu/hr)

= Actual installed

IPLVbase = efficiency of baseline equipment expressed as Integrated Part Load Value(kW/ton). Chiller units are dependent on chiller type. See Chiller Units, Convertion Values  and Baseline Efficiency Values by Chiller Type and Capacity in the Reference Tables section.

IPLVee = efficiency of high efficiency equipment expressed as Integrated Part Load Value (kW/ton)

= Actual installed

EFLH 	= Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

For example, a 100 ton air-cooled electrically operated chiller with IPLV of 14 EER (0.86 kW/ton) and baseline EER of 12.5 (0.96 kW/ton) ,in a low-rise office building in Rockford with a building permit dated on 1/1/2015 would save:

ΔkWH	= 100 * ((0.96) – (0.86)) * 949

=  9,490 kWh

###### Summer Coincident Peak Demand Savings

ΔkWSSP 		= TONS * ((PEbase) – (PEee)) * CFSSP

ΔkWPJM 		= TONS * ((PEbase) – (PEee)) * CFPJM

Where:

PEbase		= Peak efficiency of baseline equipment expressed as Full Load (kW/ton)

PEee 		= Peak efficiency of high efficiency equipment expressed as Full Load (kW/ton)

=  Actual installed

CFSSP	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

For example, a 100 ton air-cooled electrically operated chiller with a peak efficiency of 1.05 kW/ton and a baseline peak efficiency of 1.2 kW/ton would save:

ΔkWSSP 		= 100 * (1.2 – 1.05) * 0.913

= 13.7 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Reference Tables

Chillers Ratings- Chillers are rated with different units depending on equipment type as shown below

| Equipment Type | Unit |
| --- | --- |
| Air cooled, electrically operated | EER |
| Water cooled, electrically operated, positive displacement (reciprocating) | kW/ton |
| Water cooled, electrically operated, positive displacement (rotary screw and scroll) | kW/ton |

In order to convert chiller equipment ratings to IPLV, the following relationships are provided:

kW/ton 	= 12 / EER

kW/ton	 = 12 / (COP x 3.412)

COP 		= EER / 3.412

COP		 = 12 / (kW/ton) / 3.412

EER 		= 12 / kW/ton

EER 		= COP x 3.412

2015 IECC Baseline Efficiency Values by Chiller Type and Capacity (effective 1/1/2016 to 3/30/2019)

2018 IECC Baseline Efficiency Values by Chiller Type and Capacity (effective 7/1/2019)

###### Measure Code: CI-HVC-CHIL-V07-200101

###### Review Deadline: 1/1/2023

### ENERGY STAR and CEE Tier 2 Room Air Conditioner

###### Description

This measure relates to the purchase and installation of a room air conditioning unit that meets either the ENERGY STAR or CEE Tier 2 minimum qualifying efficiency specifications, in place of a baseline unit meeting minimum Federal Standard efficiency ratings presented below:

| Product Class (Btu/H) | Federal Standard CEER, with louvered sides | Federal Standard CEER, without louvered sides | ENERGY STAR CEER, with louvered sides | ENERGY STAR CEER, without louvered sides | CEE Tier 2 CEER |
| --- | --- | --- | --- | --- | --- |
| < 8,000 | 11.0 | 10.0 | 12.1 | 11.0 | 12.7 |
| 8,000 to 10,999 | 10.9 | 9.6 | 12.0 | 10.6 | 12.5 |
| 11,000 to 13,999 |  | 9.5 |  | 10.5 |  |
| 14,000 to 19,999 | 10.7 | 9.3 | 11.8 | 10.2 | 12.3 |
| 20,000 to 27,999 | 9.4 | 9.4 | 10.3 | 10.3 | 10.8 |
| >= 28,000 | 9.0 |  | 9.9 |  | 10.4 |

| Casement | Federal Standard (CEER) | ENERGY STAR (CEER) |
| --- | --- | --- |
| Casement-only | 9.5 | 10.5 |
| Casement-slider | 10.4 | 11.4 |

| Reverse Cycle -Product Class (Btu/H) | Federal Standard CEER, with louvered sides | Federal Standard CEER, without louvered sides | ENERGY STAR CEER, with louvered sides | ENERGY STAR CEER, without louvered sides |
| --- | --- | --- | --- | --- |
| < 14,000 | N/A | 9.3 | N/A | 10.2 |
| >= 14,000 | N/A | 8.7 | N/A | 9.6 |
| < 20,000 | 9.8 | N/A | 10.8 | N/A |
| >= 20,000 | 9.3 | N/A | 10.2 | N/A |

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the new room air conditioning unit must meet the ENERGY STAR efficiency standards presented above.

###### Definition of Baseline Equipment

The baseline assumption is a new room air conditioning unit that meets the current minimum federal efficiency standards presented above.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 12 years.

###### Deemed Measure Cost

The incremental cost for this measure is assumed to be $40 for an ENERGY STAR unit and $100 for a CEE Tier 2 unit.

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.  Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Savings

###### Energy Savings

ΔkWh 	= (FLHRoomAC * Btu/H * (1/CEERbase - 1/CEERee))/1000

Where:

FLHRoomAC 	= Full Load Hours of room air conditioning unit

= Equivalent Full Load Hours for cooling in Existing Buildings are provided in section 4.4 HVAC End Use

Btu/H 		= Input capacity of unit

= Actual. If unknown assume 8500 Btu/hr

CEERbase 	= Combined Energy Efficiency Ratio of baseline unit

= As provided in tables above

CEERee 	= Combined Energy Efficiency Ratio of ENERGY STAR or CEE Super Efficient unit

= Actual. If unknown assume minimum qualifying standard as provided in tables above

For example, for an 8,500 Btu/H capacity ENERGY STAR unit, with louvered sides, in a unknown location in Rockford:

ΔkWHENERGY STAR	= (1133 * 8500 * (1/10.9 – 1/12.0)) / 1000

= 81.0 kWh

###### Summer Coincident Peak Demand Savings

ΔkW = Btu/H * ((1/CEERbase - 1/CEERee))/1000) * CF

Where:

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Other variable as defined above

For example for an 8,500 Btu/H capacity ENERGY STAR unit, with louvered sides, in Rockford during system peak

ΔkWENERGY STAR	= (8500 * (1/10.9 – 1/12.0)) / 1000 * 0.913

= 0.065 kW

###### Fossil Fuel Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-ESRA-V03-220101

###### Review Deadline: 1/1/2025

### Guest Room Energy Management (PTAC & PTHP)

###### Description

This measure applied to the installation of a temperature setback and lighting control system for individual guest rooms. The savings are achieved based on Guest Room Energy Management’s (GREM’s) ability to automatically adjust the guest room’s set temperatures and control the HVAC unit for various occupancy modes.

This measure was developed to be applicable to the following program types: TOS, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Guest room temperature set point must be controlled by automatic occupancy detectors or keycard that indicates the occupancy status of the room. During unoccupied periods the default setting for controlled units differs by at least 5 degrees from the operating set point. Theoretically, the control system may also be tied into other electric loads, such as lighting and plug loads to shut them off when occupancy is not sensed.  This measure bases savings on improved HVAC controls.  If system is connected to lighting and plug loads, additional savings would be realized.  The incentive is per guestroom controlled, rather than per sensor, for multi-room suites. Replacement or upgrades of existing occupancy-based controls are not eligible for an incentive.

###### Definition of Baseline Equipment

Guest room energy management thermostats replace manual heating/cooling temperature set-point and fan On/Off/Auto thermostat controls. Two possible baselines exist based on whether housekeeping staff are directed to set-back (or turn off) thermostats when rooms are not rented.

###### Deemed Lifetime of Efficient Equipment

The measure life for GREM is 15 years.

###### Deemed Measure Cost

$260/unit.

The IMC documented for this measure is $260 per room HVAC controller, which is the cost difference between a non-programmable thermostat and a GREM.

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

A coincidence factor is not used in the determination of coincident peak kW savings.

Algorithm

###### Calculation of Savings

Below are the annual kWh savings per installed EMS for different sizes and types of HVAC units. The savings are achieved based on GREM’s ability to automatically adjust the guest room’s set temperatures and control the HVAC unit to maintain set temperatures for various occupancy modes. Note that care should be taken in selecting a value consistent with actual baseline conditions (e.g., whether housekeeping staff are directed to set-back/turn-off the thermostats when rooms are unrented). Different values are provided for Motels and Hotels since significant differences in shell performance, number of external walls per room and typical heating and cooling efficiencies result in significantly different savings estimates. Energy savings estimates are derived using a prototypical EnergyPlus simulation of a motel and a hotel. Model outputs are normalized to the installed capacity and reported here as kWh/Ton, coincident peak kW/Ton and Therms/Ton.

###### Electric Energy Savings

| Climate Zone (City based upon) | Heating Source | Baseline | Electric Savings (kWh/Ton) |
| --- | --- | --- | --- |
| Motel Electric Energy Savings |  |  |  |
| 1 (Rockford) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 744 |
|  |  | No Housekeeping Setback | 1,786 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 63 |
|  |  | No Housekeeping Setback | 155 |
|  | PTHP | Housekeeping Setback | 385 |
|  |  | No Housekeeping Setback | 986 |
| 2 (Chicago) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 506 |
|  |  | No Housekeeping Setback | 1,582 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 51 |
|  |  | No Housekeeping Setback | 163 |
|  | PTHP | Housekeeping Setback | 211 |
|  |  | No Housekeeping Setback | 798 |
| 3 (Springfield) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 462 |
|  |  | No Housekeeping Setback | 1,382 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 65 |
|  |  | No Housekeeping Setback | 198 |
|  | PTHP | Housekeeping Setback | 202 |
|  |  | No Housekeeping Setback | 736 |
| 4 (Belleville) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 559 |
|  |  | No Housekeeping Setback | 1,877 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 85 |
|  |  | No Housekeeping Setback | 287 |
|  | PTHP | Housekeeping Setback | 260 |
|  |  | No Housekeeping Setback | 1,023 |
| 5 (Marion-Williamson) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 388 |
|  |  | No Housekeeping Setback | 1,339 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 81 |
|  |  | No Housekeeping Setback | 274 |
|  | PTHP | Housekeeping Setback | 174 |
|  |  | No Housekeeping Setback | 682 |
| Hotel Electric Energy Savings |  |  |  |
| 1 (Rockford) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 204 |
|  |  | No Housekeeping Setback | 345 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 121 |
|  |  | No Housekeeping Setback | 197 |
|  | PTHP | Housekeeping Setback | 152 |
|  |  | No Housekeeping Setback | 253 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 177 |
|  |  | No Housekeeping Setback | 296 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 94 |
|  |  | No Housekeeping Setback | 148 |
| 2 (Chicago) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 188 |
|  |  | No Housekeeping Setback | 342 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 119 |
|  |  | No Housekeeping Setback | 195 |
|  | PTHP | Housekeeping Setback | 145 |
|  |  | No Housekeeping Setback | 250 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 161 |
|  |  | No Housekeeping Setback | 294 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 92 |
|  |  | No Housekeeping Setback | 147 |
| 3 (Springfield) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 182 |
|  |  | No Housekeeping Setback | 291 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 123 |
|  |  | No Housekeeping Setback | 197 |
|  | PTHP | Housekeeping Setback | 145 |
|  |  | No Housekeeping Setback | 233 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 153 |
|  |  | No Housekeeping Setback | 240 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 94 |
|  |  | No Housekeeping Setback | 146 |
| 4 (Belleville) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 182 |
|  |  | No Housekeeping Setback | 308 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 125 |
|  |  | No Housekeeping Setback | 199 |
|  | PTHP | Housekeeping Setback | 146 |
|  |  | No Housekeeping Setback | 240 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 152 |
|  |  | No Housekeeping Setback | 255 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 95 |
|  |  | No Housekeeping Setback | 147 |
| 5 (Marion-Williamson) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 171 |
|  |  | No Housekeeping Setback | 295 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 122 |
|  |  | No Housekeeping Setback | 199 |
|  | PTHP | Housekeeping Setback | 140 |
|  |  | No Housekeeping Setback | 235 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 141 |
|  |  | No Housekeeping Setback | 243 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 92 |
|  |  | No Housekeeping Setback | 146 |

###### Summer Coincident Peak Demand Savings

| Motel Coincident Peak Demand Savings |  |  |  |
| --- | --- | --- | --- |
| Climate Zone (City based upon) | Heating Source | Baseline | Coincident Peak Demand Savings (kW/Ton) |
| 1 (Rockford) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.17 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.17 |
|  | PTHP | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.17 |
| 2 (Chicago) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.06 |
|  |  | No Housekeeping Setback | 0.17 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.06 |
|  |  | No Housekeeping Setback | 0.17 |
|  | PTHP | Housekeeping Setback | 0.06 |
|  |  | No Housekeeping Setback | 0.17 |
| 3 (Springfield) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.07 |
|  |  | No Housekeeping Setback | 0.17 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.07 |
|  |  | No Housekeeping Setback | 0.17 |
|  | PTHP | Housekeeping Setback | 0.07 |
|  |  | No Housekeeping Setback | 0.17 |
| 4 (Belleville) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.10 |
|  |  | No Housekeeping Setback | 0.28 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.10 |
|  |  | No Housekeeping Setback | 0.28 |
|  | PTHP | Housekeeping Setback | 0.10 |
|  |  | No Housekeeping Setback | 0.28 |
| 5 (Marion-Williamson) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.21 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.21 |
|  | PTHP | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.21 |

| Hotel Coincident Peak Demand Savings |  |  |  |
| --- | --- | --- | --- |
| Climate Zone (City based upon) | Heating Source | Baseline | Coincident Peak Demand Savings (kW/Ton) |
| 1 (Rockford) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTHP | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.08 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.08 |
| 2 (Chicago) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.07 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.07 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTHP | Housekeeping Setback | 0.07 |
|  |  | No Housekeeping Setback | 0.11 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.07 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.07 |
| 3 (Springfield) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTHP | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.07 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.07 |
| 4 (Belleville) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTHP | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.08 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.08 |
| 5 (Marion-Williamson) | PTAC w/ Electric Resistance Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTAC w/ Gas Heating | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | PTHP | Housekeeping Setback | 0.08 |
|  |  | No Housekeeping Setback | 0.11 |
|  | Central Hot Water Fan Coil w/ Electric Resistance Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.08 |
|  | Central Hot Water Fan Coil w/ Gas Heating | Housekeeping Setback | 0.05 |
|  |  | No Housekeeping Setback | 0.08 |

###### Natural Gas Energy Savings

For PTACs with gas heating:

| Motel Natural Gas Energy Savings |  |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone (City based upon) |  | Baseline | Gas Savings (Therms/Ton) |  |
| 1 (Rockford) |  | Housekeeping Setback | 30 |  |
|  |  | No Housekeeping Setback | 71 |  |
| 2 (Chicago) |  | Housekeeping Setback | 20 |  |
|  |  | No Housekeeping Setback | 62 |  |
| 3 (Springfield) |  | Housekeeping Setback | 17 |  |
|  |  | No Housekeeping Setback | 52 |  |
| 4 (Belleville) |  | Housekeeping Setback | 21 |  |
|  |  | No Housekeeping Setback | 70 |  |
| 5 (Marion-Williamson) |  | Housekeeping Setback | 13 |  |
|  |  | No Housekeeping Setback | 47 |  |
| Hotel Natural Gas Energy Savings |  |  |  |  |  |  |
| Climate Zone (City based upon) | Heating Source |  |  | Baseline |  | Gas Savings (Therms/Ton) |
| 1 (Rockford) | PTAC w/ Gas Heating |  |  | Housekeeping Setback |  | 3.6 |
|  |  |  |  | No Housekeeping Setback |  | 6.4 |
|  | Central Hot Water Fan Coil w/ Gas Heating |  |  | Housekeeping Setback |  | 3.6 |
|  |  |  |  | No Housekeeping Setback |  | 6.4 |
| 2 (Chicago) | PTAC w/ Gas Heating |  |  | Housekeeping Setback |  | 3.0 |
|  |  |  |  | No Housekeeping Setback |  | 6.5 |
|  | Central Hot Water Fan Coil w/ Gas Heating |  |  | Housekeeping Setback |  | 3.0 |
|  |  |  |  | No Housekeeping Setback |  | 6.5 |
| 3 (Springfield) | PTAC w/ Gas Heating |  |  | Housekeeping Setback |  | 2.6 |
|  |  |  |  | No Housekeeping Setback |  | 4.1 |
|  | Central Hot Water Fan Coil w/ Gas Heating |  |  | Housekeeping Setback |  | 2.6 |
|  |  |  |  | No Housekeeping Setback |  | 4.1 |
| 4 (Belleville) | PTAC w/ Gas Heating |  |  | Housekeeping Setback |  | 2.5 |
|  |  |  |  | No Housekeeping Setback |  | 4.8 |
|  | Central Hot Water Fan Coil w/ Gas Heating |  |  | Housekeeping Setback |  | 2.5 |
|  |  |  |  | No Housekeeping Setback |  | 4.8 |
| 5 (Marion-Williamson) | PTAC w/ Gas Heating |  |  | Housekeeping Setback |  | 2.1 |
|  |  |  |  | No Housekeeping Setback |  | 4.2 |
|  | Central Hot Water Fan Coil w/ Gas Heating |  |  | Housekeeping Setback |  | 2.1 |
|  |  |  |  | No Housekeeping Setback |  | 4.2 |

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-GREM-V06-0601

###### Review Deadline: 1/1/2026

### Air and Water Source Heat Pump Systems

###### Description

This measure applies to the installation of high-efficiency air cooled and water source heat pump systems. This measure could apply to replacing an existing unit at the end of its useful life, or installation of a new unit in a new or existing building.

This measure was developed to be applicable to the following program types: TOS, NC, EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be a high-efficiency air cooled or water source, heat pump system that exceeds the baseline and meets program requirements.

###### Definition of Baseline Equipment

New construction / Time of Sale: To calculate savings with an electric baseline, the baseline equipment is assumed to be a standard-efficiency air cooled or water source heat pump system that meets the Code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher) in effect on the date of equipment purchase (if date unknown assume current Code minimum).  The rating conditions for the baseline and efficient equipment efficiencies must be equivalent.

To calculate savings with a furnace/ AC baseline, the baseline equipment is assumed to meet the Code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher).

Where unknown, the baseline should be determined via EM&V and the algorithms are provided to allow savings to be calculated from any baseline condition.

Note: IECC 2018 is baseline for all New Construction permits from July 1, 2019 and if permit date unknown.

Note: new Federal Standards affecting heat pumps become effective January 1, 2023.

Early replacement / Retrofit: The baseline for this measure is the efficiency of the existing heating and cooling equipment for the assumed remaining useful life of the existing unit and a new baseline heating and cooling system meeting the code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher) for the remainder of the measure life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 16 years.

Remaining life of existing equipment is assumed to be 6 years for ASHP and Central AC, 6 years for furnace, 8 years for boilers and 16 years for electric resistance.

###### Deemed Measure Cost

New Construction and Time of Sale: For analysis purposes, the incremental capital cost for this measure is assumed as $100 per ton for air-cooled units. The incremental cost for all other equipment types should be determined on a site-specific basis.

Early Replacement: The actual full installation cost of the Heat Pump (including any necessary electrical or distribution upgrades required) should be used. The assumed deferred cost of replacing existing equipment with a new baseline unit should also be incorporated.

###### Loadshape

Loadshape C05 - Commercial Electric Heating and Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.  Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Non fuel switch measures:

For units with cooling capacities less than 65 kBtu/hr:

ΔkWh	= Annual kWh Savingscool + Annual kWh Savingsheat

Annual kWh Savingscool 	= (Capacitycool * EFLHcool * (1/SEERbase – 1/(SEERee * SEERadj))/1000

Annual kWh Savingsheat 	= (HeatLoad * (1/HSPFbase – 1/(HSPFee * HSPFadj))/1000

For units with cooling capacities equal to or greater than 65 kBtu/hr:

ΔkWh	= Annual kWh Savingscool + Annual kWh Savingsheat

Annual kWh Savingscool 	= (Capacitycool * EFLHcool * (1/EERbase – 1/EERee))/1000

Annual kWh Savingsheat 	= (HeatLoad/3412 * (1/COPbase – 1/COPee)

Fuel switch measures:

Fuel switch measures must produce positive total lifecycle fuel savings (i.e., reduction in Btus at the premesis) in order to qualify. This is determined as follows (note for early replacement measures the lifetime savings should be calculated by calculating savings for the remaining useful life of the existing equipment and for the remaining measure life):

SiteEnergySavings (MMBTUs)	=  GasHeatReplaced + FurnaceFanSavings – HPSiteHeatConsumed + HPSiteCoolingImpact

GasHeatReplaced		= (HeatLoad * 1/AFUEbase) / 1,000,000

FurnaceFanSavings	= (FurnaceFlag * HeatLoad * 1/AFUEbase * Fe) / 1,000,000

For units with cooling capacities less than 65 kBtu/hr:

HPSiteHeatConsumed	= ((HeatLoad * (1/(HSPFee * HSPFadj))) /1000  * 3412)/ 1,000,000

HPSiteCoolingImpact 	= (FLHcool * Capacitycool * (1/SEERbase - 1/(SEERee * SEERadj)))/1000 * 3412/ 1,000,000

For units with cooling capacities greater than 65 kBtu/hr:

HPSiteHeatConsumed	= (HeatLoad * (1/COPee)) / 1,000,000

HPSiteCoolingImpact 	= (FLHcool * Capacitycool * (1/EER_base - 1/EER_ee))/1000 * 3412/ 1,000,000

If SiteEnergySavings calculated above is positive, the measure is eligible.

The appropriate savings claim is dependent on which utilities are supporting the measure as provided in a table below:

| Measure supported by: | Electric Utility claims (kWh): | Gas Utility claims (therms): |
| --- | --- | --- |
| Electric utility only | SiteEnergySavings * 1,000,000/3,412 | N/A |
| Electric and gas utility (Note utilities may make alternative agreements to how savings are allocated as long as total MMBtu savings remains the same). | %IncentiveElectric * SiteEnergySavings * 1,000,000/3,412 | %IncentiveGas * SiteEnergySavings * 10 |
| Gas utility only | N/A | SiteEnergySavings * 10 |

Note for Early Replacement measures, the efficiency terms of the existing unit should be used for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 6 years for furnace, 8 years for boilers, 15 years for electric resistance), and the efficiency terms for a new baseline unit should be used for the remaining years of the measure. See assumptions below.

Where:

Capacitycool	= input capacity of the cooling equipment in Btu per hour (1 ton of cooling capacity equals 12,000 Btu/hr).

= Actual installed

SEERbase	=Seasonal Energy Efficiency Ratio of the baseline equipment

= SEER from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code).

SEERee		= Seasonal Energy Efficiency Ratio of the energy efficient equipment.

= Actual installed

SEERadj		= Adjustment percentage to account for in-situ performance of the unit

= [(0.805 × EEReeSEERee+0.367]

EFLHcool	= Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

HSPFbase	= Heating Seasonal Performance Factor of the baseline equipment

= HSPF from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code).

HSPFee	= Heating Seasonal Performance Factor of the energy efficient equipment.

= Actual installed. If rating is COP, HSPF = COP * 3.413

HSPFadj		= Adjustment percentage to account for the heating capacity ratio of the efficient unit

= 17 °F Capacity47 °F Capacity × 0.158+0.899

= Actual using AHRI lookup values for efficient unit heating capacities rated at 17°F and 47°F.  If not available assume 1.

EFLHheat	= heating mode equivalent full load hours in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

EERbase	= Energy Efficiency Ratio of the baseline equipment

= EER from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). For air-cooled units < 65 kBtu/hr, assume the following conversion from SEER to EER for calculation of peak savings:

EER = (-0.02 * SEER2) + (1.12 * SEER)

EERee	= Energy Efficiency Ratio of the energy efficient equipment. For air-cooled units < 65 kBtu/hr, if the actual EERee is unknown, assume the conversion from SEER to EER as provided above.

= Actual installed

HeatLoad	= Calculated heat load for the building

= EFLHheat * Capacityheat

EFLHheat	= heating mode equivalent full load hours in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

Capacityheat	= input capacity of the heat pump equipment in Btu per hour.

= Actual installed

3412		= Btu per kWh.

COPbase	= coefficient of performance of the baseline equipment

= COP from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). If rating is HSPF, COP = HSPF / 3.413

COPee 		= coefficient of performance of the energy efficient equipment.

= Actual installed. If rating is HSPF, COP = HSPF / 3.413

AFUEbase 	= Baseline Annual Fuel Utilization Efficiency Rating. For early replacement measures, use actual AFUE rating for the remaining useful life of the existing equipment (6 years for furnace, 8 years for boilers). For new systems (time of sale, new construction or remaining years of early replacement), use appropriate code level efficiency.

FurnaceFlag	= 1 if system replaced is a gas furnace, 0 if not.

Fe		= Furnace Fan energy consumption as a percentage of annual fuel consumption

= 7.7%

%IncentiveElectric	= % of total incentive paid by electric utility

= Actual

%IncentiveGas		= % of total incentive paid by gas utility

= Actual

Code of Federal Redulations (baseline effective 1/1/2019):

| Equipment type | Cooling capacity | Heating type | Cooling Efficiency level | Heating Efficiency level | Compliance date |
| --- | --- | --- | --- | --- | --- |
| Small Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥65,000 Btu/h and <135,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 12.2 | N/A | 1/1/2018 |
|  |  | All Other Types of Heating | IEER = 12.0 | COP = 3.3 | 1/1/2018 |
| Large Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥135,000 Btu/h and <240,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 11.6 | N/A | 1/1/2018 |
|  |  | All Other Types of Heating | IEER = 11.4 | COP = 3.2 | 1/1/2018 |
| Very Large Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥240,000 Btu/h and <760,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 10.6 | N/A | 1/1/2018 |
|  |  | All Other Types of Heating | IEER = 10.4 | COP = 3.2 | 1/1/2018 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Split-System) | <65,000 Btu/h | All | SEER = 14.0 | HSPF = 8.2 | 1/1/2017 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Single-Package) | <65,000Btu/h | All | SEER = 14.0 | HSPF = 8.0 | 1/1/2017 |
| Small Commercial Packaged Air-Conditioning and Heating Equipment (Water Source: Water-to-Air, Water-Loop) | <17,000 Btu/h | All | EER = 12.2 | COP = 4.3 | 10/9/2015 |
|  | ≥17,000 Btu/h and <65,000 Btu/h | All | EER = 13.0 | COP = 4.3 | 10/9/2015 |
|  | ≥65,000 Btu/h and <135,000Btu/h | All | EER = 13.0 | COP = 4.3 | 10/9/2015 |

Minimum Efficiency Requirements: 2015 IECC (baseline effective 1/1/2016 to 3/30/2019)

Minimum Efficiency Requirements: 2018 IECC (baseline effective 7/1/2019 for New Construction measures)

IECC2018 Table C403.3.2(2) continued from previous page:

Non Fuel Switch example, a 5-ton cooling unit with 60,000 btu heating, an efficient SEER of 16, and an efficient HSPF of 9.5, at a restaurant in Chicago with a building permit dated after 1/1/2016 saves:

ΔkWh	= Annual kWh Savingscool + Annual kWh Savingsheat

Annual kWh Savingscool 	= (Capacitycool * EFLHcool * (1/SEERbase – 1/SEERee))/1000

Annual kWh Savingsheat 	= (HeatLoad * (1/HSPFbase – 1/HSPFee)/1000

ΔkWh 	= (60,000 * 1134 * (1/14 – 1/16))/1000 + (60,000 * 1354 * (1/8.2 – 1/9.5))/1000

= 1963.2 kWh

Fuel Switch Illustrative Examples

[for illustrative purposes 50:50 Incentive is used for joint programs]

New construction using gas furnace and central AC baseline:

For example a 60,000 Btu, 16 SEER, 9.5 HSPF Air Site Heat Pump installed in a Chicago restaurant, in place of a 120,000 Btuh natural gas furnace and 5 ton Central AC unit:

SiteEnergySavings (MMBTUs)	=  GasHeatReplaced + FurnaceFanSavings - HPSiteHeatConsumed + HPSiteCoolingImpact

GasHeatReplaced		= (HeatLoad * 1/AFUEbase) / 1,000,000

= (60,000 * 1354 * 1/0.8) / 1000000

= 101.6 MMBtu

FurnaceFanSavings	= (FurnaceFlag * HeatLoad * 1/AFUEbase * Fe) / 1,000,000

= (1 * 60,000 * 1354 * 1/0.8 * 0.077) / 1,000,000

= 7.8 MMBtu

HPSiteHeatConsumed	= ((HeatLoad * (1/(HSPFee * HSPFadj))) /1000 * 3412)/ 1,000,000

= ((60,000 * 1354 * (1/(9.5 * 1.001))) / 1000 * 3412) / 1,000,000

= 29.1 MMBtu

HPSiteCoolingImpact 	= ((FLHcool * Capacitycool * (1/SEERbase - 1/(SEERee * SEERadj)))/1000 * 3412) / 1,000,000

= ((60,000 * 1134 * (1/13 - 1/(15 * 1.011))) / 1000 * 3412)/1,000,000

= 2.5 MMBtu

SiteEnergySavings (MMBTUs)	= 101.6 + 7.8 – 29.1 + 2.5 = 82.8 MMBtu [Measure is eligible]

Fuel Switch Illustrative Example continued

Savings would be claimed as follows:

| Measure supported by: | Electric Utility claims: | Gas Utility claims: |
| --- | --- | --- |
| Electric utility only | 82.8 * 1,000,000/3412 = 24,267 kWh | N/A |
| Electric and gas utility | 0.5 * 82.8 * 1,000,000/3412 = 12,134 kWh | 0.5 * 82.8 * 10 = 414 Therms |
| Gas utility only | N/A | 82.8 * 10 = 828 Therms |

###### Summer Coincident Peak Demand Savings

ΔkW		= ((kBtu/hrcool) * (1/EERbase – 1/EERee)) *CF

Where CF value is chosen between:

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

For example, a 5 ton cooling unit with 60 kbtu heating, an efficient EER of 12.5 with a building permit dated after 1/1/2016 saves:

ΔkW		= (60 * (1/11 – 1/12.5)) *0.913

= 0.598 kW

###### Natural Gas Energy Savings

Calculation provided together with Electric Energy Savings above.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Cost Effectiveness Screening and Load Reduction Forecasting when Fuel Switching

This measure can involve fuel switching from gas to electric.

For the purposes of forecasting load reductions due to fuel switch ASHP projects per Section 16-111.5B, changes in site energy use at the customer’s meter (using ΔkWh algorithm below) adjusted for utility line losses (at-the-busbar savings), customer switching estimates, NTG, and any other adjustment factors deemed appropriate, should be used.

The inputs to cost effectiveness screening should reflect the actual impacts on the electric and fuel consumption at the customer meter and, for fuel switching measures, this will not match the output of the calculation/allocation methodology presented in the “Electric Energy Savings” and “Natural Gas Savings” sections above. Therefore in addition to the calculation of savings claimed, the following values should be used to assess the cost effectiveness of the measure. For Early Replacement measures, the efficiency terms of the existing unit should be used for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 7 years for furnace, 8 years for boilers or GSHP, 15 years for electric resistance), and the efficiency terms for a new baseline unit should be used for the remaining years of the measure.

ΔTherms	= [Heating Consumption Replaced]

= [(HeatLoad * 1/AFUEbase) / 100,000]

ΔkWh 		= [FurnaceFanSavings] - [HP heating consumption] + [Cooling savings]

For units with cooling capacities less than 65 kBtu/hr:

= [FurnaceFlag * HeatLoad * 1/AFUEbase * Fe * 0.000293] - [(HeatLoad * (1/(HSPFee * HSPFadj))/1000] + [(Capacitycool * EFLHcool * (1/SEERbase - 1/(SEER_ee * SEERadj)))/1000]

For units with cooling capacities greater than 65 kBtu/hr:

= [FurnaceFlag * HeatLoad * 1/AFUEbase * Fe * 0.000293] - [HeatLoad/3412 * (1/COPee)]  + [(Capacitycool * EFLHcool * (1/EERbase - 1/EER_ee))/1000]

###### Measure Code: CI-HVC-HPSY-V08-220101

###### Review Deadline: 1/1/2023

### High Efficiency Boiler

###### Description

To qualify for this measure the installed equipment must be replacement of an existing boiler at the end of its service life, in a commercial or multifamily space with a high efficiency, gas-fired steam or hot water boiler. High efficiency boilers achieve gas savings through the utilization of a sealed combustion chamber and multiple heat exchangers that remove a significant portion of the waste heat from flue gasses. Because multiple heat exchangers are used to remove waste heat from the escaping flue gasses, some of the flue gasses condense and must be drained.

This measure was developed to be applicable to the following program types: TOS, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a boiler used 80% or more for space heating, not process, and boiler AFUE, ET (thermal efficiency), or EC (combustion efficiency) rating must be rated greater than or equal to 85% for hot water boilers and 83% for steam boilers.

###### Definition of Baseline Equipment

Dependent on when the unit is installed and whether the unit is hot water or steam. The baseline efficiency source is the Energy Independence and Security Act of 2007 with technical amendments from Federal Register, volume 81, Number 10, January 15, 2016 for boilers <300,000 Btu/hr and Federal Register, volume 74, Number 139, July 22, 2009 for boiler ≥300,000 Btu/hr.

For boilers <300,000 Btu/hr the technical amendments include the recent compliance dates for gas-fired hot water and steam boilers manufactured on or after January 15, 2021.

Note: A new Federal Standard, applicable to only natural-draft, gas-fired steam packaged boilers, becomes effective March 2, 2022. However, this measure characterization is not adopting those appliance standards until January 1, 2023. Additionally, new Federal Standards, applicable to all hot water and steam commercial packaged boilers < 10,000,000 Btu/hr input capacity, becomes effective January 10, 2023.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 25 years.

###### Deemed Measure Cost

The measure cost for this technology is tiered based on the boiler type and combustion efficiencies. As installation costs for the base case and the measure case units are assumed to be the same, labor costs are not specified for this measure.

Incremental and Gross Measure costs for Process Boilers

| Boiler Type | Incremental Measure Cost ($/KBtu) | Full Installed Measure Cost ($/KBtu) |
| --- | --- | --- |
| Hot Water Boiler >85% EC and <90% EC | $2.17 | $12.94 |
| Hot Water Boiler >90% EC | $12.17 | $22.95 |
| Steam Boiler >83% EC and <85% EC | $4.35 | $19.24 |
| Modular Steam Boiler Arrays (>85% EC) | Custom |  |

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms	= EFLH * Capacity * ((EfficiencyEE - EfficiencyBase) / EfficiencyBase) / 100,000

Where:

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

Capacity 	= Nominal Heating Input Capacity Boiler Size (Btu/hr) for efficient unit not existing unit

= custom Boiler input capacity in Btu/hr

EfficiencyBase	= Baseline Boiler Efficiency Rating, dependant on year and boiler type

Hot water boiler baseline:

| Boiler Capacity and Distribution Type | Efficiency |
| --- | --- |
| Hot Water <300,000 Btu/hr | 84% AFUE |
| Hot Water ≥300,000 & ≤2,500,000 Btu/hr | 80% ET |
| Hot Water >2,500,000 Btu/hr | 82% EC |

Steam boiler baseline:

| Boiler Capacity and Distribution Type | Efficiency |
| --- | --- |
| Steam <300,000 Btu/hr | 82% AFUE |
| Steam - all except natural draft ≥300,000 & ≤2,500,000 Btu/hr | 79% TE |
| Steam - natural draft ≥300,000 & ≤2,500,000 Btu/hr | 77% TE |
| Steam - all except natural draft >2,500,000 Btu/hr | 79% TE |
| Steam - natural draft >2,500,000 Btu/hr | 77% TE |

EfficiencyEE	= Efficent Boiler Efficiency Rating

=actual value, specified to one significant digit (i.e., 95.7%)

For example, a 150,000 btu/hr water boiler meeting AFUE 90% is installed in Rockford at a high rise office building , in the year 2022

ΔTherms	= 2,089* 150,000  * (0.90-0.840)/0.840) / 100,000 Btu/Therm

= 224 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-BOIL-V09-220101

###### Review Deadline: 1/1/2023

### High Efficiency Furnace

###### Description

This measure covers the installation of a residential sized (<225,000 Btu/hr) or commercial sized (>=225,000 Btu/hr) high efficiency gas furnace in lieu of a standard efficiency gas furnace in a commercial or industrial space. Note commercial sized condensing gas units (>= 225,000 Btu/hr) heating 100% outside air should use 4.4.37 Unitary HVAC Condensing Furnace if appropriate. High efficiency gas furnaces achieve savings through the utilization of a sealed, super insulated combustion chamber, more efficient burners, and multiple heat exchangers that remove a significant portion of the waste heat from the flue gasses. Because multiple heat exchangers are used to remove waste heat from the escaping flue gasses, most of the flue gasses condense and must be drained.

This measure also describes savings from a brushless permanent magnet (BPM) motor (known and referred in this measure as an electronically commutated motor (ECM)) compared to a lower efficiency motor within a residential sized unit. Time of Sale and New Construction scenarios can no longer claim these electrical savings, as federal standards make ECM blower fan motors a requirement for residential-sized furnaces. Savings however are available from replacing an operational inefficient furnace with a new furnace with an ECM prior to the end of its life.

This measure was developed to be applicable to the following program types: TOS, NC and EREP.  If applied to other program types, the measure savings should be verified.

Time of sale:

  - The installation of a new high efficiency, gas-fired condensing furnace in a commercial location. This could relate to the replacement of an existing unit at the end of its useful life, or the installation of a new system.

Early replacement:

Early Replacement determination will be based on meeting the following conditions:

    - The existing unit is operational when replaced, or

    - The existing unit requires minor repairs (<$528).

    - All other conditions will be considered Time of Sale.

The Baseline AFUE of the existing unit replaced:

    - If the AFUE of the existing unit is known and <=75%, the Baseline AFUE is the actual AFUE value of the unit replaced. If the AFUE is >75%, the Baseline AFUE = 80%.

    - If the AFUE of the existing unit is unknown, use assumptions in variable list below (AFUE(exist)).

    - If the operational status or repair cost of the existing unit is unknown, use time of sale assumptions.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a furnace with input energy less than 225,000 Btu/hr rated natural gas fired furnace with an Annual Fuel Utilization Efficiency (AFUE) rating and fan electrical efficiency exceeding the program requirements:

###### Definition of Baseline Equipment

Time of Sale: The current Federal Standard for gas furnaces <225,000 Btu/hr is an AFUE rating of 80%.

For furnaces ≥225,000 Btu/hr, the baseline AFUE rating is also 80%. Note: a new Federal Standard will become effective January 1, 2023 increaseing this to 81%.

Early replacement: The baseline for this measure is the efficiency of the existing equipment for the assumed remaining useful life of the unit and a new baseline 80% AFUE for Residential sized or 81% AFUE for Commercial sized unit for the remainder of the measure life.

###### Note: a new Federal Standard will become effective January 1, 2023 and be applicable to all gas furnaces.

###### Definition of Measure Life

The expected measure life is assumed to be 16.5 years.

Remaining life of existing equipment is assumed to be 5.5 years.

###### Deemed Measure Cost

Time of Sale: The incremental capital cost for this measure depends on efficiency as listed below:

| AFUE | Installation Cost | Incremental Install Cost |
| --- | --- | --- |
| 80% | $2011 | n/a |
| 90% | $2641 | $630 |
| 91% | $2727 | $716 |
| 92% | $2813 | $802 |
| 93% | $3025 | $1,014 |
| 94% | $3237 | $1,226 |
| 95% | $3449 | $1,438 |
| 96% | $3661 | $1,650 |
| 97% | $3873 | $1,862 |

Early Replacement: The full installation cost is provided in the table above. The assumed deferred cost (after 5.5 years) of replacing existing equipment with a new 80% baseline unit is assumed to be $2,296. This cost should be discounted to present value using the nominal discount rate.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Residential sized (<225,000 Btu/hr), Early Replacement Only:

For remaining useful life of the existing furnace (assumed 5.5 years):

ΔkWh = Heating Savings + Cooling Savings + Shoulder Season Savings

Where:

Heating Savings		= Brushless DC motor or Electronically commutated motor (ECM)				= 418 kWh

Cooling Savings	= Brushless DC motor or electronically commutated motor  (ECM) savings during cooling season

If air conditioning 	= 263 kWh

If no air conditioning	= 175 kWh

If unknown (weighted average)= 241 kWh

Shoulder Season Savings	= Brushless DC motor or electronically commutated motor (ECM) savings during shoulder seasons

= 51 kWh

For example, a blower motor in a low rise office building where air conditioning presence is unknown:

ΔkWh 	= Heating Savings + Cooling Savings + Shoulder Season Savings

= 418 +241 + 51

= 710 kWh

For remaining measure life of the existing furnace (next 11 years): 0 kWh

All other applications assume 0 kWh.

###### Summer Coincident Peak Demand Savings

Residential sized (<225,000 Btu/hr) Early Replacement Only:

For remaining useful life of the existing furnace (assumed 5.5 years):

For units that have evaporator coils and condensing units and are cooling in the summer in addition to heating in the winter the summer coincident peak demand savings should be calculated.  If the unit is not equipment with coils or condensing units, the summer peak demand savings will not apply.

ΔkW	 = (CoolingSavings/HOURSyear) * CF

Where:

HOURSyear = Actual hours per year if known, otherwise use hours from Table below for building type:

| Building Type | HOURSyear | Model source |
| --- | --- | --- |
| Assembly | 2150 | eQuest |
| Assisted Living | 4373 | eQuest |
| Auto Dealership | 1605 | OpenStudio |
| College | 4065 | OpenStudio |
| Convenience Store | 2084 | eQuest |
| Drug Store | 1708 | OpenStudio |
| Elementary School | 2649 | OpenStudio |
| Emergency Services | 3277 | OpenStudio |
| Garage | 2102 | eQuest |
| Grocery | 5470 | OpenStudio |
| Healthcare Clinic | 6364 | OpenStudio |
| High School | 3141 | eQuest |
| Hospital - VAV econ | 8707 | OpenStudio |
| Hospital - CAV econ | 2336 | OpenStudio |
| Hospital - CAV no econ | 4948 | OpenStudio |
| Hospital - FCU | 8760 | OpenStudio |
| Manufacturing Facility | 2805 | eQuest |
| MF - High Rise | 6823 | OpenStudio |
| MF - Mid Rise | 4996 | OpenStudio |
| Hotel/Motel – Guest | 4155 | OpenStudio |
| Hotel/Motel - Common | 6227 | OpenStudio |
| Movie Theater | 2120 | eQuest |
| Office - High Rise - VAV econ | 3414 | OpenStudio |
| Office - High Rise - CAV econ | 4849 | eQuest |
| Office - High Rise - CAV no econ | 6049 | OpenStudio |
| Office - High Rise - FCU | 5341 | OpenStudio |
| Office - Low Rise | 3835 | OpenStudio |
| Office - Mid Rise | 3040 | OpenStudio |
| Religious Building | 2830 | eQuest |
| Restaurant | 2305 | OpenStudio |
| Retail - Department Store | 2528 | eQuest |
| Retail - Strip Mall | 2266 | eQuest |
| Warehouse | 770 | eQuest |
| Unknown | 2987 | n/a |

CF	=Summer Peak Coincidence Factor for measure is provided below for different building types:

| HVAC Pumps | CF |
| --- | --- |
| Assembly | 48.3% |
| Assisted Living | 52.9% |
| College | 14.2% |
| Convenience Store | 57.1% |
| Elementary School | 33.3% |
| Emergency Services | 19.6% |
| Garage | 61.9% |
| Grocery | 47.5% |
| Healthcare Clinic | 61.9% |
| High School | 28.8% |
| Hospital - VAV econ | 57.6% |
| Hospital - CAV econ | 61.5% |
| Hospital - CAV no econ | 64.8% |
| Hospital - FCU | 60.9% |
| Manufacturing Facility | 43.3% |
| MF - High Rise - Common | 43.7% |
| MF - Mid Rise | 24.3% |
| Hotel/Motel - Guest | 62.9% |
| Hotel/Motel - Common | 64.6% |
| Movie Theater | 41.9% |
| Office - High Rise - VAV econ | 43.2% |
| Office - High Rise - CAV econ | 48.3% |
| Office - High Rise - CAV no econ | 50.3% |
| Office - High Rise - FCU | 46.2% |
| Office - Low Rise | 47.4% |
| Office - Mid Rise | 42.8% |
| Religious Building | 43.3% |
| Restaurant | 48.8% |
| Retail - Department Store | 50.5% |
| Retail - Strip Mall | 52.8% |
| Warehouse | 22.5% |
| Unknown | 42.4% |

For example, a blower motor in a low rise office building where air conditioning presence is unknown:

ΔkW 	= (241 / 2481) * 0.474

= 0.05 kW

For remaining measure life of the existing furnace (next 11 years): 0 kW

All other applications assume 0 kWh.

###### Natural Gas Energy Savings

Time of Sale:

ΔTherms	 = (EFLH * Capacity * (AFUE(eff) / AFUE(base) - 1)) / 100,000

Early replacement:

ΔTherms for remaining life of existing unit (1st 5.5 years):

ΔTherms	 = (EFLH * Capacity * (AFUE(eff) / AFUE(exist) - 1)) / 100,000

ΔTherms for remaining measure life (next 11 years):

ΔTherms	 = (EFLH * Capacity * (AFUE(eff) / AFUE(base)-1)) / 100,000

Where:

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

Capacity 	= Nominal Heating Input Capacity Furnace Size (Btu/hr) for efficient unit not existing unit

= custom Furnace input capacity in Btu/hr

AFUE(exist)	= Existing Furnace Annual Fuel Utilization Efficiency Rating

= Use actual AFUE rating where it is possible to measure or reasonably estimate.

If unknown, assume 64.4 AFUE%.

AFUE(base)	= Baseline Furnace Annual Fuel Utilization Efficiency Rating

= For residential sized units (<225,000 Btu/hr):  80%

= For commercial sized units (>=225,000 Btu/hr):

| Program | AFUE(base) |
| --- | --- |
| Time of Sale | 80% |
| Early Replacement | 81% |

AFUE(eff)	= Efficent Furnace Annual Fuel Utilization Efficiency Rating.

= Actual. If Unknown, assume 95%.

For example,

ΔTherms	= (1428 * 150,000  * (0.92 / 0.80 – 1))/ 100,000

= 321 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-FRNC-V11-220101

###### Review Deadline: 1/1/2025

### Infrared Heaters

###### Description

A natural gas-fired radiant infrared heater uses the combustion of natural gas to heat a metal tube or ceramic panel to a very high temperature (typically between 1200 and 5000 degrees Fahrenheit). The high surface temperature causes radiative heat transfer between the heater surface and its surroundings. The surroundings will re-radiate the heat to occupants and release heat through convection to the air, providing a comfortable environment without directly heating air.

Infrared heaters are ideal for space heating applications where there are elevated ceilings with high thermal stratification, spaces with high ventilation or air infiltration rates, or a need for spot heating within an unconditioned or industrial space. Aircraft hangers, warehouses, greenhouses, manufacturing production areas, pools, and loading docks are space types that can be efficiently served by a radiant infrared heater.

This measure was developed to be applicable to the following program types: TOS, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a natural gas heater with an electric ignition that uses non-conditioned air for combustion. Gross Radiant Coefficient (GRC) is provided by the manufacturer and defined as the ratio of radiant heat output delivered in Btu to the natural gas input energy.

###### Definition of Baseline Equipment

The baseline equipment is a standard natural gas fired warm air heater.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is  $2.70 per kBtu/hr input capacity.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

Natural gas savings for this measure are based on the standard practice of HVAC designers to size a gas-fired radiant infrared heater at a lower input capacity than an equivalent warm air unit heater for an identical application.

ΔTherms = Therms(base) – Therms(IR)

Therms(base) 	= Capacity/RSF * EFLH/100,000

Therms(IR) 	= Capacity * EFLH/100,000

Where:

Capacity		= Input capacity of radiant infrared heater in btu/hr

= Actual

| Gross Radiant Coefficient (GRC) | RSF (Radiation Sizing Factor) |
| --- | --- |
| GRC < 0.67 | 0.85 |
| 0.67 ≤ GRC | 0.70 |

RSF		= Radiation Sizing Factor, dependent on Gross Radiant Coefficient as listed below:,  				If Gross Radiant Coefficient is unavailable, assume RSF = 0.85.

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

100,000		= Btu to therm conversion factor

For example: a radiant heater with a natural gas input capacity of 125,000 Btu/hr and a Gross Radiant Coefficient of 0.45 installed in a warehouse in Chicago will save: ΔTherms = Therms(base) – Therms(IR) Therms(base) = 125,000/0.85*1286/100,000 = 1891.176 Therms Therms(IR) = 125,000*1286/100,000 = 1607.500 Therms ΔTherms = 1891.176 – 1670.500 = 283.676 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-IRHT-V02-210101

###### Review Deadline: 1/1/2023

### Package Terminal Air Conditioner (PTAC) and Package Terminal Heat Pump (PTHP)

###### Description

A PTAC is a packaged terminal air conditioner that cools and sometimes provides heat through an electric resistance heater (heat strip). A PTHP is a packaged terminal heat pump. A PTHP uses its compressor year round to heat or cool. In warm weather, it efficiently captures heat from inside your building and pumps it outside for cooling. In cool weather, it captures heat from outdoor air and pumps it into your home, adding heat from electric heat strips as necessary to provide heat.

This measure characterizes:

- Time of Sale: the purchase and installation of a new efficient PTAC or PTHP.

- Early Replacement: the early removal of an existing PTAC or PTHP from service, prior to its natural end of life, and replacement with a new efficient PTAC or PTHP unit. Savings are calculated between existing unit and efficient unit consumption during the remaining life of the existing unit, and between new baseline unit and efficient unit consumption for the remainder of the measure life. The measure is only valid for non-fuel switching installations – for example replacing a cooling only PTAC with a PTHP can currently not use the TRM.

This measure was developed to be applicable to the following program types: TOS NC, EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be PTACs or PTHPs that exceed baseline efficiencies.

###### Definition of Baseline Equipment

Time of Sale: the baseline condition is equipment that meets the Code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher) in effect on the date of equipment purchase (if date is unknown, assume current Code minimum).

Early Replacement: the baseline is the existing PTAC or PTHP for the assumed remaining useful life of the unit and the new baseline as defined above for the remainder of the measure life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 8 years.

Remaining life of existing equipment is assumed to be 3 years.

###### Deemed Measure Cost

Time of Sale: The incremental capital cost for this equipment is estimated to be $84/ton.

Early Replacement: The measure cost is the full cost of removing the existing unit and installing a new one. The actual program cost should be used. If unknown assume $1,047 per ton.

The assumed deferred cost (after 5 years) of replacing existing equipment with new baseline unit is assumed to be $1,039 per ton. This cost should be discounted to present value using the nominal discount rate.

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.  Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Electric savings for PTACs and PTHPs should be calculated using the following algorithms

###### Energy Savings

Time of Sale:

PTAC ΔkWh	= Annual kWh Savingscool

PTHP ΔkWh	= Annual kWh Savingscool + Annual kWh Savingsheat

Annual kWh Savingscool 	= (kBtu/hrcool) * [(1/EERbase) – (1/EERee)] * EFLHcool

Annual kWh Savingsheat 	= (kBtu/hrheat)/3.412 * [(1/COPbase) – (1/COPee)] * EFLHheat

Early Replacement:

ΔkWh for remaining life of existing unit (1st 5years)  	= Annual kWh Savingscool + Annual kWh Savingsheat

Annual kWh Savingscool 	= (kBtu/hrcool) * [(1/EERexist) – (1/EERee)] * EFLHcool

Annual kWh Savingsheat 	= (kBtu/hrheat)/3.412 * [(1/COPexist) – (1/COPee)] * EFLHheat

ΔkWh for remaining measure life (next 10 years)  	= Annual kWh Savingscool + Annual kWh Savingsheat

Annual kWh Savingscool 	= (kBtu/hrcool) * [(1/EERbase) – (1/EERee)] * EFLHcool

Annual kWh Savingsheat 	= (kBtu/hrheat)/3.412 * [(1/COPbase) – (1/COPee)] * EFLHheat

Where:

kBtu/hrcool 	= capacity of the cooling equipment in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr).

= Actual installed

EFLHcool	= Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use:

EFLHheat	= Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

EERexist	= Energy Efficiency Ratio of the existing equipment

= Actual. If unknown assume 10.2 EER for PTAC and 10.4 EER for PTHP.

EERbase	= Energy Efficiency Ratio of the baseline equipment; see the table below for values.

= Based on applicable Code on date of equipment purchase (if unknown assume current Code

Copy of Table C403.2.3(3): Minimum Efficiency Reguirements: Electrically operated packaged terminal air conditioners, packaged terminal heat pumps

| Equipment Type | IECC 2015/2018 Minimum Efficiency (baseline effective 1/1/2016) | Federal Regulations Minimum Efficiency (baseline effective 1/1/2019) |
| --- | --- | --- |
| PTAC (Cooling mode) Standard Sized | 14.0 – (0.300 x Cap/1000) EER | 14.0 – (0.300 x Cap/1000) EER Compliance date: 1/1/2017 |
| PTAC (Cooling mode) Non-Standard Size* | 10.9 – (0.213 x Cap/1000) EER | 10.9 – (0.213 x Cap/1000) EER Compliance date: 10/7/2010 |
| PTHP (Cooling mode) Standard Sized | 14.0 – (0.300 x Cap/1000) EER | 14.0 – (0.300 x Cap/1000) EER Complainace date: 10/8/2012 |
| PTHP (Cooling mode) Non-Standard Size* | 10.8 – (0.213 x Cap/1000) EER | 10.8 – (0.213 x Cap/1000) EER Compliance date: 10/7/2010 |
| PTHP (Heating mode) Standard Sized | 3.2 – (0.026 x Cap/1000) COP | 3.7 – (0.052 x Cap/1000) COP Compliance date: 10/8/2012 |
| PTHP (Heating mode) Non-Standard Size* | 2.9 – (0.026 x Cap/1000) COP | 2.9 – (0.026 x Cap/1000) COP Compliance date: 10/7/2010 |

Table notes: “Cap” = The rated cooling capacity of the project in Btu/hr. If the units capacity is less than 7000 Btu/hr, use 7,000 Btu/hr in the calculation. If the unit’s capacity is greater than 15,000 Btu/hr, use 15,000 Btu/hr in the calculations.

* Non-Standard Size apply only to units with existing sleeves less than 16 inches (406mm) in height and less than 42 inches (1067 mm) in width. Replacement unit shall be factory labeled as follows “MANUFACTURED FOR REPLACEMENT APPLICATIONS ONLY; NOT TO BE INSTALLED IN NEW CONSTRUCTION PROJECTS”.

EERee	= Energy Efficiency Ratio of the energy efficient equipment. For air-cooled units < 65 kBtu/hr, if the actual EERee is unknown, assume the following conversion from SEER to EER for calculation of peak savings: EER = (-0.02 * SEER2) + (1.12 * SEER)

= Actual installed

kBtu/hrheat	= capacity of the heating equipment in kBtu per hour.

= Actual installed

3.412		= Btu per Wh.

COPexist	= coefficient of performance of the existing equipment

= Actual. If unknown assume 1.0 COP for PTAC units and 2.9 COP for PTHPs

COPbase	= coefficient of performance of the baseline equipment; see table above for values.

COPee 		= coefficient of performance of the energy efficient equipment.

= Actual installed.

Time of Sale (assuming new construction baseline):

For example, a 1 ton PTAC with an efficient EER of 12 in a guest room of a hotel in Rockford with a building permit dated after 1/1/2016 saves:

= [(12) * [(1/10.4) – (1/12)] * 1,042

=  160 kWh

Early Replacement (assuming replacement baseline for deferred replacement in 3 years):

For example, a 1 ton PTHP with an efficient EER of 12, COP of 3.0 in a guest room of a hotel in Rockford replaces a PTAC unit (with electric resistance heat) with unknown efficiency.

ΔkWh for remaining life of existing unit (1st 3 years)

= (12 * (1/10.2 – 1/12) * 1,042) + (12/3.412 * (1/1.0 – 1/3.0) * 1,758)

= 184 + 4,122

= 4,306 kWh

ΔkWh for remaining measure life (next 5 years)

= (12 * (1/10.4 – 1/12) * 1,042) + (12/3.412 * (1/1.0 – 1/3.0) * 1,758)

= 160 + 4,122

= 4,282 kWh

###### Summer Coincident Peak Demand Savings

Time of Sale:

ΔkW		= (kBtu/hrcool) * [(1/EERbase) – (1/EERee)] *CF

Early Replacement:

ΔkW for remaining life of existing unit (1st 5years)  = (kBtu/hrcool) * [(1/EERexist) – (1/EERee)] *CF

ΔkW for remaining measure life (next 10 years)  = (kBtu/hrcool) * [(1/EERbase) – (1/EERee)] *CF

Where:

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Time of Sale:

For example, a 1 ton replacement cooling unit with no heating with an efficient EER of 12 with a building permit dated after 1/1/2016 saves:

ΔkWSSP		= (12 * (1/10.4 – 1/12) *0.913

= 0.1405 kW

For example, a 1 ton PTHP with an efficient EER of 12, COP of 3.0 replacing a PTAC unit with unknown efficiency saves:

ΔkW for remaining life of existing unit (1st 3 years):

ΔkWSSP		= 12 * (1/10.2 – 1/12) * 0.913

= 0.1611 kW

ΔkW for remaining measure life (next 5 years):

ΔkWSSP		= 12 * (1/10.4 – 1/12) * 0.913

= 0.1405 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-PTAC-V11-220101

###### Review Deadline: 1/1/2025

### Pipe Insulation

###### Description

This measure provides rebates for installation of 1” – 4” fiberglass, foam, calcium silicate or other types of insulation with similar insulating properties to existing bare pipe on straight piping as well as other pipe components such as elbows, tees, valves, and flanges for all non-residential installations.

Savings are provided in two forms; default savings estimates on a per linear foot basis and savings calculated with a multitude of varying parameters with the use of an external calculator. The default savings estimates are provided in the ‘Calculation of Savings’ section below. They provide estimated savings for measure applications with select and default parameters. The external tool, however, allows more flexibility and provides comprehensive analysis to pipe insulation projects, taking into account all on-site variables.

Default per linear foot savings estimates are provided for the both exposed indoor or above ground outdoor piping distributing fluid in the following system types (natural gas fired systems only):

- Hydronic heating systems (with or without outdoor reset controls), including:

  - boiler systems that do not circulate water around a central loop and operate upon demand from a thermostat (“non-recirculation”)

  - systems that recirculate during heating season only (“Recirculation – heating season only”)

  - systems recirculating year round (“Recirculation – year round”)

- Domestic hot water

- Low and high-pressure steam systems

  - non-recirculation

  - recirculation - heating season only

  - recirculation - year round

With the use of the external tool to account for varying parameter inputs, savings are calculated using the “Pipe Insulation” calculator available on the Nicor Gas website at: https://www.nicorgas.com/emerging. Savings are approached through the following inputs:

- Pipe Material: Copper, Steel, Stainless Steel

- Pipe Location: Indoor (Heated, Semi-Heated, Unheated, Unspecified) or Outdoor

- Application: Hot Water Space Heating, Steam (5, 15, 40, 65, 100, 150 psi) for various system types detailed in the subsequent system type list below

- Thermal Regain Factor (based on pipe location)

- Building Type

- Nominal Pipe Size (inches)

- Insulation Thickness (inches): 1”-4”, specified in ½” increments

- Hot Water/Steam Boiler Efficiency (%): 75%-90%, specified in 2.5% increments

- Climate Zone: Rockford, Chicago, Springfield, Belleville, Marion

- Length of Installed Pipe (feet)

- Number of Elbows, Tees, Flanges, and/or Valves

Process piping can also use the algorithms provided but requires custom entry of hours.

For new construction applications, minimum qualifying nominal pipe diameter is 1”. Piping must have at least 1” of insulation and outdoor piping must include an all-weather protective jacket. New advanced insulating materials may be thinner and savings can be calculated with 3E Plus v4.1.

The relevant code of compliance should be followed for direction on minimum permitted insulation thickness for a nominal pipe diameter. As per the International Energy Conservation Code (IECC) 2018, the minimum permitted insulation thickness is 1” for installations pertaining to new construction or major renovation heating HVAC applications . However, there are exceptions based on Fluid Operating Temperature Range, Insulation thermal conductivity range, install locations and pipe sizes –indicating the minimum insulation thickness required for parameters described in the column headers presented in the table below.

| Fluid Operating Temperature Range and Usage (°F) | Insulation Conductivity |  | Nominal Pipe or Tube Size (inches) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductivity Btu.in/(h.ft2.°F) | Mean Rating Temperature, °F | <1 | 1 to <1.5 | 1.5 to <4 | 4 to <8 | ≥8 |
| >350 | 0.32 - 0.34 | 250 | 4.5 | 5.0 | 5.0 | 5.0 | 5.0 |
| 251 - 350 | 0.29 - 0.32 | 200 | 3.0 | 4.0 | 4.5 | 4.5 | 4.5 |
| 201 - 250 | 0.27 - 0.30 | 150 | 2.5 | 2.5 | 2.5 | 3.0 | 3.0 |
| 141 - 200 | 0.25 - 0.29 | 125 | 1.5 | 1.5 | 2.0 | 2.0 | 2.0 |
| 105 - 140 | 0.21 - 0.28 | 100 | 1.0 | 1.0 | 1.5 | 1.5 | 1.5 |
| 40 -60 | 0.21 - 0.27 | 75 | 0.5 | 0.5 | 1.0 | 1.0 | 1.0 |
| <40 | 0.20 - 0.26 | 50 | 0.5 | 1.0 | 1.0 | 1.0 | 1.5 |

Note – The above table is not representative of the applicability of the workpaper measure and does not reflect any limitations in the web-based calculator. This is merely the requirements cited by the IECC 2018 code for pipe insulation.

This measure was developed to be applicable to the following program types:  RF, DI

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient case is installing pipe wrap insulation to a length of pipe. Indoor piping must have at least 1” of insulation (or equivalent R-value) and outdoor piping must have at least 2” of insulation (or equivalent R-value) and include an all-weather protective jacket. Minimum qualifying pipe diameter is 1.” Insulation must be continuous and contiguous over fittings that directly connect to straight pipe, including elbows and tees.

###### Definition of Baseline Equipment

The base case for savings estimates is a bare pipe. Pipes are required by new construction code to be insulated but are still commonly found uninsulated in older commercial buildings.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 15 years.

###### Deemed Measure Cost

Actual costs should be used if known. Otherwise, the deemed measure costs below based on RS Means pricing reference materials may be used. The following table summarizes the estimated costs for this measure per foot of insulation added and include installation costs:

| Insulation Thickness |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1 Inch | 1.5 Inches | 2 Inches | 2.5 Inches |
| Pipe- RS Means # | 220719.10.5140 | 220719.10.4900 | 220719.10.4900 | Extrapolated |
| Jacket- RS Means # | 220719.30.0152 & 220719.40.0240 | 220719.30.0140 & 220719.40.0140 | 220719.30.0140 & 220719.40.0140 | 220719.30.0140 & 220719.40.0140 |
| Pipe Insulation Type | Calcium Silicate | Calcium Silicate | Calcium Silicate | Calcium Silicate |
| Jacket Type (Indoor) | PVC | PVC | PVC | PVC |
| Jacket Type (Outdoor) | Aluminum | Aluminum | Aluminum | Aluminum |
| Insulation Cost per foot [1] | $11.45 | $15.73 | $20.23 | $24.58 |
| Jacket Cost per foot (Indoor) [2] | $4.90 | $6.70 | $6.70 | $6.70 |
| Jacket Cost per foot (Outdoor) [3] | $6.75 | $9.27 | $9.27 | $9.27 |
| Total Cost per foot (Indoor) = [1+2] | $16.35 | $22.43 | $26.93 | $31.28 |
| Total Cost per foot (Outdoor) = [1+3] | $18.20 | $25.00 | $29.50 | $33.85 |

| Insulation Thickness (continued) |  |  |  |
| --- | --- | --- | --- |
|  | 3 Inches | 3.5 Inches | 4 Inches |
| Pipe- RS Means # | 220719.10.4900 | Extrapolated | Extrapolated |
| Jacket- RS Means # | 220719.30.0140 & 220719.40.0140 | 220719.30.0140 & 220719.40.0140 | 220719.30.0140 & 220719.40.0140 |
| Pipe Insulation Type | Calcium Silicate | Calcium Silicate | Calcium Silicate |
| Jacket Type (Indoor) | PVC | PVC | PVC |
| Jacket Type (Outdoor) | Aluminum | Aluminum | Aluminum |
| Insulation Cost per foot [1] | $28.92 | $33.32 | $37.70 |
| Jacket Cost per foot (Indoor) [2] | $6.70 | $6.70 | $6.70 |
| Jacket Cost per foot (Outdoor) [3] | $9.27 | $9.27 | $9.27 |
| Total Cost per foot (Indoor) = [1+2] | $35.62 | $40.02 | $44.40 |
| Total Cost per foot (Outdoor) = [1+3] | $38.19 | $42.59 | $46.97 |

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

Δtherms per foot 	= [((Qbase – Qeff) * EFLH) / (100,000 * ηBoiler)] * TRF

= [Modeled or provided by tables below] * TRF

Δtherms			= (Lsp + Loc,i) * Δtherms per foot

Where:

EFLH		= Equivalent Full Load Hours for Heating in Existing Buildings or New Construction

= Actual or defaults by building type provided in Section 4.4, HVAC end use

For year round recirculation or domestic hot water:

= 8,766

For heating season recirculation, hours with the outside air temperature below 55°F:

| Zone | Hours |
| --- | --- |
| Zone 1 (Rockford) | 5,039 |
| Zone 2 (Chicago) | 4,963 |
| Zone 3 (Springfield) | 4,495 |
| Zone 4 (Belleville/ | 4,021 |
| Zone 5 (Marion) | 4,150 |

Qbase 		= Heat Loss from Bare Pipe (Btu/hr/ft)

= Calculated where possible using 3E Plusv4.1 software. For defaults see table below

Qeff		= Heat Loss from Insulated Pipe (Btu/hr/ft)

= Calculated where possible using 3E Plusv4.1 software. For defaults see table below

100,000 		= conversion factor (1 therm = 100,000 Btu)

ηBoiler 		= Efficiency of the boiler being used to generate the hot water or steam in the pipe

= Actual or if unknown use default values given below:

= 81.9% for water boilers

= 80.7% for steam boilers, except multifamily low-pressure

= 64.8% for multifamily low-pressure steam boilers

TRF	= Thermal Regain Factor for pipe location and use,

see table below. The Custom TRF option may be used on any pipe location, including pipe locations with deemed TRFs specifically listed in the table below, if supporting justification and calculations for the Custom TRF are provided.

May vary seasonally such as: TRF[summer] * summer hours + TRF[winter] * winter hours where TRF values reflecting summer and winter conditions are apportioned by the hours for those conditions. TRF may also be adjusted by building specific balance point temperature (BPT) and operating hours above and below that BPT.

| Pipe Location | Assumed Regain | TRF, Thermal Regain Factor |
| --- | --- | --- |
| Outdoor | 0% | 1.0 |
| Indoor, conditioned space during the heating season, 55°F BPT | 85% | 0.15 |
| Indoor, conditioned space, not during the heating season, 55°F BPT | 0% | 1.0 |
| Indoor, conditioned, annual use (e.g. hot water or process loads), 55°F BPT | 45% | 0.55 |
| Indoor, semi- conditioned, (unconditioned space, with heat transfer to conditioned space. E.g., boiler room, ceiling plenum, basement, crawlspace, wall), during the heating season, 55°F BPT | 30% | 0.70 |
| Indoor, semi-conditioned, not during the heating season, 55°F BPT | 0% | 1.0 |
| Indoor, semi-conditioned, annual use, 55°F BPT | 16% | 0.84 |
| Indoor, unconditioned spaces, (no heat transfer to conditioned space) | 0% | 1.0 |
| Location not specified - Commercial | 23% | 0.77 |
| Location not specified – Industrial | 16% | 0.84 |
| Custom | Custom | 1 – assumed regain |

Lsp		= Length of straight pipe to be insulated (linear foot)

= actual installed (linear foot)

Loc,I	= Total equivalent length of the other components (valves and tees) of pipe to be insulated

= Actual installed (linear foot). See table “Equivalent Length of Other Components – Elbows and Tees” for equivalent lengths.

The heat loss estimates (Qbase and Qeff) were developed using the 3E Plus v4.1 software program. The energy savings analysis is based on adding 1-inch (indoor) or 2-inch (outdoor) thick insulation around bare pipe. The thermal conductivity of pipe insulation varies by material and temperature rating; to obtain a typical value, a range of materials allowed for this measure were averaged. For insulation materials not in the table below, use 3E Plusv4.0 software to calculate Qbase and Qeff.

| Insulation Type | Conductivity (Btu.in / hr.ft2.ºF @ 75F) | Max temp (ºF) |
| --- | --- | --- |
| Polyethylene foam | 0.25 | 200 |
| Flexible polyurethane-based foam | 0.27 | 200 |
| Fiberglass | 0.31 | 250 |
| Melamine foam | 0.26 | 350 |
| Flexible silicon foam | 0.40 | 392 |
| Calcium silicate | 0.40 | 1200 |
| Cellular glass | 0.31 | 400 |
| Average conductivity of all these materials (Btu.in / hr.ft2.ºF @ 75ºF) | 0.31 |  |

The pipe fluid temperature assumption used depends upon both the system type and whether there is outdoor reset controls:

| System Type | Fluid temperature assumption (°F) |
| --- | --- |
| Hot Water space heating with outdoor reset - Non recirculation | 145 |
| Hot Water space heating without outdoor reset - Non recirculation | 170 |
| Hot Water space heating with outdoor reset – Recirculation heating season only | 145 |
| Hot Water space heating without outdoor reset – Recirculation heating season only | 170 |
| Hot Water space heating with outdoor reset – Recirculation year round | 130 |
| Hot Water space heating without outdoor reset – Recirculation year round | 170 |
| Domestic Hot Water | 125 |
| 5 psi Steam (low pressure) | 225 |
| 15 psi Steam (low pressure) | 250 |
| 40 psi Steam (low pressure) | 287 |
| 65 psi Steam (high pressure) | 312 |
| 100 psi Steam (high pressure) | 338 |
| 150 psi Steam (high pressure) | 365 |

| Example System Types | Indoor Insulation, Hot Water | Indoor Insulation, 5 psi Steam | Indoor Insulation, 65 psi Steam | Domestic Hot Water | Outdoor Insulation, Hot Water | Outdoor Insulation, 5 psi Steam | Outdoor Insulation, 65 psi Steam |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Insulation thickness (inch) | 1 | 2 | 2.5 | 1 | 3 | 3.5 | 4 |
| Temperature, Fluid in Pipe (ºF) | 170 (w/o reset) 145 (w/ reset heat) 130 (w/reset year) | 225 | 312 | 125 | 170 (w/o reset) 145 (w/ reset heat) 130 (w/reset year) | 225 | 312 |
| Climate Zone | Climate Zone 2: Chicago |  |  |  |  |  |  |
| Building Type | Office – Mid Rise |  |  |  |  |  |  |
| Operating Time (hrs/yr) | 1,629 (non-recirc) 4,963 (recirc heating season) 8,766 (recirc year-round) |  |  |  |  |  |  |
| Ambient Temperature (ºF) | 75 | 75 | 75 | 75 | 48.6 | 48.6 | 48.6 |
| Wind speed (mph) | 0 | 0 | 0 | 0 | 5.0 | 5.0 | 5.0 |
| Boiler / Water Heater efficiency | 75% | 80% | 85% | 67% | 80% | 85% | 90% |
| Pipe parameters |  |  |  |  |  |  |  |
| Pipe Location | Indoor Heated | Indoor Semi-heated | Indoor Unheated | n/a | Outdoor |  |  |
| Pipe material | Copper | Steel | Stainless Steel | Copper | Copper | Steel | Stainless Steel |
| Length of Pipe (ft) | 100 |  |  |  |  |  |  |
| Pipe size for Heat Loss Calc | 2” | 2” | 2” | 2” | 2” | 2” | 2” |
| Outer Diameter, Pipe, actual | 2.38” | 2.38” | 2.38” | 2.38” | 2.38” | 2.38” | 2.38” |
| Heat Loss, Bare Pipe (from 3EPlus) (Btu/hr.ft) | 113.5 (w/o reset) 77.8 (w/ reset heat) 58 (w/reset year) | 232.2 | 286.3 | 52 | 460.2 (w/o reset) 363.4 (w/ reset heat) 306 (w/reset year) | 709.5 | 942.2 |
| Insulation parameters |  |  |  |  |  |  |  |
| Average Heat Loss, Insulation (from 3EPlus) (Btu/hr.ft) | 21.6 (w/o reset) 15.8 (w/ reset heat) 12.4 (w/reset year) | 22.6 | 31.8 | 13.25 | 15.2 (w/o reset) 12.1 (w/ reset heat) 10.2 (w/reset year) | 20.4 | 28.2 |
| Annual Energy Savings/ft |  |  |  |  |  |  |  |
| Annual Gas Use, Base Case (therms/yr/ft) | 2.46 (w/o reset) 5.15 (w/ reset heat) 6.78 (w/reset year) | 4.73 (non recirc) 14.4 (recirc heat) 25.4 (recirc year) | 5.5 (non recirc) 16.7 (recirc heat) 29.5 (recirc year) | 6.76 | 9.37 (w/o reset) 22.5 (w/ reset heat) 33.5 (w/reset year) | 13.6 (non recirc) 41.4 (recirc heat) 73.2 (recirc year) | 17.1 (non recirc) 52.0 (recirc heat) 91.8 (recirc year) |
| Annual Gas Use, Measure case (therms/yr/ft) | 0.46 (w/o reset) 1.05 (w/ reset heat) 1.48 (w/reset year) | 0.43 (non recirc) 1.4 (recirc heat) 2.4 (recirc year) | 0.6 (non recirc) 1.8 (recirc heat) 3.2 (recirc year) | 1.73 | 0.3 (w/o reset) 0.7 (w/ reset heat) 1.1 (w/reset year) | 0.4 (non recirc) 1.2 (recirc heat) 2.1 (recirc year) | 0.6 (non recirc) 1.6 (recirc heat) 2.8 (recirc year) |
| Annual Gas Savings (therms/yr/ft) | 2.0 (w/o reset) 4.1 (w/ reset heat) 5.3 (w/reset year) | 4.3 (non recirc) 13.0 (recirc heat) 23.0 (recirc year) | 4.9(non recirc) 14.9 (recirc heat) 26.3 (recirc year) | 5.02 | 9.1 (w/o reset) 21.8 (w/ reset heat) 32.4 (w/reset year) | 13.2 (non recirc) 40.2 (recirc heat) 71.1 (recirc year) | 16.5 (non recirc) 50.4 (recirc heat) 89 (recirc year) |
| Elbows, Tees, Flanges, & Valves |  |  |  |  |  |  |  |
| Number of Elbows | 5 | 10 | 20 | n/a | 5 | 10 | 20 |
| Number of Tees | 5 | 10 | 20 | n/a | 5 | 10 | 20 |
| Number of Flanges | 5 | 10 | 20 | n/a | 5 | 10 | 20 |
| Number of Valves | 5 | 10 | 20 | n/a | 5 | 10 | 20 |
| Annual Energy Savings |  |  |  |  |  |  |  |
| Total Gas Savings (therms/yr) | 39 (w/o reset) 80 (w/ reset heat) 104 (w/reset year) | 478 (non recirc) 1,456 (recirc heat) 2,571 (recirc year) | 1,072 (non recirc) 3,267 (recirc heat) 5,770 (recirc year) | 502 | 930 (w/o reset) 2,832 (w/ reset heat) 4,211 (w/reset year) | 2,112 (non recirc) 6,434 (recirc heat) 11,364 (recirc year) | 3,635 (non recirc) 11,074 (recirc heat) 19,560 (recirc year) |

Heat = heating season only, year = year round

Values below must be multiplied by the appropriate Thermal Regain Factor (TRF). All variables were the same except for hours of operation in the calculation of the default savings per foot for the various building types and applications as presented in the table below:

Savings Summary for Indoor pipe insulation by System Type and Building Type (Δtherms per foot) (continues for 3.5 pages)

| Location | System Type | Building Type | Annual therm Savings per linear foot (therm /ft) (2" pipe / 1" insulation for hot water, 2" insulation for steam) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Indoor | Hot Water Space Heating with outdoor reset – non-recirculation | Assembly | 1.32 | 1.36 | 1.21 | 0.81 | 1.24 |
|  |  | Assisted Living | 1.25 | 1.22 | 1.07 | 0.79 | 0.95 |
|  |  | College | 1.13 | 1.06 | 0.95 | 0.53 | 0.63 |
|  |  | Convenience Store | 1.10 | 1.01 | 0.90 | 0.65 | 0.72 |
|  |  | Elementary School | 1.32 | 1.29 | 1.13 | 0.78 | 0.95 |
|  |  | Garage | 0.73 | 0.72 | 0.63 | 0.50 | 0.56 |
|  |  | Grocery | 1.19 | 1.19 | 1.04 | 0.65 | 0.78 |
|  |  | Healthcare Clinic | 1.17 | 1.20 | 1.05 | 0.71 | 0.75 |
|  |  | High School | 1.37 | 1.38 | 1.23 | 0.88 | 1.03 |
|  |  | Hospital - CAV no econ | 1.31 | 1.35 | 1.15 | 0.99 | 1.12 |
|  |  | Hospital - CAV econ | 1.33 | 1.37 | 1.17 | 1.01 | 1.15 |
|  |  | Hospital - VAV econ | 0.54 | 0.51 | 0.39 | 0.23 | 0.25 |
|  |  | Hospital - FCU | 0.98 | 1.12 | 0.91 | 1.07 | 1.44 |
|  |  | Hotel/Motel | 1.31 | 1.27 | 1.14 | 0.78 | 0.96 |
|  |  | Hotel/Motel - Common | 1.19 | 1.21 | 1.15 | 0.93 | 0.98 |
|  |  | Hotel/Motel - Guest | 1.30 | 1.26 | 1.13 | 0.75 | 0.93 |
|  |  | Manufacturing Facility | 0.78 | 0.75 | 0.70 | 0.42 | 0.47 |
|  |  | MF - High Rise | 1.13 | 1.12 | 1.02 | 0.87 | 0.87 |
|  |  | MF - High Rise - Common | 1.35 | 1.31 | 1.17 | 0.81 | 1.04 |
|  |  | MF - High Rise - Residential | 1.09 | 1.08 | 0.99 | 0.85 | 0.83 |
|  |  | MF - Mid Rise | 1.23 | 1.25 | 1.07 | 0.79 | 0.90 |
|  |  | Movie Theater | 1.35 | 1.33 | 1.24 | 0.94 | 1.12 |
|  |  | Office - High Rise - CAV no econ | 1.50 | 1.52 | 1.38 | 0.93 | 1.01 |
|  |  | Office - High Rise - CAV econ | 1.55 | 1.58 | 1.45 | 1.00 | 1.10 |
|  |  | Office - High Rise - VAV econ | 1.13 | 1.15 | 0.95 | 0.56 | 0.63 |
|  |  | Office - High Rise - FCU | 0.83 | 0.82 | 0.71 | 0.37 | 0.39 |
|  |  | Office - Low Rise | 1.06 | 1.06 | 0.84 | 0.51 | 0.59 |
|  |  | Office - Mid Rise | 1.17 | 1.18 | 0.99 | 0.63 | 0.70 |
|  |  | Religious Building | 1.19 | 1.11 | 1.07 | 0.78 | 0.89 |
|  |  | Restaurant | 1.00 | 1.00 | 0.90 | 0.68 | 0.81 |
|  |  | Retail - Department Store | 1.03 | 0.95 | 0.89 | 0.58 | 0.66 |
|  |  | Retail - Strip Mall | 0.99 | 0.91 | 0.81 | 0.56 | 0.60 |
|  |  | Warehouse | 1.08 | 1.01 | 1.04 | 0.65 | 0.80 |
|  |  | Unknown | 1.15 | 1.14 | 1.01 | 0.73 | 0.84 |

|  |  |  | Annual therm Savings per linear foot (therm /ft) (2" pipe / 1" insulation for hot water, 2" insulation for steam) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location | System Type | Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Indoor | Hot Water Space Heating without outdoor reset – non-recirculation | Assembly | 1.96 | 2.00 | 1.79 | 1.19 | 1.83 |  |
|  |  | Assisted Living | 1.84 | 1.80 | 1.58 | 1.16 | 1.40 |  |
|  |  | College | 1.67 | 1.56 | 1.40 | 0.78 | 0.93 |  |
|  |  | Convenience Store | 1.62 | 1.50 | 1.33 | 0.95 | 1.06 |  |
|  |  | Elementary School | 1.95 | 1.90 | 1.68 | 1.16 | 1.40 |  |
|  |  | Garage | 1.08 | 1.06 | 0.93 | 0.74 | 0.82 |  |
|  |  | Grocery | 1.76 | 1.75 | 1.54 | 0.96 | 1.15 |  |
|  |  | Healthcare Clinic | 1.73 | 1.77 | 1.55 | 1.05 | 1.11 |  |
|  |  | High School | 2.02 | 2.03 | 1.82 | 1.30 | 1.52 |  |
|  |  | Hospital - CAV no econ | 1.93 | 1.99 | 1.69 | 1.46 | 1.65 |  |
|  |  | Hospital - CAV econ | 1.96 | 2.03 | 1.73 | 1.50 | 1.70 |  |
|  |  | Hospital - VAV econ | 0.80 | 0.76 | 0.57 | 0.34 | 0.37 |  |
|  |  | Hospital - FCU | 1.45 | 1.65 | 1.35 | 1.58 | 2.13 |  |
|  |  | Hotel/Motel | 1.93 | 1.87 | 1.69 | 1.16 | 1.41 |  |
|  |  | Hotel/Motel - Common | 1.75 | 1.78 | 1.69 | 1.38 | 1.45 |  |
|  |  | Hotel/Motel - Guest | 1.92 | 1.86 | 1.66 | 1.11 | 1.37 |  |
|  |  | Manufacturing Facility | 1.15 | 1.11 | 1.03 | 0.62 | 0.69 |  |
|  |  | MF - High Rise | 1.67 | 1.65 | 1.50 | 1.28 | 1.28 |  |
|  |  | MF - High Rise - Common | 1.99 | 1.93 | 1.73 | 1.19 | 1.54 |  |
|  |  | MF - High Rise - Residential | 1.61 | 1.60 | 1.46 | 1.26 | 1.23 |  |
|  |  | MF - Mid Rise | 1.82 | 1.84 | 1.59 | 1.17 | 1.33 |  |
|  |  | Movie Theater | 1.99 | 1.96 | 1.83 | 1.39 | 1.66 |  |
|  |  | Office - High Rise - CAV no econ | 2.21 | 2.24 | 2.04 | 1.37 | 1.49 |  |
|  |  | Office - High Rise - CAV econ | 2.29 | 2.33 | 2.14 | 1.48 | 1.63 |  |
|  |  | Office - High Rise - VAV econ | 1.67 | 1.70 | 1.40 | 0.83 | 0.93 |  |
|  |  | Office - High Rise - FCU | 1.22 | 1.21 | 1.04 | 0.55 | 0.58 |  |
|  |  | Office - Low Rise | 1.56 | 1.56 | 1.24 | 0.76 | 0.87 |  |
|  |  | Office - Mid Rise | 1.73 | 1.74 | 1.47 | 0.94 | 1.04 |  |
|  |  | Religious Building | 1.75 | 1.65 | 1.58 | 1.15 | 1.32 |  |
|  |  | Restaurant | 1.48 | 1.48 | 1.33 | 1.01 | 1.19 |  |
|  |  | Retail - Department Store | 1.52 | 1.40 | 1.31 | 0.85 | 0.97 |  |
|  |  | Retail - Strip Mall | 1.46 | 1.35 | 1.19 | 0.82 | 0.89 |  |
|  |  | Warehouse | 1.59 | 1.49 | 1.53 | 0.96 | 1.18 |  |
|  |  | Unknown | 1.70 | 1.68 | 1.50 | 1.07 | 1.25 |  |
|  | Hot Water with outdoor reset | All buildings, Recirculation heating season only (Hours below 55F) | 3.73 | 3.68 | 3.33 | 2.98 | 3.08 |  |
|  | Hot Water w/o outdoor reset | All buildings, Recirculation heating season only (Hours below 55F) | 5.51 | 5.43 | 4.92 | 4.40 | 4.54 |  |
|  | Hot Water with outdoor reset | All buildings, Recirculation year round (All hours) | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 |  |
|  | Hot Water w/o outdoor reset | All buildings, Recirculation year round (All hours) | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 |  |
|  | Domestic Hot Water | DHW circulation loop | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 |  |

|  |  |  | Annual therm Savings per linear foot (therm /ft) (2" pipe / 1" insulation for hot water, 2" insulation for steam) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location | System Type | Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
|  | LP Steam – non-recirculation | Assembly | 4.25 | 4.36 | 3.89 | 2.59 | 3.97 |  |
|  |  | Assisted Living | 4.01 | 3.92 | 3.44 | 2.53 | 3.04 |  |
|  |  | College | 3.64 | 3.40 | 3.04 | 1.69 | 2.02 |  |
|  |  | Convenience Store | 3.52 | 3.26 | 2.89 | 2.07 | 2.32 |  |
|  |  | Elementary School | 4.24 | 4.13 | 3.64 | 2.52 | 3.05 |  |
|  |  | Garage | 2.34 | 2.31 | 2.03 | 1.62 | 1.79 |  |
|  |  | Grocery | 3.83 | 3.81 | 3.34 | 2.08 | 2.49 |  |
|  |  | Healthcare Clinic | 3.76 | 3.85 | 3.36 | 2.29 | 2.42 |  |
|  |  | High School | 4.39 | 4.42 | 3.96 | 2.82 | 3.30 |  |
|  |  | Hospital - CAV no econ | 4.20 | 4.33 | 3.69 | 3.17 | 3.60 |  |
|  |  | Hospital - CAV econ | 4.25 | 4.41 | 3.76 | 3.26 | 3.70 |  |
|  |  | Hospital - VAV econ | 1.74 | 1.65 | 1.24 | 0.75 | 0.81 |  |
|  |  | Hospital - FCU | 3.15 | 3.60 | 2.93 | 3.44 | 4.63 |  |
|  |  | Hotel/Motel | 4.19 | 4.07 | 3.67 | 2.51 | 3.07 |  |
|  |  | Hotel/Motel - Common | 3.81 | 3.87 | 3.68 | 3.00 | 3.15 |  |
|  |  | Hotel/Motel - Guest | 4.18 | 4.05 | 3.62 | 2.42 | 2.98 |  |
|  |  | Manufacturing Facility | 2.49 | 2.41 | 2.23 | 1.35 | 1.51 |  |
|  |  | MF - High Rise | 4.52 | 4.46 | 4.07 | 3.46 | 3.47 |  |
|  |  | MF - High Rise - Common | 5.38 | 5.22 | 4.68 | 3.23 | 4.17 |  |
|  |  | MF - High Rise - Residential | 4.37 | 4.34 | 3.94 | 3.41 | 3.33 |  |
|  |  | MF - Mid Rise | 4.94 | 4.99 | 4.30 | 3.16 | 3.60 |  |
|  |  | Movie Theater | 4.33 | 4.26 | 3.98 | 3.03 | 3.61 |  |
|  |  | Office - High Rise - CAV no econ | 4.81 | 4.88 | 4.45 | 2.98 | 3.24 |  |
|  |  | Office - High Rise - CAV econ | 4.97 | 5.07 | 4.66 | 3.21 | 3.54 |  |
|  |  | Office - High Rise - VAV econ | 3.64 | 3.71 | 3.06 | 1.81 | 2.01 |  |
|  |  | Office - High Rise - FCU | 2.66 | 2.62 | 2.27 | 1.20 | 1.26 |  |
|  |  | Office - Low Rise | 3.40 | 3.39 | 2.69 | 1.65 | 1.89 |  |
|  |  | Office - Mid Rise | 3.77 | 3.78 | 3.19 | 2.03 | 2.26 |  |
|  |  | Religious Building | 3.82 | 3.58 | 3.43 | 2.51 | 2.87 |  |
|  |  | Restaurant | 3.21 | 3.22 | 2.89 | 2.19 | 2.60 |  |
|  |  | Retail - Department Store | 3.31 | 3.04 | 2.86 | 1.86 | 2.12 |  |
|  |  | Retail - Strip Mall | 3.17 | 2.94 | 2.59 | 1.79 | 1.93 |  |
|  |  | Warehouse | 3.46 | 3.23 | 3.33 | 2.08 | 2.56 |  |
|  |  | Unknown | 3.70 | 3.66 | 3.26 | 2.34 | 2.71 |  |
|  | LP Steam | All buildings, Recirculation heating season only (Hours below 55F) | 11.99 | 11.81 | 10.70 | 9.57 | 9.88 |  |
|  | LP Steam | All buildings, Recirculation year round (All hours) | 20.84 | 20.84 | 20.84 | 20.84 | 20.84 |  |

|  |  |  | Annual therm Savings per linear foot (therm /ft) (2" pipe / 1" insulation for hot water, 2" insulation for steam) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location | System Type | Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
|  | HP Steam – non-recirculation | Assembly | 8.02 | 8.22 | 7.34 | 4.89 | 7.49 |  |
|  |  | Assisted Living | 7.56 | 7.39 | 6.49 | 4.77 | 5.73 |  |
|  |  | College | 6.87 | 6.42 | 5.73 | 3.18 | 3.81 |  |
|  |  | Convenience Store | 6.65 | 6.14 | 5.45 | 3.91 | 4.37 |  |
|  |  | Elementary School | 8.00 | 7.79 | 6.87 | 4.75 | 5.76 |  |
|  |  | Garage | 4.42 | 4.35 | 3.82 | 3.05 | 3.38 |  |
|  |  | Grocery | 7.22 | 7.19 | 6.30 | 3.93 | 4.70 |  |
|  |  | Healthcare Clinic | 7.09 | 7.27 | 6.35 | 4.32 | 4.57 |  |
|  |  | High School | 8.28 | 8.34 | 7.48 | 5.33 | 6.23 |  |
|  |  | Hospital - CAV no econ | 7.92 | 8.16 | 6.95 | 5.98 | 6.79 |  |
|  |  | Hospital - CAV econ | 8.03 | 8.32 | 7.09 | 6.14 | 6.98 |  |
|  |  | Hospital - VAV econ | 3.28 | 3.12 | 2.35 | 1.41 | 1.53 |  |
|  |  | Hospital - FCU | 5.95 | 6.79 | 5.53 | 6.50 | 8.73 |  |
|  |  | Hotel/Motel | 7.91 | 7.69 | 6.93 | 4.74 | 5.79 |  |
|  |  | Hotel/Motel - Common | 7.18 | 7.30 | 6.95 | 5.65 | 5.94 |  |
|  |  | Hotel/Motel - Guest | 7.89 | 7.64 | 6.83 | 4.57 | 5.62 |  |
|  |  | Manufacturing Facility | 4.70 | 4.55 | 4.22 | 2.55 | 2.84 |  |
|  |  | MF - High Rise | 6.85 | 6.76 | 6.16 | 5.25 | 5.26 |  |
|  |  | MF - High Rise - Common | 8.15 | 7.91 | 7.09 | 4.89 | 6.31 |  |
|  |  | MF - High Rise - Residential | 6.62 | 6.57 | 5.97 | 5.17 | 5.04 |  |
|  |  | MF - Mid Rise | 7.48 | 7.57 | 6.51 | 4.79 | 5.46 |  |
|  |  | Movie Theater | 8.16 | 8.04 | 7.52 | 5.71 | 6.80 |  |
|  |  | Office - High Rise - CAV no econ | 9.07 | 9.20 | 8.39 | 5.62 | 6.12 |  |
|  |  | Office - High Rise - CAV econ | 9.38 | 9.57 | 8.80 | 6.06 | 6.67 |  |
|  |  | Office - High Rise - VAV econ | 6.86 | 6.99 | 5.76 | 3.41 | 3.80 |  |
|  |  | Office - High Rise - FCU | 5.02 | 4.95 | 4.27 | 2.27 | 2.38 |  |
|  |  | Office - Low Rise | 6.41 | 6.40 | 5.08 | 3.11 | 3.56 |  |
|  |  | Office - Mid Rise | 7.12 | 7.12 | 6.03 | 3.84 | 4.27 |  |
|  |  | Religious Building | 7.20 | 6.75 | 6.46 | 4.73 | 5.41 |  |
|  |  | Restaurant | 6.06 | 6.08 | 5.46 | 4.13 | 4.90 |  |
|  |  | Retail - Department Store | 6.25 | 5.74 | 5.39 | 3.51 | 4.00 |  |
|  |  | Retail - Strip Mall | 5.98 | 5.54 | 4.89 | 3.37 | 3.63 |  |
|  |  | Warehouse | 6.53 | 6.09 | 6.29 | 3.93 | 4.84 |  |
|  |  | Unknown | 6.97 | 6.91 | 6.14 | 4.41 | 5.11 |  |
|  | HP Steam | All buildings, Recirculation heating season only (Hours below 55F) | 22.62 | 22.28 | 20.18 | 18.05 | 18.63 |  |
|  | HP Steam | All buildings, Recirculation year round (All hours) | 39.32 | 39.32 | 39.32 | 39.32 | 39.32 |  |

Savings Summary for Outdoor pipe insulation by System Type and Building Type (Δtherms per foot) (continues for 3.5 pages)

|  |  |  | Annual therm Savings per linear foot (therm /ft) (2" pipe / 1" insulation for hot water, 2" insulation for steam) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location | System Type | Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Outdoor | Hot Water Space Heating with outdoor reset – non-recirculation | Assembly | 5.61 | 5.75 | 5.14 | 3.42 | 5.24 |
|  |  | Assisted Living | 5.28 | 5.17 | 4.54 | 3.34 | 4.01 |
|  |  | College | 4.80 | 4.49 | 4.00 | 2.23 | 2.66 |
|  |  | Convenience Store | 4.65 | 4.29 | 3.81 | 2.74 | 3.06 |
|  |  | Elementary School | 5.59 | 5.45 | 4.81 | 3.32 | 4.03 |
|  |  | Garage | 3.09 | 3.04 | 2.67 | 2.13 | 2.36 |
|  |  | Grocery | 5.05 | 5.03 | 4.41 | 2.75 | 3.29 |
|  |  | Healthcare Clinic | 4.96 | 5.08 | 4.44 | 3.03 | 3.20 |
|  |  | High School | 5.79 | 5.83 | 5.23 | 3.72 | 4.36 |
|  |  | Hospital - CAV no econ | 5.54 | 5.71 | 4.86 | 4.18 | 4.74 |
|  |  | Hospital - CAV econ | 5.62 | 5.82 | 4.96 | 4.30 | 4.88 |
|  |  | Hospital - VAV econ | 2.29 | 2.18 | 1.64 | 0.98 | 1.07 |
|  |  | Hospital - FCU | 4.16 | 4.75 | 3.87 | 4.54 | 6.11 |
|  |  | Hotel/Motel | 5.53 | 5.37 | 4.85 | 3.32 | 4.05 |
|  |  | Hotel/Motel - Common | 5.02 | 5.11 | 4.86 | 3.95 | 4.15 |
|  |  | Hotel/Motel - Guest | 5.52 | 5.34 | 4.77 | 3.20 | 3.93 |
|  |  | Manufacturing Facility | 3.29 | 3.18 | 2.95 | 1.78 | 1.99 |
|  |  | MF - High Rise | 4.80 | 4.73 | 4.31 | 3.67 | 3.68 |
|  |  | MF - High Rise - Common | 5.70 | 5.54 | 4.96 | 3.42 | 4.41 |
|  |  | MF - High Rise - Residential | 4.63 | 4.60 | 4.17 | 3.62 | 3.53 |
|  |  | MF - Mid Rise | 5.23 | 5.29 | 4.55 | 3.35 | 3.82 |
|  |  | Movie Theater | 5.71 | 5.62 | 5.25 | 4.00 | 4.76 |
|  |  | Office - High Rise - CAV no econ | 6.34 | 6.44 | 5.87 | 3.93 | 4.28 |
|  |  | Office - High Rise - CAV econ | 6.56 | 6.69 | 6.16 | 4.24 | 4.67 |
|  |  | Office - High Rise - VAV econ | 4.80 | 4.89 | 4.03 | 2.38 | 2.66 |
|  |  | Office - High Rise - FCU | 3.52 | 3.46 | 2.99 | 1.58 | 1.67 |
|  |  | Office - Low Rise | 4.48 | 4.48 | 3.55 | 2.18 | 2.49 |
|  |  | Office - Mid Rise | 4.98 | 4.98 | 4.22 | 2.69 | 2.98 |
|  |  | Religious Building | 5.03 | 4.72 | 4.52 | 3.31 | 3.78 |
|  |  | Restaurant | 4.24 | 4.26 | 3.82 | 2.89 | 3.43 |
|  |  | Retail - Department Store | 4.37 | 4.01 | 3.77 | 2.45 | 2.80 |
|  |  | Retail - Strip Mall | 4.18 | 3.87 | 3.42 | 2.36 | 2.55 |
|  |  | Warehouse | 4.57 | 4.26 | 4.40 | 2.75 | 3.38 |
|  |  | Unknown | 4.88 | 4.83 | 4.30 | 3.09 | 3.57 |
|  | Hot Water Space Heating without outdoor reset – non-recirculation | Assembly | 7.10 | 7.27 | 6.49 | 4.33 | 6.63 |
|  |  | Assisted Living | 6.69 | 6.53 | 5.74 | 4.22 | 5.08 |
|  |  | College | 6.08 | 5.68 | 5.07 | 2.81 | 3.37 |
|  |  | Convenience Store | 5.88 | 5.43 | 4.82 | 3.46 | 3.86 |
|  |  | Elementary School | 7.07 | 6.90 | 6.08 | 4.20 | 5.10 |
|  |  | Garage | 3.91 | 3.85 | 3.38 | 2.70 | 2.99 |
|  |  | Grocery | 6.39 | 6.36 | 5.58 | 3.48 | 4.16 |
|  |  | Healthcare Clinic | 6.27 | 6.44 | 5.62 | 3.83 | 4.05 |
|  |  | High School | 7.33 | 7.38 | 6.62 | 4.71 | 5.51 |
|  |  | Hospital - CAV no econ | 7.01 | 7.22 | 6.15 | 5.29 | 6.00 |
|  |  | Hospital - CAV econ | 7.10 | 7.36 | 6.28 | 5.44 | 6.17 |
|  |  | Hospital - VAV econ | 2.91 | 2.76 | 2.07 | 1.24 | 1.35 |
|  |  | Hospital - FCU | 5.26 | 6.01 | 4.89 | 5.75 | 7.73 |
|  |  | Hotel/Motel | 6.99 | 6.80 | 6.13 | 4.20 | 5.12 |
|  |  | Hotel/Motel - Common | 6.36 | 6.46 | 6.15 | 5.00 | 5.25 |
|  |  | Hotel/Motel - Guest | 6.99 | 6.76 | 6.04 | 4.05 | 4.97 |
|  |  | Manufacturing Facility | 4.17 | 4.03 | 3.73 | 2.26 | 2.52 |
|  |  | MF - High Rise | 6.06 | 5.98 | 5.45 | 4.64 | 4.65 |
|  |  | MF - High Rise - Common | 7.21 | 7.00 | 6.28 | 4.33 | 5.58 |
|  |  | MF - High Rise - Residential | 5.86 | 5.82 | 5.28 | 4.57 | 4.46 |
|  |  | MF - Mid Rise | 6.62 | 6.70 | 5.76 | 4.24 | 4.83 |
|  |  | Movie Theater | 7.22 | 7.11 | 6.65 | 5.05 | 6.02 |
|  |  | Office - High Rise - CAV no econ | 8.02 | 8.15 | 7.42 | 4.97 | 5.42 |
|  |  | Office - High Rise - CAV econ | 8.30 | 8.47 | 7.78 | 5.37 | 5.91 |
|  |  | Office - High Rise - VAV econ | 6.07 | 6.19 | 5.10 | 3.01 | 3.36 |
|  |  | [Grab your reader’s attention with a great quote from the document or use this space to emphasize a key point. To place this text box anywhere on the page, just drag it.] Office - High Rise - FCU | 4.44 | 4.37 | 3.78 | 2.01 | 2.10 |
|  |  | Office - Low Rise | 5.68 | 5.66 | 4.50 | 2.75 | 3.15 |
|  |  | Office - Mid Rise | 6.30 | 6.30 | 5.34 | 3.40 | 3.77 |
|  |  | Religious Building | 6.37 | 5.97 | 5.72 | 4.19 | 4.79 |
|  |  | Restaurant | 5.37 | 5.38 | 4.83 | 3.66 | 4.33 |
|  |  | Retail - Department Store | 5.53 | 5.08 | 4.77 | 3.10 | 3.54 |
|  |  | Retail - Strip Mall | 5.29 | 4.90 | 4.33 | 2.98 | 3.22 |
|  |  | Warehouse | 5.78 | 5.39 | 5.56 | 3.47 | 4.28 |
|  |  | Unknown | 6.17 | 6.11 | 5.44 | 3.90 | 4.52 |
|  | Hot Water with outdoor reset | All buildings, Recirculation heating season only (Hours below 55F) | 15.82 | 15.58 | 14.11 | 12.62 | 13.03 |
|  | Hot Water without outdoor reset | All buildings, Recirculation heating season only (Hours below 55F) | 20.02 | 19.71 | 17.86 | 15.97 | 16.49 |
|  | Hot Water with outdoor reset | All buildings, Recirculation year round (All hours) | 23.16 | 23.16 | 23.16 | 23.16 | 23.16 |
|  | Hot Water without outdoor reset | All buildings, Recirculation year round (All hours) | 34.79 | 34.79 | 34.79 | 34.79 | 34.79 |
|  | LP Steam – non-recirculation | Assembly | 11.11 | 11.38 | 10.16 | 6.77 | 10.37 |
|  |  | Assisted Living | 10.46 | 10.23 | 8.99 | 6.61 | 7.94 |
|  |  | College | 9.51 | 8.89 | 7.93 | 4.40 | 5.28 |
|  |  | Convenience Store | 9.21 | 8.50 | 7.55 | 5.42 | 6.05 |
|  |  | Elementary School | 11.07 | 10.79 | 9.52 | 6.57 | 7.98 |
|  |  | Garage | 6.12 | 6.02 | 5.29 | 4.23 | 4.68 |
|  |  | Grocery | 10.00 | 9.96 | 8.73 | 5.45 | 6.50 |
|  |  | Healthcare Clinic | 9.81 | 10.07 | 8.79 | 5.99 | 6.33 |
|  |  | High School | 11.47 | 11.54 | 10.35 | 7.38 | 8.63 |
|  |  | Hospital - CAV no econ | 10.97 | 11.30 | 9.63 | 8.28 | 9.40 |
|  |  | Hospital - CAV econ | 11.11 | 11.52 | 9.82 | 8.51 | 9.66 |
|  |  | Hospital - VAV econ | 4.54 | 4.32 | 3.25 | 1.95 | 2.11 |
|  |  | Hospital - FCU | 8.24 | 9.41 | 7.66 | 9.00 | 12.10 |
|  |  | Hotel/Motel | 10.95 | 10.64 | 9.60 | 6.56 | 8.02 |
|  |  | Hotel/Motel - Common | 9.95 | 10.11 | 9.62 | 7.83 | 8.23 |
|  |  | Hotel/Motel - Guest | 10.93 | 10.57 | 9.46 | 6.33 | 7.78 |
|  |  | Manufacturing Facility | 6.51 | 6.30 | 5.84 | 3.53 | 3.94 |
|  |  | MF - High Rise | 11.82 | 11.66 | 10.63 | 9.05 | 9.07 |
|  |  | MF - High Rise - Common | 14.05 | 13.65 | 12.23 | 8.43 | 10.89 |
|  |  | MF - High Rise - Residential | 11.42 | 11.33 | 10.30 | 8.92 | 8.70 |
|  |  | MF - Mid Rise | 12.90 | 13.05 | 11.23 | 8.26 | 9.41 |
|  |  | Movie Theater | 11.30 | 11.14 | 10.41 | 7.91 | 9.42 |
|  |  | Office - High Rise - CAV no econ | 12.56 | 12.74 | 11.62 | 7.78 | 8.47 |
|  |  | Office - High Rise - CAV econ | 12.99 | 13.25 | 12.19 | 8.40 | 9.24 |
|  |  | Office - High Rise - VAV econ | 9.49 | 9.69 | 7.98 | 4.71 | 5.26 |
|  |  | Office - High Rise - FCU | 6.96 | 6.85 | 5.92 | 3.15 | 3.29 |
|  |  | Office - Low Rise | 8.88 | 8.86 | 7.04 | 4.31 | 4.93 |
|  |  | Office - Mid Rise | 9.86 | 9.86 | 8.35 | 5.31 | 5.91 |
|  |  | Religious Building | 9.97 | 9.35 | 8.95 | 6.56 | 7.50 |
|  |  | Restaurant | 8.39 | 8.42 | 7.56 | 5.72 | 6.78 |
|  |  | Retail - Department Store | 8.65 | 7.95 | 7.46 | 4.85 | 5.54 |
|  |  | Retail - Strip Mall | 8.28 | 7.67 | 6.77 | 4.67 | 5.03 |
|  |  | Warehouse | 9.05 | 8.44 | 8.71 | 5.44 | 6.70 |
|  |  | Unknown | 9.66 | 9.57 | 8.51 | 6.11 | 7.08 |
|  | LP Steam | All buildings, Recirculation heating season only (Hours below 55F) | 31.32 | 30.85 | 27.94 | 25.00 | 25.80 |
|  | LP Steam | All buildings, Recirculation year round (All hours) | 54.46 | 54.46 | 54.46 | 54.46 | 54.46 |
|  | HP Steam – non-recirculation | Assembly | 17.20 | 17.62 | 15.73 | 10.48 | 16.06 |
|  |  | Assisted Living | 16.20 | 15.84 | 13.91 | 10.23 | 12.29 |
|  |  | College | 14.73 | 13.76 | 12.28 | 6.82 | 8.17 |
|  |  | Convenience Store | 14.25 | 13.16 | 11.68 | 8.38 | 9.36 |
|  |  | Elementary School | 17.14 | 16.70 | 14.73 | 10.18 | 12.35 |
|  |  | Garage | 9.47 | 9.32 | 8.20 | 6.54 | 7.24 |
|  |  | Grocery | 15.47 | 15.41 | 13.51 | 8.43 | 10.07 |
|  |  | Healthcare Clinic | 15.19 | 15.59 | 13.61 | 9.27 | 9.81 |
|  |  | High School | 17.75 | 17.87 | 16.03 | 11.42 | 13.36 |
|  |  | Hospital - CAV no econ | 16.98 | 17.49 | 14.90 | 12.82 | 14.55 |
|  |  | Hospital - CAV econ | 17.21 | 17.83 | 15.20 | 13.17 | 14.96 |
|  |  | Hospital - VAV econ | 7.04 | 6.68 | 5.02 | 3.02 | 3.27 |
|  |  | Hospital - FCU | 12.76 | 14.56 | 11.85 | 13.93 | 18.73 |
|  |  | Hotel/Motel | 16.95 | 16.48 | 14.86 | 10.17 | 12.41 |
|  |  | Hotel/Motel - Common | 15.40 | 15.65 | 14.90 | 12.12 | 12.74 |
|  |  | Hotel/Motel - Guest | 16.92 | 16.38 | 14.64 | 9.80 | 12.05 |
|  |  | Manufacturing Facility | 10.09 | 9.75 | 9.04 | 5.46 | 6.10 |
|  |  | MF - High Rise | 14.69 | 14.50 | 13.22 | 11.25 | 11.28 |
|  |  | MF - High Rise - Common | 17.46 | 16.96 | 15.21 | 10.48 | 13.53 |
|  |  | MF - High Rise - Residential | 14.19 | 14.08 | 12.80 | 11.09 | 10.81 |
|  |  | MF - Mid Rise | 16.04 | 16.22 | 13.96 | 10.26 | 11.70 |
|  |  | Movie Theater | 17.49 | 17.23 | 16.12 | 12.25 | 14.59 |
|  |  | Office - High Rise - CAV no econ | 19.44 | 19.73 | 17.98 | 12.05 | 13.12 |
|  |  | Office - High Rise - CAV econ | 20.10 | 20.51 | 18.86 | 13.00 | 14.30 |
|  |  | Office - High Rise - VAV econ | 14.70 | 14.99 | 12.36 | 7.30 | 8.14 |
|  |  | Office - High Rise - FCU | 10.76 | 10.60 | 9.16 | 4.86 | 5.10 |
|  |  | Office - Low Rise | 13.75 | 13.71 | 10.89 | 6.66 | 7.63 |
|  |  | Office - Mid Rise | 15.25 | 15.27 | 12.92 | 8.23 | 9.15 |
|  |  | Religious Building | 15.43 | 14.47 | 13.85 | 10.15 | 11.60 |
|  |  | Restaurant | 12.99 | 13.03 | 11.70 | 8.85 | 10.49 |
|  |  | Retail - Department Store | 13.39 | 12.31 | 11.55 | 7.52 | 8.57 |
|  |  | Retail - Strip Mall | 12.82 | 11.87 | 10.49 | 7.23 | 7.79 |
|  |  | Warehouse | 14.01 | 13.06 | 13.48 | 8.41 | 10.37 |
|  |  | Unknown | 14.95 | 14.81 | 13.17 | 9.45 | 10.96 |
|  | HP Steam | All buildings, Recirculation heating season only (Hours below 55F) | 48.49 | 47.76 | 43.25 | 38.69 | 39.94 |
|  | HP Steam | All buildings, Recirculation year round (All hours) | 84.30 | 84.30 | 84.30 | 84.30 | 84.30 |

For insulation covering elbows and tees that connect straight pipe, a calculated surface area will be assumed based on the dimensions for fittings given by ANSI/ASME B36.19. The surface area is then converted to an equivalent length of pipe that must be added to the total length of straight pipe in order to calculate total savings. Equivalent pipe lengths are given in 1” increments in pipe diameter for simplicity. In the case of pipe diameters in between full inch diameters, the closest equivalent length should be used. The larger pipe sizes mostly apply to steam header piping, which has the most heat loss per foot.

Calculated Surface Areas of Elbows and Tees

| Nominal Pipe Diameter | Calculated Surface Area (ft) |  |
| --- | --- | --- |
|  | 90 Degree Elbow | Straight Tee |
| 1” | 0.10 | 0.13 |
| 2” | 0.41 | 0.39 |
| 3” | 0.93 | 0.77 |
| 4” | 1.64 | 1.21 |
| 5” | 2.57 | 1.77 |
| 6” | 3.70 | 2.44 |
| 8” | 6.58 | 3.95 |
| 10” | 10.28 | 5.98 |
| 12” | 14.80 | 8.34 |

Equivalent Length of Other Components – Elbows and Tees (Loc)

| Nominal Pipe Diameter | Equivalent Length of Other Components (ft) |  |
| --- | --- | --- |
|  | 90 Degree Elbow | Straight Tee |
| 1” | 0.30 | 0.38 |
| 2” | 0.66 | 0.63 |
| 3” | 1.01 | 0.84 |
| 4” | 1.40 | 1.03 |
| 5” | 1.76 | 1.22 |
| 6” | 2.13 | 1.41 |
| 8” | 2.91 | 1.75 |
| 10” | 3.65 | 2.13 |
| 12” | 4.44 | 2.50 |

For insulation around valves or flanges, a surface area from ASTM standard C1129-12 will be assumed for 2” pipes. For 1” pipes, which weren’t included in the standard, a linear-trended value will be used. The surface area is then converted to an equivalent length of either 1” or 2” straight pipe that must be added to the total length of straight pipe in order to calculate total savings.

Calculated Surface Areas of Flanges and Valves

| Valves |  |  |  |  |  | Flanges |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Class (psi) | 150 | 300 | 600 | 900 |  | Class (psi) | 150 | 300 | 600 | 900 |
| NPS (in) | ft2 | ft2 | ft2 | ft2 |  | NPS (in) | ft2 | ft2 | ft2 | ft2 |
| 1 | 0.69 | 1.8 | 1.8 | 2.4 |  | 1 | 0.36 | 0.36 | 0.4 | 1.23 |
| 2 | 2.21 | 2.94 | 2.94 | 5.2 |  | 2 | 0.71 | 0.84 | 0.88 | 1.54 |
| 2.5 | 2.97 | 3.51 | 3.91 | 6.6 |  |  |  |  |  |  |
| 3 | 3.37 | 4.39 | 4.69 | 6.5 |  | 3 | 1.06 | 1.32 | 1.36 | 1.85 |
| 4 | 4.68 | 6.06 | 7.64 | 9.37 |  | 4 | 1.44 | 1.83 | 2.23 | 2.64 |
| 6 | 7.03 | 9.71 | 13.03 | 15.8 |  | 6 | 2.04 | 2.72 | 3.6 | 4.37 |
| 8 | 10.3 | 13.5 | 18.4 | 23.8 |  | 8 | 2.92 | 3.74 | 4.89 | 6.4 |
| 10 | 13.8 | 18 | 26.5 | 32.1 |  | 10 | 3.68 | 4.8 | 6.93 | 8.47 |
| 12 | 16.1 | 24.1 | 31.9 | 41.9 |  | 12 | 5.01 | 6.34 | 7.97 | 10.43 |

Equivalent Length of Other Components - Flanges and Valves (Loc)

| ANSI Class (psi) | Equivalent Length of Other Components (ft) |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1” Valve | 1” Flange | 2” Valve | 2” Flange |
| 150 | 2.00 | 1.04 | 3.56 | 1.14 |
| 300 | 5.22 | 1.04 | 4.73 | 1.35 |
| 600 | 5.22 | 1.16 | 4.73 | 1.42 |
| 900 | 6.96 | 3.57 | 8.37 | 2.48 |
| ANSI Class (psi) | 3" Valve | 3" Flange | 4" Valve | 4" Flange |
| 150 | 3.67 | 1.16 | 3.98 | 1.22 |
| 300 | 4.79 | 1.44 | 5.15 | 1.56 |
| 600 | 5.11 | 1.48 | 6.49 | 1.90 |
| 900 | 7.09 | 2.02 | 7.96 | 2.24 |

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-PINS-V07-220101

###### Review Deadline: 1/1/2024

### Single-Package and Split System Unitary Air Conditioners

###### Description

This measure promotes the installation of high-efficiency unitary air-, water-, and evaporatively-cooled air conditioning equipment, both single-package and split systems. Air conditioning (AC) systems are a major consumer of electricity and systems that exceed baseline efficiency requirements can significantly reduce energy consumption. This measure could apply to the replacing of an existing unit at the end of its useful life or the installation of a new unit in a new or existing building.

This measure was developed to be applicable to the following program types: TOS, NC, EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is assumed to be a high-efficiency air-, water-, or evaporatively-cooled air conditioner that exceeds the energy efficiency requirements as prescribed by the program.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to be a standard-efficiency air-, water, or evaporatively-cooled air conditioner that meets the Code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher) in effect on the date of equipment purchase (if date is unknown, assume current Code minimum).

For Early Replacement programs, use the actual efficiency of the existing unit or assume IECC code base in place at the original time of existing unit installation. To qualify under the early replacement characterization, baseline equipment must meet these additional qualifications:

- The existing unit is operational when replaced or the existing unit would be operational with minor repairs.

Note: IECC 2018 is scheduled to become effective July 1, 2019 and will become baseline for all New Construction permits from that date.

Note: new Federal Standards become effective January 1, 2023.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years.

For early replacement, the remaining life of existing equipment is assumed to be 5 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is based upon capacity and efficiency level (defined be CEE specifications), as outlined in the following table:

|  | Incremental cost ($/ton) |  |
| --- | --- | --- |
| Capacity | Up to and including CEE Tier 1 units | CEE Tier 2 and above |
| < 135,000 Btu/hr | $63 | $127 |
| 135,000 Btu/hr to > 250,000 Btu/hr | $63 | $127 |
| 250,000 Btu/hr and greater | $19 | $38 |

For early replacement the full cost of the installed unit should be used. If unknown use defaults below. The assumed deferred cost (after 5 years) of replacing existing equipment with a new baseline unit is also provided. This future cost should be discounted to present value using the real discount rate:

|  | Full Install Cost ($/ton) |  |  |
| --- | --- | --- | --- |
| Capacity | Base Units | Up to and including CEE Tier 1 units | CEE Tier 2 and above |
| < 135,000 Btu/hr | $895 | $958 | $1,021 |
| 135,000 Btu/hr to > 250,000 Btu/hr | $762 | $825 | $889 |
| 250,000 Btu/hr and greater | $673 | $691 | $710 |

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.  Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Time of Sale:

For units with cooling capacities less than 65 kBtu/hr:

ΔkWH	= (kBtu/hr) * [(1/SEERbase) – (1/SEERee)] * EFLH

For units with cooling capacities equal to or greater than 65 kBtu/hr:

ΔkWH	= (kBtu/hr) * [(1/IEERbase) – (1/IEERee)] * EFLH

Early replacement:

For units with cooling capacities less than 65 kBtu/hr:

For remaining life of existing unit (1st 5 years):

ΔkWH	= (kBtu/hr) * [(1/SEERexist) – (1/SEERee)] * EFLH

For remaining measure life (next 10 years):

ΔkWH	= (kBtu/hr) * [(1/SEERbase) – (1/SEERee)] * EFLH

For units with cooling capacities equal to or greater than 65 kBtu/hr:

For remaining life of existing unit (1st 5 years):

ΔkWH	= (kBtu/hr) * [(1/IEERexist) – (1/IEERee)] * EFLH

NOTE: If the existing equipment age is such that IEER ratings are not available, EER may be substitued when necessary. In such instances both existing and efficient unit efficiencies should be specified in EER.

For remaining measure life (next 10 years):

ΔkWH	= (kBtu/hr) * [(1/IEERbase) – (1/IEERee)] * EFLH

Where:

kBtu/hr 	= capacity of the cooling equipment actually installed in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr)

SEERbase 	= Seasonal Energy Efficiency Ratio of the baseline equipment

= SEER values from tables below, based on applicable Code on date of equipment purchase (if unknown assume current Code).

SEERee 		= Seasonal Energy Efficiency Ratio of the energy efficient equipment (actually installed)

SEERexist 	= Seasonal Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation

IEERbase 	= Integrated Energy Efficiency Ratio of the baseline equipment. See table below based on applicable Code on date of equipment purchase (if unknown assume current Code).

IEERee 		= Integrated Energy Efficiency Ratio of the energy efficient equipment (actually installed)

IEERexist 	= Integrated Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation

EFLH 	= Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

The rating conditions for the baseline and efficient equipment efficiencies must be equivalent.

Code of Federal Redulations (baseline effective 1/1/2019):

| Equipment type | Cooling capacity | Heating type | Efficiency level | Compliance date |
| --- | --- | --- | --- | --- |
| Small Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥65,000 Btu/h and <135,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 12.9 | 1/1/2018 |
|  |  | All Other Types of Heating | IEER = 12.7 | 1/1/2018 |
| Large Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥135,000 Btu/h and <240,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 12.4 | 1/1/2018 |
|  |  | All Other Types of Heating | IEER = 12.2 | 1/1/2018 |
| Very Large Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥240,000 Btu/h and <760,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 11.6 | 1/1/2018 |
|  |  | All Other Types of Heating | IEER = 11.4 | 1/1/2018 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Split-System) | <65,000 Btu/h | All | SEER = 13.0 | 6/16/2008 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Single-Package) | <65,000Btu/h | All | SEER = 14.0 | 1/1/2017 |

2015 IECC Minimum Efficiency Requirements (baseline effective 1/1/2016 to 3/30/2019)

2018 IECC Minimum Efficiency Requirements (baseline effective 7/1/2019 for New Construction measures)

For example, a 5 ton air cooled split system with a SEER of 15 at a retail strip mall in Rockford would save:

ΔkWH	= (60) * [(1/13) – (1/15)] * 950

= 585 kWh

###### Summer Coincident Peak Demand Savings

Time of Sale:

ΔkW 	= (kBtu/hr * (1/EERbase - 1/EERee)) * CF

Early Replacement:

For remaining life of existing unit (1st 5 years):

ΔkW	= (kBtu/hr) * [(1/EERexist) – (1/EERee)] * CF

For remaining measure life (next 10 years):

ΔkW	= (kBtu/hr) * [(1/EERbase) – (1/EERee)] * CF

Where:

EERbase 	= Energy Efficiency Ratio of the baseline equipment

= EER values from tables above, based on applicable Code on date of equipment purchase (if unknown assume current Code). (For air-cooled units < 65 kBtu/hr, assume the following conversion from SEER to EER for calculation of peak savings: EER = (-0.02 * SEER2) + (1.12 * SEER))

EERee 	= Energy Efficiency Ratio of the energy efficient equipment.  If the actual EERee is unknown, assume the conversion from SEER to EER for calculation of peak savings as above).

= Actual installed

EERexist 	= Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

For example, a 5 ton air cooled split system with a SEER of 15 in Rockford would save:

ΔkWSSP 	= (60) * [(1/11.2) – (1/12.3)] * .913

= 0.437 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Measure Code: CI-HVC-SPUA-V08-220101

###### Review Deadline: 1/1/2023

### Steam Trap Replacement or Repair

###### Description

The measure applies to the repair or replacement of steam traps in the failed open state that allow steam to escape the steam distribution system or return to the condensate receiver leading to increased steam generation.  The measure is applicable to commercial applications, commercial HVAC (low pressure steam) including multifamily buildings, low pressure industrial applications, medium pressure industrial applications, applications and high-pressure industrial applications.

This measure was developed to be applicable to the following program types: TOS, RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Customers must have steam traps in the failed open or leaking state to qualify for rebates.  However, if a commercial customer opts to replace all traps without inspection, rebates and the savings are discounted to take into consideration the fact that some traps are being replaced that have not yet failed.

###### Definition of Baseline Equipment

The baseline criterion is a faulty steam trapin the failed open or leaking state. No minimum leak rate is required.  Any leaking or blow through trap can be repaired or replaced.  If a commercial customer chooses to repair or replace all the steam traps at the facility without verification, the savings are adjusted. Savings for commercial full replacement projects are reduced by the percentage of traps found to be leaking on average from the studies listed.  If an audit is performed on a commercial site, then the leaking and blowdown can be adjusted.

###### Deemed Lifetime of Efficient Equipment

For standard steam traps the life of this measure is 6 years.

For Venturi steam traps the measure life is 20 years if replacing a faulty mechanical steam trap. If replacing an operational mechanical steam trap, the measure life is 14 years, having been reduced by the six-year measure life established for the Steam Trap Replacement or Repair measure from the IL TRM. By applying this conservative approach of reducing the measure life by the full estimated useful life of the existing steam trap, there is no need to survey or produce an inventory of the age of existing steam traps.

Venturi steam traps do not contain any moving parts, and their manufacturers cite this feature for the reduced failure rate leading to longer operational life than mechanical steam traps. Venturi steam traps have been observed to operate in excess of 20 years. Venturi steam traps also typically come with a 10-year warranty that can be extended up to 20 years. Therefore, savings may be claimed on a year-to-year basis for venturi steam traps undergoing annual maintenance that have exhausted their deemed 20-year measure life.

###### Deemed Measure Cost

| Steam System | Cost per trap ($) |
| --- | --- |
| Commercial Dry Cleaners | 77 |
| Commercial Heating (including Multifamily), low pressure steam | 77 |
| Industrial Medium Pressure >15 psig, < 30 psig | 180 |
| Steam Trap, Industrial Medium Pressure ≥30 <75 psig | 223 |
| Steam Trap, Industrial High Pressure ≥75 <125 psig | 276 |
| Steam Trap, Industrial High Pressure ≥125 <175 psig | 322 |
| Steam Trap, Industrial High Pressure ≥175 <250 psig | 370 |
| Steam Trap, Industrial High Pressure ≥250 psig | 418 |

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Energy Savings

###### Electric Energy Savings

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure but should not be included in TRC tests to avoid double counting the economic benefit of water savings.  These savings only apply to situations in which steam is lost from the steam system.

ΔkWhwater = ΔWater (gallons) / 1,000,000 * Ewater supply

Where

Ewater supply	= Water Supply Energy Factor (kWh/Million Gallons)

= 2,571

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

ΔTherm 	= Sa * (Hv + Hs * (T1 - Tsource)) * Hours * L / (100,000 * ηB)

Where:

Sa 	= Steam loss per leaking trap (lbs/hr)

For systems used in space heating applications that operate at 5 psig or lower, use the following equation to calculate Sa.  The condensate return system pressure, P2, will typically be atmospheric pressure, 14.696 psia.

Sa 	= 1519.3 * P1 * D2 * [(1/T1) * (γ/(γ-1)) * ((P2/P1)(2/γ) - (P2/P1)((γ+1)/γ))]0.5 * A * FF

For all other steam systems and applications, use the following equation.

Sa	= 24.24 * P1 * D2 * A * FF

Defaults are provided in table below if custom calculation is not performed.

Where:

1519.3	= Constant, (s2 * °R0.5)/(ft * hr)

P1 	= Average steam trap inlet pressure (absolute, psia).  If not available, use defaults provided in table below (note that defaults are provided in psig, not psia).

D	= Diameter of orifice, inches. Actual value should be used wherever possible as this value     has a significant impact on steam flowrate value.

T1 	= Temperature of Saturated Steam (°R)

= 507.89 * P10.0962

Where:

507.89 = Constant, °R*(in2/lbf)0.0962

γ 	= Heat Capacity Ratio (unitless)

= 5.071 * 10-4 * P1 + 1.332

P2 	= Average steam trap outlet pressure (absolute psia). If unknown, assume atmospheric pressure, 14.696 psia.

A 	= Adjustment factor

= 50%, all steam systems.  This factor accounts for reduction in the maximum theoretical steam flow to the average steam flow (the Enbridge factor).

FF	= Flow Factor.  In addition to the Adjustment factor (A), an additional 50 percent flow factor adjustment is recommended for medium and high-pressure steam systems to address industrial float and thermostatic style traps where additional blockage is possible.

24.24 	= Constant lbm/(hr-psia-in2)

Default Steam Loss per Trap (Sa) are provided below for different system types:

| Steam System | Average Steam Trap Inlet Pressure psig | Diameter of Orifice in | Adjustment Factor | Flow Factor | Average Actual Steam Loss per Leaking Trap (lbm/hr/trap) |  |
| --- | --- | --- | --- | --- | --- | --- |
| Commercial Dry Cleaners | 82.8 | 0.125 | 50% | 100% | 18.5 |  |
| Multifamily LPS Space Heating - calculate Sa as provided above. If using default value, cap total savings at 20% of building consumption | - | - | 50% | 100% | 6.9 |
| Commercial LPS Space Heating | - | - | 50% | 100% | 6.9 |
| Industrial or Process Low Pressure, <15 psig | - | - | 50% | 100% | 6.9 |  |
| Medium Pressure >15 psig < 30 psig | 16 | 0.1875 | 50% | 50% | 6.5 |  |
| Medium Pressure ≥30 <75 psig | 47 | 0.2500 | 50% | 50% | 23.4 |  |
| High Pressure ≥75 <125 psig | 101 | 0.2500 | 50% | 50% | 43.8 |  |
| High Pressure ≥125 <175 psig | 146 | 0.2500 | 50% | 50% | 60.9 |  |
| High Pressure ≥175 <250 psig | 202 | 0.2500 | 50% | 50% | 82.1 |  |
| High Pressure ≥250 ≤300 psig | 263 | 0.2500 | 50% | 50% | 105.2 |  |
| High Pressure > 300 psig | Custom | Custom | 50% | 50% | Calculated |  |

Hv 	= Heat of vaporization of steam, (Btu/lbm)

| Steam System | Average Inlet Pressure psig | Heat of Vaporization (Btu/lbm) |
| --- | --- | --- |
| Commercial Dry Cleaners | -- | 890 |
| Commercial Space Heating (including Multifamily) LPS | -- | 951 |
| Industrial and Process Low Pressure ≤15 psig | -- | 951 |
| Medium Pressure >15 psig < 30 psig | 16 | 944 |
| Medium Pressure ≥30 <75 psig | 47 | 915 |
| High Pressure ≥75 <125 psig | 101 | 880 |
| High Pressure ≥125 <175 psig | 146 | 859 |
| High Pressure ≥175 <250 psig | 202 | 837 |
| High Pressure ≥250 ≤300 psig | 263 | 816 |
| High Pressure > 300 psig | -- | Custom |

Hs 	= Specfic heat of water, (Btu/(lbm * °R))

= 1.001

Tsource 	= Incoming water temperature

= 513.67°R

ηB  	= Boiler efficiency

= custom, if unknown:

= 80.7% for steam boilers, except multifamily low-pressure

= 64.8% for multifamily low-pressure steam boilers

Hours	= Annual hours when steam system is pressurized

= custom, if unknown:

| Steam System | Zone (where applicable) | Hours/Yr |
| --- | --- | --- |
| Commercial Dry Cleaners | All Climate Zones | 2,425 |
| Industrial and Process Low Pressure ≤15 psig |  | 8,282 |
| Medium Pressure >15 psig < 30 psig |  | 8,282 |
| Medium Pressure ≥30 <75 psig |  | 8,282 |
| High Pressure ≥75 <125 psig |  | 8,282 |
| High Pressure ≥125 <175 psig |  | 8,282 |
| High Pressure ≥175 <250 psig |  | 8,282 |
| High Pressure ≥250 psig |  | 8,282 |
| Commercial Space Heating LPS | Rockford | 4,272 |
|  | Chicago | 4,029 |
|  | Springfield | 3,406 |
|  | Belleville | 2,515 |
|  | Marion | 2,546 |
| Multifamily Space Heating LPS | For steam traps that are part of steam systems where the boiler cycles on/off to maintain space setpoint temperature or for steam traps located downstream of a steam control valve that opens/closes to maintain setpoint temperature, use Heating EFLH values in Section 4.4 for High Rise or Mid-Rise MF buildings. For steam traps that are exposed to steam continuously throughout the heating season, use the values listed above for Commercial Space Heating LPS for your appropriate climate zone. |  |

L	= Leaking & blow-thru

L is 1.0 when applied to the replacment of an individual leaking trap.  If a number of steam traps are replaced and the system has not been audited, the leaking and blow-thru is applied to reflect the assumed percentage of steam traps that were actually leaking and need to be replaced.  A custom value can be utilized if a supported by an evaluation.

| Steam System | L (%) |
| --- | --- |
| Custom | Custom |
| Commercial Dry Cleaners | 27% |
| Commercial Heating (including Multifamily) LPS | 27% |
| Industrial and Process Low Pressure ≤15 psig | 16% |
| Medium Pressure >15 psig < 30 psig | 16% |
| Medium Pressure ≥30 <75 psig | 16% |
| High Pressure ≥75 <125 psig | 16% |
| High Pressure ≥125 <175 psig | 16% |
| High Pressure ≥175 <250 psig | 16% |
| High Pressure > 300 psig | 16% |

For example, a commercial dry cleaning facility with the default hours of operation and boiler efficiency;

ΔTherms = Sa * (Hv + Hs * (T1 - Tsource)) * Hours * L / (100,000 * ηB)

T1	= 507.89 * P10.0962

= 507.89 * (82.8 + 14.696)0.0962

= 789.1°R

ΔTherms 	= 18.5 lbs/hr/trap * (890 Btu/lb + 1.001 * (789.1°R - 513.7°R)) * 2,425hrs * 27%/(100,000 *  80.7%)

= 175.0 therms per trap

###### Water Impact Descriptions and Calculation

The hourly water volume saved per each repaired or replaced leaking trap is calculated by dividing the “Average Actual Steam Loss per Leaking Trap (lbm/hr/trap)” by the density of water saved, 8.33 lbm/gal, that replaces the lost steam. The average actual steam loss is provided in the table for parameter Sa, the “Average actual steam loss per leaking trap” in the Natural Gas savings section above. Annual water savings are calculated using Hours and L, the leaking and blow through factor, as defined above.

Water savings only apply to situations where condensate is lost from the steam system.  If a condensate recovery system is in place, assume zero water savings or provide a custom calculation based on site-specific operation.

The annual water savings for a replaced or repaired trap is given by:

ΔWater 	= GAL * Hours * L

Where:

GAL 	= average actual water volume saved per leaking trap, as listed in the following table and based on steam system type.

Other variables as defined above.

| Steam System* | Average Actual Steam Loss per Leaking Trap (lbm/hr/trap) | GAL: Average Actual Water Volume Saved per Leaking Trap Atmospheric Venting (gal/hr/trap) |
| --- | --- | --- |
| Commercial Dry Cleaners | 19.1 | 2.29 |
| Commercial Heating (including Multifamily) LPS | 6.9 | 0.83 |
| Industrial or Process Low Pressure, <15 psig | 6.9 | 0.83 |
| Medium Pressure >15 psig < 30 psig | 6.5 | 0.78 |
| Medium Pressure ≥30 <75 psig | 23.4 | 2.81 |
| High Pressure ≥75 <125 psig | 43.8 | 5.26 |
| High Pressure ≥125 <175 psig | 60.9 | 7.31 |
| High Pressure ≥175 <250 psig | 82.1 | 9.86 |
| High Pressure ≥250 ≤300 psig | 105.2 | 12.63 |
| High Pressure > 300 psig | Calculated | Calculated Steam Loss / 8.33 |

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-STRE-V08-210101

###### Review Deadline: 1/1/2023

### Variable Speed Drives for HVAC Pumps and Cooling Tower Fans

###### Description

This measure is applied to variable speed drives (VSD) which are installed on the following HVAC system applications: chilled water pump, hot water pumps and cooling tower fans.  There is a separate measure for HVAC supply and return fans. All other VSD applications require custom analysis by the program administrator. The VSD will modulate the speed of the motor when it does not need to run at full load. Since the power of the motor is proportional to the cube of the speed for these types of applications, significant energy savings will result.

This measure is not applicable for:

- Cooling towers, chilled or hot water pumps with any process load.

- VSD installation in existing cooling towers with 2-speed motors. (current code requires 2-speed motors for cooling towers with motors greater than 7.5 HP)

- VSD installation in new cooling towers with motors greater than 7.5 HP

This measure was developed to be applicable to the following program types: TOS, RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The VSD is applied to a motor which does not have a VSD. This measure is not applicable for replacing failed VSDs. The application must have a variable load and installation is to include the necessary controls.  Savings are based on application of VSDs to a range of baseline load conditions including no control, inlet guide vanes, outlet guide vanes and throttling valves.

###### Definition of Baseline Equipment

The time of sale baseline is a new motor installed without a VSD or other methods of control.  Retrofit baseline is an existing motor operating as is.  Retrofit baselines may or may not include guide vanes, throttling valves or other methods of control.  This information shall be collected from the customer.

Installations of new equipment with VSDs which are required by IECC 2012 or 2015 as adopted by the State of Illinois are not eligible for incentives.

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date..

###### Deemed Lifetime of Efficient Equipment

The expected measure life for HVAC application is 15 years;  measure life for process is 15 years.

###### Deemed Measure Cost

Customer provided costs will be used when available.  Default measure costs are noted below for up to 20 hp motors.  Custom costs must be gathered from the customer for motor sizes not listed below.

| HP | Cost |
| --- | --- |
| 1 -5 HP | $ 1,330 |
| 7.5 HP | $ 1,622 |
| 10 HP | $ 1,898 |
| 15 HP | $ 2,518 |
| 20 HP | $ 3,059 |

###### Loadshape

Loadshape C42 - VFD - Boiler feedwater pumps <10 HP

Loadshape C43 - VFD - Chilled water pumps <10 HP

Loadshape C44 - VFD Boiler circulation pumps <10 HP

Loadshape C48 - VFD Boiler draft fans <10 HP

Loadshape C49 - VFD Cooling Tower Fans <10 HP

###### Coincidence Factor

The demand savings factor (DSF) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh  = BHP /EFFi * Hours * ESF

Where:

BHP 	= System Brake Horsepower

(Nominal motor HP * Motor load factor)

Motors are assumed to have a load factor of 65% for calculating kW if actual values cannot be determined.  Custom load factor may be applied if known.

EFFi 	= Motor efficiency, installed. Actual motor efficiency shall be used to calculate kW.  If not known a default value of 93% shall be used.

Hours	= Default hours are provided for HVAC applications which vary by HVAC application and building type. When available (provided via Energy Management Software or metered), actual hours should be used.

| Building Type | Heating Run Hours | Cooling Run Hours | Model Source |
| --- | --- | --- | --- |
| Assembly | 4888 | 2150 | eQuest |
| Assisted Living | 4711 | 4373 | eQuest |
| Auto Dealership | 5270 | 1605 | OpenStudio |
| College | 7005 | 4065 | OpenStudio |
| Convenience Store | 4136 | 2084 | eQuest |
| Drug Store | 4940 | 1708 | OpenStudio |
| Elementary School | 6028 | 2649 | OpenStudio |
| Emergency Services | 3936 | 3277 | OpenStudio |
| Garage | 4849 | 2102 | eQuest |
| Grocery | 7452 | 5470 | OpenStudio |
| Healthcare Clinic | 8760 | 6364 | OpenStudio |
| High School | 5480 | 3141 | eQuest |
| Hospital - VAV econ | 8107 | 8707 | OpenStudio |
| Hospital - CAV econ | 3045 | 2336 | OpenStudio |
| Hospital - CAV no econ | 2927 | 4948 | OpenStudio |
| Hospital - FCU | 4371 | 8760 | OpenStudio |
| Manufacturing Facility | 3821 | 2805 | eQuest |
| MF - High Rise | 5168 | 6823 | OpenStudio |
| MF - Mid Rise | 6011 | 4996 | OpenStudio |
| Hotel/Motel - Guest | 5632 | 4155 | OpenStudio |
| Hotel/Motel - Common | 6340 | 6227 | OpenStudio |
| Movie Theater | 5063 | 2120 | eQuest |
| Office - High Rise - VAV econ | 5646 | 3414 | OpenStudio |
| Office - High Rise - CAV econ | 5361 | 4849 | eQuest |
| Office - High Rise - CAV no econ | 4202 | 6049 | OpenStudio |
| Office - High Rise - FCU | 4600 | 5341 | OpenStudio |
| Office - Low Rise | 3834 | 3835 | OpenStudio |
| Office - Mid Rise | 6119 | 3040 | OpenStudio |
| Religious Building | 5199 | 2830 | eQuest |
| Restaurant | 3476 | 2305 | OpenStudio |
| Retail - Department Store | 4249 | 2528 | eQuest |
| Retail - Strip Mall | 4475 | 2266 | eQuest |
| Warehouse | 4606 | 770 | eQuest |
| Unknown | 5038 | 2987 | n/a |

The type of hours to apply depends on the VFD application, according to the table below.

| Application | Hours Type |
| --- | --- |
| Hot Water Pump | Heating |
| Chilled Water Pump | Cooling |
| Cooling Tower Fan | Cooling |

ESF	= Energy savings factor varies by VFD application.  Units are kW/HP.

| Application | ESF |
| --- | --- |
| Hot Water Pump | 0.249 |
| Chilled Water Pump | 0.081 |
| Cooling Tower Fan | 0.502 |

###### Summer Coincident Peak Demand Savings

ΔkW  =BHP/EFFi * DSF

Where:

DSF 	= Demand Savings Factor varies by VFD application. Units are kW/HP. Values listed below are based on typical peak load for the listed application.

| Application | DSF |
| --- | --- |
| Hot Water Pump | 0 |
| Chilled Water Pump | 0 |
| Cooling Tower Fan | 0.407 |

###### Fossil Fuel Impact Descriptions and Calculation

There are no expected fossil fuel impacts for this measure.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-VSDHP-V08-210101

###### Review Deadline: 1/1/2024

### Small Commercial Programmable Thermostats – Retired 12/31/2019. Replaced with 4.4.48 Small Commercial Thermostats

### Demand Controlled Ventilation

###### Description

Demand control ventilation (DCV) adjusts outside ventilation air based on the number of occupants and the ventilation demands that those occupants create. DCV is part of a building's ventilation system control strategy. It may include hardware, software, and controls as an integral part of a building's ventilation design.  Active control of the ventilation system provides the opportunity to reduce heating and cooling energy use.

The primary component is a control sensor to communicate either directly with the economizer or with a central computer. The component is most typically a carbon dioxide (CO2) sensor, occupancy sensor, or turnstile counter.  This measure is applicable to multiple building types, and savings are classified by the specific building types defined in the Illinois TRM. This measure is modeled to assume night time set backs are in operation and minimum outside air is being used when the building is unoccupied. Systems that have static louvers or that are open at night will likely have greater savings by using the custom program.

Demand controlled ventilation controls can also be added to the exhaust fans to enclosed parking garages. The fans modulate the ventilation airflow based on pollutant concentrations (primarily carbon monoxide) in the space.

This measure does not apply to packaged single-zone (PSZ) rooftop units with functioning economizers. For PSZ with functioning economizers, see 4.4.41 Advanced Rooftop Controls.

This measure was developed to be applicable to the following program types: RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

###### The efficient equipment condition is defined by new CO2 sensors installed on return air systems where no other sensors were previously installed. For heating savings, this measure does not apply to any system with terminal reheat (constant volume or variable air volume). For terminal reheat system a custom savings calculation should be used.

###### Definition of Baseline Equipment

The base case for this measure is a space with no demand control capability. The current code minimum for outside air (OA) is 17 CFM per occupant (ASHRAE 62.1 - 2016) which is the value for office space assumed in this measure.

This measure does not apply to packaged single-zone (PSZ) rooftop units with functioning economizers. For PSZ with functioning economizers, see 4.4.41 Advanced Rooftop Controls.

###### Deemed Lifetime of Efficient Equipment

The deemed measure life is 10 years and based on CO2 sensor estimated life.

###### Deemed Measure Cost

The deemed measure cost is assumed to be the full cost of installation of a DCV retrofit including sensor cost ($500) and installation ($1000 labor) for a total of $1,500.

Adding demand controlled ventilation to parking garages is assumed to cost $500 per sensor including the cost of the controller. The installation cost is estimated at $1,000 for labor.

###### Loadshape

Commercial ventilation C23

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

For facilities heated by natural gas,

∆kWh  	= Condition Space/1000 * SFcooling

For facilities heated by heat pumps,

∆kWh  	= Condition Space/1000 * SFcooling+ Condition Space/1000 * SFHeat HP

For facilities heated by electric resistance,

∆kWh  = Condition Space/1000 * SFcooling+ Condition Space/1000 * SFHeat ER

Where:

Conditioned Space 	= actual square footage of conditioned space controlled by sensor

SFcooling	= Cooling Savings Factor

= value in table below based on building type and weather zone

SFHeat HP			= Heating Savings factor for facilities heated by Heat Pump (HP)

= value in table below based on building type and weather zone

SFHeat ER			= Heating Savings factor for facilities heated by Electric Resistance (ER)

= value in table below based on building type and weather zone

###### Saving Factor Tables

| Building Type | SFcooling (kWh/1000 SqFt) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Office - Low-rise | 285 | 289 | 299 | 298 | 305 |
| Office - Mid-rise | 225 | 228 | 234 | 233 | 237 |
| Office - High-rise | 267 | 271 | 279 | 279 | 284 |
| Religious Building | 763 | 780 | 886 | 889 | 910 |
| Restaurant | 498 | 510 | 573 | 593 | 615 |
| Retail - Department Store | 388 | 393 | 410 | 415 | 423 |
| Retail - Strip Mall | 269 | 272 | 285 | 285 | 290 |
| Convenience Store | 355 | 357 | 368 | 370 | 374 |
| Elementary School | 358 | 367 | 410 | 405 | 415 |
| High School | 350 | 359 | 401 | 396 | 406 |
| College/University | 400 | 426 | 472 | 488 | 519 |
| Healthcare Clinic | 349 | 354 | 389 | 392 | 398 |
| Lodging | 407 | 409 | 423 | 424 | 428 |
| Manufacturing | 175 | 177 | 183 | 248 | 185 |
| Special Assembly Auditorium | 563 | 581 | 668 | 677 | 711 |
| Default (non-garage) | 377 | 385 | 419 | 426 | 433 |
| Enclosed Parking Garage | 925 | 925 | 925 | 925 | 925 |

| Building Type | SF Heat HP (kWh/1000 SqFt) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Office - Low-rise | 234 | 205 | 181 | 171 | 147 |
| Office - Mid-rise | 157 | 138 | 121 | 115 | 99 |
| Office - High-rise | 211 | 185 | 163 | 154 | 133 |
| Religious Building | 1,508 | 1,333 | 1,180 | 1,125 | 1,008 |
| Restaurant | 1,067 | 962 | 837 | 816 | 720 |
| Retail - Department Store | 368 | 329 | 291 | 285 | 249 |
| Retail - Strip Mall | 246 | 215 | 195 | 186 | 165 |
| Convenience Store | 180 | 163 | 141 | 138 | 121 |
| Elementary School | 657 | 572 | 508 | 473 | 418 |
| High School | 641 | 558 | 495 | 461 | 406 |
| College/University | 1,267 | 1,114 | 980 | 945 | 798 |
| Healthcare Clinic | 447 | 396 | 348 | 334 | 299 |
| Lodging | 205 | 184 | 159 | 154 | 135 |
| Manufacturing | 130 | 114 | 101 | 172 | 83 |
| Special Assembly Auditorium | 1,773 | 1,564 | 1,414 | 1,378 | 1,212 |
| Default (non-garage) | 606 | 535 | 474 | 460 | 400 |

| Building Type | SF Heat ER (kWh/1000 SqFt) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Office - Low-rise | 703 | 615 | 542 | 512 | 441 |
| Office - Mid-rise | 471 | 413 | 364 | 345 | 298 |
| Office - High-rise | 633 | 554 | 489 | 462 | 398 |
| Religious Building | 4,523 | 3,999 | 3,541 | 3,376 | 3,024 |
| Restaurant | 3,201 | 2,886 | 2,511 | 2,449 | 2,159 |
| Retail - Department Store | 1,103 | 987 | 874 | 855 | 748 |
| Retail - Strip Mall | 738 | 646 | 584 | 559 | 495 |
| Convenience Store | 541 | 488 | 423 | 413 | 364 |
| Elementary School | 1,972 | 1,715 | 1,523 | 1,420 | 1,254 |
| High School | 1,924 | 1,673 | 1,484 | 1,383 | 1,219 |
| College/University | 3,801 | 3,341 | 2,940 | 2,834 | 2,394 |
| Healthcare Clinic | 1,341 | 1,188 | 1,044 | 1,001 | 896 |
| Lodging | 616 | 551 | 477 | 462 | 406 |
| Manufacturing | 390 | 343 | 303 | 516 | 250 |
| Special Assembly Auditorium | 5,320 | 4,691 | 4,243 | 4,133 | 3,636 |
| Default (non-garage) | 1,819 | 1,606 | 1,423 | 1,381 | 1,199 |

For example, for a 7,500 SqFt of low-rise office space in Chicago with gas heat.

ΔkWh	= 7,500 /1000 *289

= 2,168 kWh

###### Summer Coincident Peak Demand Savings

NA

###### Natural Gas Savings

∆therms  = Condition Space/1000 * SF Heat Gas

Where:

SF Heat Gas	= value in table below based on building type and weather zone.

| Building Type | SFHeat Gas (Therm/1000 sq ft) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Office - Low-rise | 30 | 26 | 23 | 22 | 19 |
| Office - Mid-rise | 20 | 18 | 16 | 15 | 13 |
| Office- High-rise | 27 | 24 | 21 | 20 | 17 |
| Religious BuiIding | 193 | 171 | 151 | 144 | 129 |
| Restaurant | 137 | 123 | 107 | 104 | 92 |
| RetaiI - Department Store | 47 | 42 | 37 | 36 | 32 |
| Retail - Strip Mall | 31 | 28 | 25 | 24 | 21 |
| Convenience Store | 23 | 21 | 18 | 18 | 16 |
| Elementary School | 84 | 73 | 65 | 61 | 53 |
| High School | 82 | 71 | 63 | 59 | 52 |
| College/ University | 162 | 143 | 125 | 121 | 102 |
| Healthcare Clinic | 57 | 51 | 45 | 43 | 38 |
| Lodging | 26 | 23 | 20 | 20 | 17 |
| Manufacturing | 17 | 15 | 13 | 22 | 11 |
| Special Assembly Auditorium | 227 | 200 | 181 | 176 | 155 |
| De-fault | 78 | 68 | 61 | 59 | 51 |

For example, for a 7500 SqFt of low-rise office space in Chicago.

ΔTherms	= 7,500/1,000 * 26

= 195 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure code: CI-HVC-DCV-V06-220101

###### Review Deadline: 1/1/2024

### High Turndown Burner for Space Heating Boilers

###### Description

This measure is for a non-residential boilers equipped with linkageless controls providing space heating with burners having a turndown less than 6:1. Turndown is the ratio of the high firing rate to the low firing rate. When boilers are subjected to loads below the low firing rate, the boiler must cycle on/off to meet the load requirements. A higher turndown ratio reduces burner startups, provides better load control, saves wear-and-tear on the burner, and reduces purge-air requirements, all of these benefits result in better overall efficiency.

This measure was developed to be applicable to the following program types:  NC, TOS, RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify the boiler linkageless burner must operate with a turndown greater than or equal to 10:1 and be subjected to loads less than or equal to 30% of the full fire input MBH for greater than 60% of the operating hours.

###### Definition of Baseline Equipment

The baseline boiler utilizes a linkageless burner with a turndown ration of 6:1 or less and is used primarily for space heating. Redundant boilers do not qualify. Code requirements must be considered.

Note: beginning with the 2015 edition, IECC makes the following requirements for boiler turndown:

Boiler Systems with design input of greater than 1,000,000 Btu/h shall comply with the turndown ratio specified in the following table.

The system turndown requirement shall be met through the use of multiple single-input boilers, one or more modulating boilers or a combination of single-input and modulating boilers.

| BOILER SYSTEM DESIGN INPUT | MINIMUM TURNDOWN RATIO |
| --- | --- |
| ≥ 1,000,000 and less than or equal to 5,000,000 | 3 to 1 |
| > 5,000,000 and less than or equal to 10,000,000 | 4 to 1 |
| > 10,000,000 | 5 to 1 |

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be the lower of remaining useful life of the boiler, or 21 years.

###### Deemed Measure Cost

Actual costs shall be used as available. When unknown, the deemed installed measure cost including labor is approximately $2.53/MBtu/hr.

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

Δtherms	= Ngi * SF * EFLH / 100

Where:

Ngi	= Boiler gas input size (kBtu/hr) = custom

SF 	= Savings Factor = Percentage of energy loss per hour

= (∑ ((EL_base – EL_eff) * H_cycling)) / H)*100

Where:

EL_base	= Base Boiler Percentage of energy loss due to cycling at % of Base Boiler Load where BL_base ≤ TDR_base

= 0.003 * (Cycles_base)2 – 0.001 * Cycles_base

Where:

Cycles_base = Number of Cycles/hour of base boiler

= TDR_base / BL

Where:

BL = % of full boiler load at bin hours being evaluated. This is assumed to be a straight line based on 0% load at the building balance point (assumed to be 55F), and full load corrected for the oversizing (OSF) at the lowest temperature bin of -10 to -5F.

OSF = Oversizing Factor = 1.3, or custom

TDR_base = Turndown ratio = 0.33, or custom

EL_eff  = Efficient Boiler Percentage of energy loss due to cycling at % of Efficient Boiler Load

= 0.003 * (Cycles_eff)2 – 0.001 * Cycles_eff

Where:

Cycles_eff = Number of Cycles/hour

= TDR_eff / BL

Where:

TDR_eff = Turndown ratio = 0.10,  or custom

H_cycling = Hours base boiler is cycling at % of base boiler load

= see table below or custom

H  	= Total Number of Hours in Heating Season

= 4,946 or custom

100	= convert to a percentage

SF = 69.1 / 4946 *100 = 1.4% or custom (see table below for summary of values)

| Temperature | H_cycling | BL | EL_base | EL_eff | (EL_base-EL_eff)* Hours |
| --- | --- | --- | --- | --- | --- |
| 50 to 55 | 601 | 6.0% | 8.5% | 0.7% | 47.2 |
| 45 to 50 | 603 | 12.0% | 2.0% | 0.0% | 12.0 |
| 40 to 45 | 455 | 18.0% | 0.8% | 0.0% | 3.8 |
| 35 to 40 | 925 | 24.0% | 0.4% | 0.0% | 4.0 |
| 30 to 35 | 814 | 30.0% | 0.3% | 0.0% | 2.1 |
| Total |  |  |  |  | 69.1 |

EFLH	= Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

100 	= convert kBtu to therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVAC-HTBC-V05-200601

###### Review Deadline: 1/1/2024

### Linkageless Boiler Controls for Space Heating

###### Description

This measure is for a non-residential boiler providing space heating with single point positioning combustion control. In single-point positioning control, the fuel valve is linked to the combustion air damper via a jackshaft mechanism to maintain correspondence between fuel and combustion air input. Most boilers with single point positioning control do not maintain low excess air levels over their entire firing range. Generally, these boilers are calibrated at high fire, but due to the non-linearity required for efficient combustion, excess air levels tend to dramatically increase as the firing rate decreases. Boiler efficiency drops as the excess air levels are increased.

This measure was developed to be applicable to the following program types:  TOS, NC, RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify the boiler burner must have a linkageless control system allowing the combustion air damper position to be adjusted and set for optimal efficiency at several firing rates throughout the burner’s firing range. This requires the fuel valve and combustion air damper to each be powered by a separate actuator. An alternative to the combustion air damper is a Variable Speed Drive on the combustion air fan.

###### Definition of Baseline Equipment

The baseline boiler utilizes single point positioning for the burner combustion control.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 20 years.

###### Deemed Measure Cost

The deemed measure cost is estimated at $8,500.

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

When a Variable Speed Drive is incorporated, electrical savings are calculated according to the “4.4.17 Variable Speed Drive for HVAC Pumps and Cooling Tower Fans” measure.

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

ΔTherms	= Ngi * SF * EFLH / 100

Where:

Ngi	= Boiler gas input size (kBtu/hr) = custom

SF 	= Savings factor

Note:  Savings factor is the percentage increase in efficiency as a result of the addition of linkageless burner controls. At an average boiler load of 35%, single point controls are assumed to have excess air of 91%, while linkageless controls are assumed to have 34% excess air. The difference between controls types is 57% at this average operating condition. A 15% reduction in excess air is approximately a 1% increase in efficiency. Therefore the nominal combustion efficiency increase is 57 / 15 * 1% = 3.8%.

= 3.8%

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

100 	= convert kBtu to therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-LBC-V06-220101

###### Review Deadline: 1/1/2027

### Oxygen Trim Controls for Space Heating Boilers

###### Description

This measure is for a non-residential boiler providing space heating without oxygen trim combustion controls. Oxygen trim controls limit the amount of excess oxygen provided to the burner for combustion. This oxygen level is dependent upon the amount of air provided. Oxygen trim control converts parallel positioning, linkageless controls, into a closed-loop control configuration with the addition of an exhaust gas analyzer and PID controller. Boilers with oxygen trim controls can maintain a predetermined excess air rate (generally 15% to 30% excess air) over the entire burner firing rate. Boilers without these controls typically have excess air rates around 30% over the entire firing rate. Boiler efficiency drops as the excess air levels are increased.

This measure was developed to be applicable to the following program types:  NC, TOS, RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify the boiler burner must have an oxygen control system allowing the combustion air to be adjusted to maintain a predetermined excess oxygen level in the flue exhaust at all firing rates throughout the burner’s firing range. This requires an oxygen sensor in the flue exhaust and linkageless fuel valve and combustion air controls.

###### Definition of Baseline Equipment

The baseline boiler utilizes single point positioning for the burner combustion control.

###### Deemed Lifetime of Efficient Equipment

The measure life for the O2 Trim controls is 20 years.

###### Deemed Measure Cost

The deemed measure cost is approximately $23,250.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms 	= Ngi * SF * EFLH / 100

Where:

Ngi	= Boiler gas input size (kBtu/hr)

= Custom

SF 	= Savings factor

Note:  Savings factor is the percentage reduction in gas consumption as a result of the addition of O2 trim controls. Linkageless controls have an excess air rate of 28% over the entire firing range. O2 trim controls have an excess air rate of 15%. The average difference is 13%. A 15% reduction in excess air is approximately a 1% increase in efficiency. Therefore, the nominal combustion efficiency increase is 13 / 15 * 1% = 0.87%.

= 0.87%

EFLH	= Default Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use. When available, actual hours should be used.

100 	= convert kBtu to therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

The deemed annual Operations and Maintenance cost is $800.

###### Measure Code: CI-HVC-O2TC-V02-220101

###### Review Deadline: 1/1/2026

### Shut Off Damper for Space Heating Boilers or Furnaces

###### Description

This measure is for non-residential atmospheric boilers or furnaces providing space heating without a shut off damper. When appliances are on standby mode warm room air is drawn through the stack via the draft hood or dilution air inlet at a rate proportional to the stack height, diameter and outdoor temperature. More air is drawn through the vent immediately after the appliance shuts off and the flue is still hot. Installation of a new shut off damper can prevent heat from being drawn up the warm vent and reducing the amount of air that passes through the furnace or boiler heat exchanger. This reduction in air can slightly increase overall operating efficiency by reducing the time needed to achieve steady-state operating conditions.

This measure was developed to be applicable to the following program types:  RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify the space heating boiler or furnace must have a new electrically or thermally activated shut off damper installed on either the exhaust flue or combustion air intake. Barometric dampers do not qualify. The damper actuation shall be interlocked with the firing controls.

###### Definition of Baseline Equipment

The baseline boiler or furnace incorporates no shut off damper on the combustion air intake or flue exhaust.

###### Deemed Lifetime of Efficient Equipment

The measure life for the shut off damper is 15 years, or for the remaining lifetime of the heating equipment, whichever is less.

###### Deemed Measure Cost

Given the variability in cost associated with differences in system specifications and design, as well as choice of measure technology, actual installed costs should be used as available or based on program-specific qualification requirements. When unavailable, a deemed measure cost of $1,500 shall be assumed.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms 	= Ngi * SF * EFLH / 100

Where:

Ngi	= Boiler gas input size (kBtu/hr)

= Custom

SF 	= Savings factor

= 1%

Note:  The savings factor assumes the boiler or furnace is located in an unconditioned space. The savings factor can be higher for those units located within conditioned space.

EFLH	= Default Equivalent Full Load Hours for heating in Existing Buildings are provided in section 4.4 HVAC End Use. When available, actual hours should be used.

100 	= convert kBtu to therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

A deemed, one-time Operations and Maintenance cost of $150 shall be included in cost-effectiveness calculations and occur in year 10 of the measure life to account for controller replacement.

###### Measure Code: CI-HVC-SODP-V02-200601

###### Review Deadline: 1/1/2024

### Small Pipe Insulation

###### Description

This measure provides rebates for adding insulation to bare pipes with inner diameters of ½” and ¾”. Insulation must be at least one inch thick. Since new construction projects are required by code to have pipe insulation, this measure is only for retrofits of existing facilities. This covers bare straight pipe as well as all fittings.

Default savings are provided on a per linear foot basis. It is assumed that the majority of pipes less than one inch in commercial facilities are used for domestic hot water. However, this measure can cover hydronic heating systems as well as low and high pressure steam systems.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient case is a ½“or ¾“ diameter pipe with at least one inch of insulation. Insulation must be protected from damage which includes moisture, sunlight, equipment maintenance and wind. Outdoor pipes should have a weather protective jacket. Insulation must be continuous over straight pipe, elbows and tees.

###### Definition of Baseline Equipment

The base case for savings estimates is a bare hot water or steam pipe with a fluid temperature of 105 degrees Fahrenheit or greater. Current new construction code requires insulation amounts similar to this measure though this base case is commonly found in older existing buildings.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 15 years.

###### Deemed Measure Cost

The incremental measure cost for insulation is the full cost of adding insulation to the pipe. Actual installation costs should be used for the measure cost. For planning purposes, the following costs can be used to estimate the full cost of materials and labor.

| Insulation Thickness | ¾” pipe | ½” pipe |
| --- | --- | --- |
| 1” | $4.45 | $4.15 |

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

ΔTherms per foot 	= [((Qbase – Qeff) * EFLH) / (100,000 * ηBoiler)] * TRF

= [Modeled or provided by tables below] * TRF

ΔTherms		= (Lsp + Loc,i) * Δtherms per foot

Where:

EFLH		= Equivalent Full Load Hours for Heating

= Actual or defaults by building type in Existing Buildings provided in Section 4.4, HVAC end use

For year round recirculation or domestic hot water:

= 8,766

For heating season recirculation, hours with the outside air temperature below 55°F:

| Zone | Hours |
| --- | --- |
| Zone 1 (Rockford) | 5,039 |
| Zone 2 (Chicago) | 4,963 |
| Zone 3 (Springfield) | 4,495 |
| Zone 4 (Belleville/ | 4,021 |
| Zone 5 (Marion) | 4,150 |

Qbase 		= Heat Loss from Bare Pipe (Btu/hr/ft)

= Calculated where possible using 3E Plusv4.0 software. For defaults see table below

Qeff		= Heat Loss from Insulated Pipe (Btu/hr/ft)

= Calculated where possible using 3E Plusv4.0 software. For defaults see table below

100,000 		= conversion factor (1 therm = 100,000 Btu)

ηBoiler 		= Efficiency of the boiler being used to generate the hot water or steam in the pipe

= 81.9% for water boilers

= 80.7% for steam boilers, except multifamily low-pressure

= 64.8% for multifamily low-pressure steam boilers.

TRF	= Thermal Regain Factor for pipe location and use, see table below. The Custom TRF option may be used on any pipe location, including pipe locations with deemed TRFs specifically listed in the table below, if supporting justification and calculations for the Custom TRF are provided.

May vary seasonally such as: TRF[summer] * summer hours + TRF[winter] * winter hours where TRF values reflecting summer and winter conditions are apportioned by the hours for those conditions. TRF may also be adjusted by building specific balance point temperature (BPT) and operating hours above and below that BPT.

| Pipe Location | Assumed Regain | TRF, Thermal Regain Factor |
| --- | --- | --- |
| Outdoor | 0% | 1.0 |
| Indoor, conditioned space during the heating season, 55°F BPT | 85% | 0.15 |
| Indoor, conditioned space, not during the heating season, 55°F BPT | 0% | 1.0 |
| Indoor, conditioned, annual use (e.g. hot water or process loads), 55°F BPT | 45% | 0.55 |
| Indoor, semi- conditioned, (unconditioned space, with heat transfer to conditioned space. E.g., boiler room, ceiling plenum, basement, crawlspace, wall), during the heating season, 55°F BPT | 30% | 0.70 |
| Indoor, semi-conditioned, not during the heating season, 55°F BPT | 0% | 1.0 |
| Indoor, semi-conditioned, annual use, 55°F BPT | 16% | 0.84 |
| Indoor, unconditioned spaces, (no heat transfer to conditioned space) | 0% | 1.0 |
| Location not specified - Commercial | 23% | 0.77 |
| Location not specified – Industrial | 16% | 0.84 |
| Custom | Custom | 1 – assumed regain |

Lsp 	= Length of straight pipe to be insulated (linear foot)

Loc,i 	= Total equivalent length of (elbows and tees) of pipe to be insulated. Use table below to determine equivalent lengths.

| Nominal Pipe Diameter | Equivalent Length (ft) |  |
| --- | --- | --- |
|  | 90 Degree Elbow | Straight Tee |
| 1/2" | 0.04 | 0.03 |
| 3/4" | 0.06 | 0.05 |

The table below shows the deemed therm savings by building type and region on a per linear foot basis for both ½” and ¾” copper pipe.

The following table provides deemed values for 1/2" copper pipe, temperatures are assumed by category below, and insulation is assumed to be one inch fiberglass.

| Piping Use | Building Type | Annual Therms Saved / Linear Foot |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Space Heating Non-recirculating | Assembly | 0.117 | 0.120 | 0.107 | 0.071 | 0.109 |
|  | Assisted Living | 0.110 | 0.107 | 0.094 | 0.069 | 0.083 |
|  | College | 0.100 | 0.093 | 0.083 | 0.046 | 0.055 |
|  | Convenience Store | 0.097 | 0.089 | 0.079 | 0.057 | 0.064 |
|  | Elementary School | 0.116 | 0.113 | 0.100 | 0.069 | 0.084 |
|  | Garage | 0.064 | 0.063 | 0.056 | 0.044 | 0.049 |
|  | Grocery | 0.105 | 0.105 | 0.092 | 0.057 | 0.068 |
|  | Healthcare Clinic | 0.103 | 0.106 | 0.092 | 0.063 | 0.066 |
|  | High School | 0.120 | 0.121 | 0.109 | 0.077 | 0.091 |
|  | Hospital - CAV no econ | 0.115 | 0.119 | 0.101 | 0.087 | 0.099 |
|  | Hospital - CAV econ | 0.117 | 0.121 | 0.103 | 0.089 | 0.101 |
|  | Hospital - VAV econ | 0.048 | 0.045 | 0.034 | 0.020 | 0.022 |
|  | Hospital - FCU | 0.087 | 0.099 | 0.080 | 0.094 | 0.127 |
|  | Hotel/Motel | 0.115 | 0.112 | 0.101 | 0.069 | 0.084 |
|  | Hotel/Motel - Common | 0.104 | 0.106 | 0.101 | 0.082 | 0.086 |
|  | Hotel/Motel - Guest | 0.115 | 0.111 | 0.099 | 0.066 | 0.082 |
|  | Manufacturing Facility | 0.068 | 0.066 | 0.061 | 0.037 | 0.041 |
|  | MF - High Rise | 0.100 | 0.098 | 0.090 | 0.076 | 0.076 |
|  | MF - High Rise - Common | 0.118 | 0.115 | 0.103 | 0.071 | 0.092 |
|  | MF - High Rise - Residential | 0.096 | 0.096 | 0.087 | 0.075 | 0.073 |
|  | MF - Mid Rise | 0.109 | 0.110 | 0.095 | 0.070 | 0.079 |
|  | Movie Theater | 0.119 | 0.117 | 0.109 | 0.083 | 0.099 |
|  | Office - High Rise - CAV no econ | 0.132 | 0.134 | 0.122 | 0.082 | 0.089 |
|  | Office - High Rise - CAV econ | 0.136 | 0.139 | 0.128 | 0.088 | 0.097 |
|  | Office - High Rise - VAV econ | 0.100 | 0.102 | 0.084 | 0.050 | 0.055 |
|  | Office - High Rise - FCU | 0.073 | 0.072 | 0.062 | 0.033 | 0.035 |
|  | Office - Low Rise | 0.093 | 0.093 | 0.074 | 0.045 | 0.052 |
|  | Office - Mid Rise | 0.103 | 0.104 | 0.088 | 0.056 | 0.062 |
|  | Religious Building | 0.105 | 0.098 | 0.094 | 0.069 | 0.079 |
|  | Restaurant | 0.088 | 0.088 | 0.079 | 0.060 | 0.071 |
|  | Retail - Department Store | 0.091 | 0.083 | 0.078 | 0.051 | 0.058 |
|  | Retail - Strip Mall | 0.087 | 0.081 | 0.071 | 0.049 | 0.053 |
|  | Warehouse | 0.095 | 0.089 | 0.091 | 0.057 | 0.070 |
|  | Unknown | 0.101 | 0.100 | 0.089 | 0.064 | 0.074 |
| Space Heating - recirculation heating season only | All buildings (Hours below 55°F) | 0.329 | 0.324 | 0.293 | 0.262 | 0.271 |
| Space Heating - recirculation year round | All buildings (All hours) | 0.572 | 0.572 | 0.572 | 0.572 | 0.572 |
| DHW | Recirculation loop | 0.572 | 0.572 | 0.572 | 0.572 | 0.572 |
| Process | Custom | Custom |  |  |  |  |

The following table provides deemed savings values for 3/4" copper pipe with temperatures assumed by category below, insulation is assumed to be one inch fiberglass.

| Piping Use | Building Type | Annual Therms Saved / Linear Foot |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Space Heating Non-recirculating | Assembly | 0.142 | 0.145 | 0.129 | 0.086 | 0.132 |
|  | Assisted Living | 0.133 | 0.130 | 0.115 | 0.084 | 0.101 |
|  | College | 0.121 | 0.113 | 0.101 | 0.056 | 0.067 |
|  | Convenience Store | 0.117 | 0.108 | 0.096 | 0.069 | 0.077 |
|  | Elementary School | 0.141 | 0.137 | 0.121 | 0.084 | 0.102 |
|  | Garage | 0.078 | 0.077 | 0.067 | 0.054 | 0.060 |
|  | Grocery | 0.127 | 0.127 | 0.111 | 0.069 | 0.083 |
|  | Healthcare Clinic | 0.125 | 0.128 | 0.112 | 0.076 | 0.081 |
|  | High School | 0.146 | 0.147 | 0.132 | 0.094 | 0.110 |
|  | Hospital - CAV no econ | 0.140 | 0.144 | 0.123 | 0.105 | 0.120 |
|  | Hospital - CAV econ | 0.142 | 0.147 | 0.125 | 0.108 | 0.123 |
|  | Hospital - VAV econ | 0.058 | 0.055 | 0.041 | 0.025 | 0.027 |
|  | Hospital - FCU | 0.105 | 0.120 | 0.098 | 0.115 | 0.154 |
|  | Hotel/Motel | 0.140 | 0.136 | 0.122 | 0.084 | 0.102 |
|  | Hotel/Motel - Common | 0.127 | 0.129 | 0.123 | 0.100 | 0.105 |
|  | Hotel/Motel - Guest | 0.139 | 0.135 | 0.120 | 0.081 | 0.099 |
|  | Manufacturing Facility | 0.083 | 0.080 | 0.074 | 0.045 | 0.050 |
|  | MF - High Rise | 0.121 | 0.119 | 0.109 | 0.093 | 0.093 |
|  | MF - High Rise - Common | 0.144 | 0.140 | 0.125 | 0.086 | 0.111 |
|  | MF - High Rise - Residential | 0.117 | 0.116 | 0.105 | 0.091 | 0.089 |
|  | MF - Mid Rise | 0.132 | 0.134 | 0.115 | 0.085 | 0.096 |
|  | Movie Theater | 0.144 | 0.142 | 0.133 | 0.101 | 0.120 |
|  | Office - High Rise - CAV no econ | 0.160 | 0.162 | 0.148 | 0.099 | 0.108 |
|  | Office - High Rise - CAV econ | 0.165 | 0.169 | 0.155 | 0.107 | 0.118 |
|  | Office - High Rise - VAV econ | 0.121 | 0.123 | 0.102 | 0.060 | 0.067 |
|  | Office - High Rise - FCU | 0.089 | 0.087 | 0.075 | 0.040 | 0.042 |
|  | Office - Low Rise | 0.113 | 0.113 | 0.090 | 0.055 | 0.063 |
|  | Office - Mid Rise | 0.126 | 0.126 | 0.106 | 0.068 | 0.075 |
|  | Religious Building | 0.127 | 0.119 | 0.114 | 0.084 | 0.095 |
|  | Restaurant | 0.107 | 0.107 | 0.096 | 0.073 | 0.086 |
|  | Retail - Department Store | 0.110 | 0.101 | 0.095 | 0.062 | 0.071 |
|  | Retail - Strip Mall | 0.106 | 0.098 | 0.086 | 0.059 | 0.064 |
|  | Warehouse | 0.115 | 0.108 | 0.111 | 0.069 | 0.085 |
|  | Unknown | 0.123 | 0.122 | 0.108 | 0.078 | 0.090 |
| Space Heating - recirculation heating season only | All buildings (Hours below 55°F) | 0.399 | 0.393 | 0.356 | 0.319 | 0.329 |
| Space Heating - recirculation year round | All buildings (All hours) | 0.694 | 0.694 | 0.694 | 0.694 | 0.694 |
| DHW | Recirculation loop | 0.694 | 0.694 | 0.694 | 0.694 | 0.694 |
| Process | Custom | Custom |  |  |  |  |

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-SPIN-V03-220101

###### Review Deadline: 1/1/2024

### Small Commercial Programmable Thermostat Adjustments – Retired 12/31/2019.

### Variable Speed Drives for HVAC Supply and Return Fans

###### Description

This measure is applied to variable speed drives (VSD) which are installed on HVAC supply fans and return fans. The VSD will modulate the speed of the motor when it does not need to run at full load. Since the power of the motor is proportional to the cube of the speed for these types of applications, significant energy savings will result.

Note this measure should be used for evaluating control system modifications. If combined with the evaluation of a more efficient over a baseline fan, measure ‘4.4.53 HVAC Supply, Return and Exhaust Fans – Fan Energy Index’ should be utilized. The FEPnew value from measure 4.4.53 should be used to replace the 0.746×HP×LFηmotor term in this measure.

This measure was developed to be applicable to the following program types: TOS, RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The VSD is applied to a motor which does not have a VSD. The application must have a variable load and installation is to include the necessary controls.  Savings are based on application of VSDs to a range of baseline load conditions including no control, inlet guide vanes, outlet guide vanes and throttling valves.

###### Definition of Baseline Equipment

The time of sale baseline is a new motor installed without a VSD or other methods of control.  Retrofit baseline is an existing motor operating as is.  Retrofit baselines may or may not include guide vanes, throttling valves or other methods of control.  This information shall be collected from the customer.

Installations of new equipment with VSDs which are required by IECC 2012 or 2015 as adopted by the State of Illinois are not eligible for incentives.

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

###### Deemed Lifetime of Efficient Equipment

The expected measure life for all VSDs is 15 years.

###### Deemed Measure Cost

Customer provided costs will be used when available.  Default measure costs are noted below for up to 75 hp motors. Custom costs must be gathered from the customer for motor sizes not listed below.

| HP | Cost |
| --- | --- |
| 5 HP | $ 2,250 |
| 15 HP | $ 3,318 |
| 25 HP | $ 4,386 |
| 50 HP | $ 6,573 |
| 75 HP | $ 8,532 |

###### Loadshape

Loadshape C39 - VFD - Supply fans <10 HP

Loadshape C40 - VFD - Return fans <10 HP

Loadshape C41 - VFD - Exhaust fans <10 HP

###### Coincidence Factor

The demand savings factor (DSF) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Note this measure should be used for evaluating control system modifications. If combined with the evaluation of a more efficient over a baseline fan, measure ‘4.4.53 HVAC Supply, Return and Exhaust Fans – Fan Energy Index’ should be utilized. The FEPnew value from measure 4.4.53 should be used to replace the 0.746×HP×LFηmotor term in this measure.

| kWhBase = | 0.746×HP×LFηmotor×RHRSBase×0%100%%FF×PLRBase |
| --- | --- |
| kWhRetrofit = | 0.746×HP×LFηmotor×RHRSbase×0%100%(%FF×PLRRetrofit) |
| ∆kWhfan = | kWhBase-kWhRetrofit |
| ∆kWhtotal = | ∆kWhfan×(1+IEenergy) |

Where:

kWhBase 	= Baseline annual energy consumption (kWh/yr)

kWhRetrofit 	= Retrofit annual energy consumption (kWh/yr)

∆kWhfan 	= Fan-only annual energy savings

∆kWhtotal 	= Total project annual energy savings

0.746 		= Conversion factor for HP to kWh

HP		= Nominal horsepower of controlled motor

LF 		= Load Factor; Motor Load at Fan Design CFM (Default = 65%)

ηmotor		= Installed nominal/nameplate motor efficiency

Default motor is a NEMA Premium Efficiency, ODP, 4-pole/1800 RPM fan motor

NEMA Premium Efficiency Motors Default Efficiencies

| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | # of Poles |  |  | # of Poles |  |  |
|  | 6 | 4 | 2 | 6 | 4 | 2 |
|  | Speed (RPM) |  |  | Speed (RPM) |  |  |
|  | 1200 | 1800 Default | 3600 | 1200 | 1800 | 3600 |
| 1 | 0.825 | 0.855 | 0.770 | 0.825 | 0.855 | 0.770 |
| 1.5 | 0.865 | 0.865 | 0.840 | 0.875 | 0.865 | 0.840 |
| 2 | 0.875 | 0.865 | 0.855 | 0.885 | 0.865 | 0.855 |
| 3 | 0.885 | 0.895 | 0.855 | 0.895 | 0.895 | 0.865 |
| 5 | 0.895 | 0.895 | 0.865 | 0.895 | 0.895 | 0.885 |
| 7.5 | 0.902 | 0.910 | 0.885 | 0.910 | 0.917 | 0.895 |
| 10 | 0.917 | 0.917 | 0.895 | 0.910 | 0.917 | 0.902 |
| 15 | 0.917 | 0.930 | 0.902 | 0.917 | 0.924 | 0.910 |
| 20 | 0.924 | 0.930 | 0.910 | 0.917 | 0.930 | 0.910 |
| 25 | 0.930 | 0.936 | 0.917 | 0.930 | 0.936 | 0.917 |
| 30 | 0.936 | 0.941 | 0.917 | 0.930 | 0.936 | 0.917 |
| 40 | 0.941 | 0.941 | 0.924 | 0.941 | 0.941 | 0.924 |
| 50 | 0.941 | 0.945 | 0.930 | 0.941 | 0.945 | 0.930 |
| 60 | 0.945 | 0.950 | 0.936 | 0.945 | 0.950 | 0.936 |
| 75 | 0.945 | 0.950 | 0.936 | 0.945 | 0.954 | 0.936 |
| 100 | 0.950 | 0.954 | 0.936 | 0.950 | 0.954 | 0.941 |
| 125 | 0.950 | 0.954 | 0.941 | 0.950 | 0.954 | 0.950 |
| 150 | 0.954 | 0.958 | 0.941 | 0.958 | 0.958 | 0.950 |
| 200 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.954 |
| 250 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.958 |
| 300 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 350 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 400 | 0.958 | 0.958 | 0.958 | 0.958 | 0.962 | 0.958 |
| 450 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |
| 500 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |

RHRSBase	= Annual operating hours for fan motor based on building type

Default hours are provided for HVAC applications which vary by HVAC application and building type. When available (provided via Energy Management Software or metered),  actual hours should be used.

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly | 7235 | eQuest |
| Assisted Living | 8760 | eQuest |
| Auto Dealership | 7451 | OpenStudio |
| College | 4836 | OpenStudio |
| Convenience Store | 7004 | eQuest |
| Drug Store | 7156 | OpenStudio |
| Elementary School | 3765 | OpenStudio |
| Emergency Services | 8760 | OpenStudio |
| Garage | 7357 | eQuest |
| Grocery | 8543 | OpenStudio |
| Healthcare Clinic | 4314 | OpenStudio |
| High School | 3460 | OpenStudio |
| Hospital - VAV econ | 4666 | OpenStudio |
| Hospital - CAV econ | 8021 | OpenStudio |
| Hospital - CAV no econ | 7924 | OpenStudio |
| Hospital - FCU | 4055 | OpenStudio |
| Manufacturing Facility | 8706 | eQuest |
| MF - High Rise | 8760 | OpenStudio |
| MF - Mid Rise | 8760 | OpenStudio |
| Hotel/Motel - Guest | 2409 | OpenStudio |
| Hotel/Motel - Common | 8683 | OpenStudio |
| Movie Theater | 7505 | eQuest |
| Office - High Rise - VAV econ | 2369 | OpenStudio |
| Office - High Rise - CAV econ | 2279 | OpenStudio |
| Office - High Rise - CAV no econ | 5303 | OpenStudio |
| Office - High Rise - FCU | 1648 | OpenStudio |
| Office - Low Rise | 6345 | OpenStudio |
| Office - Mid Rise | 3440 | OpenStudio |
| Religious Building | 7380 | eQuest |
| Restaurant | 7302 | OpenStudio |
| Retail - Department Store | 7155 | OpenStudio |
| Retail - Strip Mall | 6921 | OpenStudio |
| Warehouse | 6832 | OpenStudio |
| Unknown | 6241 | n/a |

%FF		= Percentage of run-time spent within a given flow fraction range

Default Fan Duty Cycle Based on 2012 ASHRAE Handbook; HVAC Systems and Equipment, page 45.11, Figure 12.

| Flow Fraction (% of design cfm) | Percent of Time at Flow Fraction |
| --- | --- |
| 0% to 10% | 0.0% |
| 10% to 20% | 1.0% |
| 20% to 30% | 5.5% |
| 30% to 40% | 15.5% |
| 40% to 50% | 22.0% |
| 50% to 60% | 25.0% |
| 60% to 70% | 19.0% |
| 70% to 80% | 8.5% |
| 80% to 90% | 3.0% |
| 90% to 100% | 0.5% |

PLRBase	= Part load ratio for a given flow fraction range based on the baseline flow control type

PLRRetrofit	= Part load ratio for a given flow fraction range based on the retrofit flow control type

| Control Type | Flow Fraction |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% |
| No Control or Bypass Damper | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Discharge Dampers | 0.46 | 0.55 | 0.63 | 0.70 | 0.77 | 0.83 | 0.88 | 0.93 | 0.97 | 1.00 |
| Outlet Damper, BI & Airfoil Fans | 0.53 | 0.53 | 0.57 | 0.64 | 0.72 | 0.80 | 0.89 | 0.96 | 1.02 | 1.05 |
| Inlet Damper Box | 0.56 | 0.60 | 0.62 | 0.64 | 0.66 | 0.69 | 0.74 | 0.81 | 0.92 | 1.07 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.53 | 0.56 | 0.57 | 0.59 | 0.60 | 0.62 | 0.67 | 0.74 | 0.85 | 1.00 |
| Inlet Vane Dampers | 0.38 | 0.40 | 0.42 | 0.44 | 0.48 | 0.53 | 0.60 | 0.70 | 0.83 | 0.99 |
| Outlet Damper, FC Fans | 0.22 | 0.26 | 0.30 | 0.37 | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06 |
| Eddy Current Drives | 0.17 | 0.20 | 0.25 | 0.32 | 0.41 | 0.51 | 0.63 | 0.76 | 0.90 | 1.04 |
| Inlet Guide Vane, FC Fans | 0.21 | 0.22 | 0.23 | 0.26 | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04 |
| VFD with duct static pressure controls | 0.09 | 0.10 | 0.11 | 0.15 | 0.20 | 0.29 | 0.41 | 0.57 | 0.76 | 1.01 |
| VFD with low/no duct static pressure | 0.05 | 0.06 | 0.09 | 0.12 | 0.18 | 0.27 | 0.39 | 0.55 | 0.75 | 1.00 |

Provided below is the resultant values based upon the defaults provided above:

| Control Type | 0%100%%FF×PLRBase |
| --- | --- |
| No Control or Bypass Damper | 1.00 |
| Discharge Dampers | 0.80 |
| Outlet Damper, BI & Airfoil Fans | 0.78 |
| Inlet Damper Box | 0.69 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.63 |
| Inlet Vane Dampers | 0.53 |
| Outlet Damper, FC Fans | 0.53 |
| Eddy Current Drives | 0.49 |
| Inlet Guide Vane, FC Fans | 0.39 |
| VFD with duct static pressure controls | 0.30 |
| VFD with low/no duct static pressure | 0.27 |

IEenergy		= HVAC interactive effects factor for energy (default = 15.7%)

###### Summer Coincident Peak Demand Savings

| kWBase = | 0.746×HP×LFηmotor×PLRBase, FFpeak |
| --- | --- |
| kWRetrofit = | 0.746×HP×LFηmotor× PLRRetrofit, FFpeak |
| ∆kWfan = | kWBase-kWRetrofit |
| ∆kWtotal = | ∆kWfan×(1+IEdemand) |

Where:

kWBase 		= Baseline summer coincident peak demand (kW)

kWRetrofit 		= Retrofit summer coincident peak demand (kW)

∆kWfan 		= Fan-only summer coincident peak demand impact

∆kWtotal 		= Total project summer coincident peak demand impact

PLRBase,FFpeak	= The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the baseline flow control type (default average flow fraction during peak period = 90%)

PLRRetrofit,FFpeak	= The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the retrofit flow control type (default average flow fraction during peak period = 90%)

IEdemand	= HVAC interactive effects factor for summer coincident peak demand
 (default = 15.7%)

###### Fossil Fuel Impact Descriptions and Calculation

There are no expected fossil fuel impacts for this measure.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-VSDF-V07-220101

###### Review Deadline: 1/1/2026

### Energy Recovery Ventilator

###### Description

This measure includes the addition of energy recovery equipment on existing or new unitary equipment, where energy recovery is not required by the IECC 2012/2015/2018. This measure analyzes the heating and cooling savings potential from recovering energy from exhaust or relief building air. This measure assumes that during unoccupied hours of the building no exhaust or relief air is available for energy recovery.

This measure was developed to be applicable to the following program types:  TOS, NC, RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Efficient equipment is unitary equipment that incorporates energy recovery not required by the IECC 2012/2015/2018.

###### Definition of Baseline Equipment

The baseline is unitary equipment not required by IECC 2012/2015/2018 to incorporate energy recovery.

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

###### Deemed Lifetime of Efficient Equipment

The measure life for the domestic energy recovery equipment is 15 years.

###### Deemed Measure Cost

The incremental cost for this measure assumes cost of cabinet and controls incorporated into packaged and built up air handler units. Additionally, it assumes a 1 to 1 ratio of fresh and exhausted air.

| Energy Recovery Equipment Type | Incremental Cost $/CFM |
| --- | --- |
| Plate Heat Exchanger | $3.75 |
| Rotary Wheel | $3.75 |
| Heat Pipe | $3.75 |

###### Deemed O&M Cost Adjustments

There are no expected O&M savings associated with this measure.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings Electric Energy Savings

The electric energy savings calculation here represents the net electric energy savings from reduced cooling requirements after accounting for increased fan power caused by additional pressure drop from the ERV device. These savings do not account for heating energy savings in HVAC systems using heat pumps or electric resistance heat. This calculation does not apply to wheel-type devices with purge sections, or to sensible-only devices such as heat pipes.

ΔkWh 		= (cfm) * Normalized Electric Energy Savings

cfm		= design supply air flow of energy recovery ventilator in cubic feet per minute

= rated energy recovery ventilator supply air flow * (1 – Exhaust Air Transfer Ratio)

Exhaust Air Transfer Ratio 		= percentage of supply air made up of cross-leakage      from exhaust air; value provided by vendor

= 0.05 (default)

Normalized Electric Energy Savings

= kWh/cfm savings value for the expected energy savings (net of fan energy penalty) as detailed in Table 1 – Electric Energy Savings Summary (kWh/cfm)

Table 1 – Electric Energy Savings Summary (kWh/cfm)

| Building Type | Normalized Electricity Savings (kWh/OA cfm) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 - Rockford | Zone 2 - Chicago | Zone 3 - Springfield | Zone 4 - Mt. Vernon/Belleville | Zone 5 - Marion |
| Enthalpy Wheel - 75% sensible and latent effectiveness |  |  |  |  |  |
| Assembly | NA | NA | NA | 0.107 | 0.229 |
| Education | NA | NA | 0.371 | 0.245 | 0.369 |
| Grocery | NA | NA | 0.239 | 0.523 | 0.630 |
| Healthcare | 1.551 | 1.594 | 2.508 | 2.999 | 3.077 |
| Multifamily | 2.178 | 2.566 | 3.781 | 4.746 | 5.029 |
| Office | 0.974 | 1.169 | 2.379 | 2.998 | 3.194 |
| Retail | 0.048 | 0.124 | 0.389 | 1.027 | 1.063 |
| Enthalpy Plate - 50% sensible and latent effectiveness |  |  |  |  |  |
| Assembly | NA | NA | NA | NA | NA |
| Education | NA | NA | NA | NA | 0.035 |
| Grocery | NA | NA | NA | 0.002 | 0.102 |
| Healthcare | 0.923 | 0.963 | 1.548 | 1.841 | 1.908 |
| Multifamily | 0.627 | 0.908 | 1.450 | 2.341 | 2.509 |
| Office | 0.309 | 0.487 | 1.321 | 1.705 | 1.918 |
| Retail | NA | NA | NA | 0.398 | 0.435 |

###### Summer Coincident Peak Demand Savings

ΔkW = (cfm) * Normalized Electric Peak Demand Savings * CF

= design supply air flow of energy recovery ventilator in cubic feet per minute

= rated energy recovery ventilator supply air flow * (1 – Exhaust Air Transfer Ratio)

Exhaust Air Transfer Ratio 		= percentage of supply air made up of cross-leakage      from exhaust air; value provided by vendor

= 0.05 (default)

CF	= 1.0

Normalized Electric Peak Demand Savings

= kW/cfm savings value for the appropriate combination of building type, climate zone, and measure scenario per Table 2 – Electric Peak Demand Savings Summary (kW/cfm)

Table 2 – Electric Peak Demand Savings Summary (kW/cfm)

| Building Type | Normalized Electric Demand Savings (kW/OA cfm) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 - Rockford | Zone 2 - Chicago | Zone 3 - Springfield | Zone 4 - Mt. Vernon/Belleville | Zone 5 - Marion |
| Enthalpy Wheel - 75% sensible and latent efficiency |  |  |  |  |  |
| Assembly | 0.00127 | 0.00092 | 0.00111 | 0.00213 | 0.00209 |
| Education | 0.00159 | 0.00164 | 0.00282 | 0.00202 | 0.00308 |
| Grocery | 0.00115 | 0.00159 | 0.00152 | 0.00153 | 0.00187 |
| Healthcare | 0.00465 | 0.00433 | 0.00480 | 0.00443 | 0.00443 |
| Multifamily | 0.00210 | 0.00325 | 0.00298 | 0.00370 | 0.00381 |
| Office | 0.00538 | 0.00518 | 0.00527 | 0.00529 | 0.00589 |
| Retail | 0.00156 | 0.00195 | 0.00020 | 0.00217 | 0.00223 |
| Enthalpy Plate - 50% sensible and latent efficiency |  |  |  |  |  |
| Assembly | NA | NA | 0.00024 | 0.00115 | 0.00113 |
| Education | 0.00114 | 0.00118 | 0.00201 | 0.00142 | 0.00218 |
| Grocery | 0.00059 | 0.00089 | 0.00083 | 0.00079 | 0.00102 |
| Healthcare | 0.00287 | 0.00284 | 0.00306 | 0.00292 | 0.00275 |
| Multifamily | NA | 0.00128 | 0.00111 | 0.00172 | 0.00167 |
| Office | 0.00351 | 0.00344 | 0.00344 | 0.00345 | 0.00384 |
| Retail | 0.00087 | 0.00123 | 0.00001 | 0.00119 | 0.00124 |

###### Natural Gas Savings

Gas savings algorithm is derived from the following:

ΔTherms 	= (Design Heating Load * TE_ERV * EFLH * OccHours/24) / (100,000 * µHeat)

Where:

Design Heating Load 	= (1.08 * CFM * ΔT)

1.08  	= A constant for sensible heat equations (BTU/h/CFM.°F)

CFM	= Cubic Feet per Minute of Energy Recovery Ventilator

ΔT 	= T_RA – T_DD

T_RA 	= Temperature of the Return Air = 70°F or custom

T_DD 	= Temperature on design day of outside air

= (see Table below) or custom

| Zone | Weather Station | T_DD, Temperature, °F |
| --- | --- | --- |
| 1 | Greater Rockford | -5.8 |
| 2 | Chicago/O’Hare ARPT. | -1.5 |
| 3 | Springfield/Capital | 0.4 |
| 4 | Scott AFB MidAmerica | 9.0 |
| 5 | Cape Girardeau Regional | 9.7 |
| Average | - | 2.4 |

TE_ERV 			= Thermal Effectiveness of Energy Recovery Equipment

= (see Table below) or custom

| Heat Recovery Equipment Type | TE_ERV (%) |
| --- | --- |
| Fixed Plate | 0.65 |
| Rotary Equipment | 0.68 |
| Heat Pipe | 0.55 |

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

OccHour	s		= Average Hours per day facility is occupied

= custom or use Modeling Inputs in eQuest models:

| Building Type | Weekday | Saturday | Sunday | Holiday | Annual Operating Hours | OccHours |
| --- | --- | --- | --- | --- | --- | --- |
| Assembly/Convention Center | 10am-9pm | 10am-9pm | 10am-9pm | closed | 3905 | 10.7 |
| Assisted Living | 24/7 | 24/7 | 24/7 | 24/7 | 8760 | 24.0 |
| College | 8am-9pm | closed | closed | closed | 3263 | 8.9 |
| Convenience Store | 7am-10pm | 9am-9pm | 10am-5pm | 10am-5pm | 4823 | 13.2 |
| Elementary School | 8am-4pm (20% in summer) | closed | closed | closed | 1606 | 4.4 |
| Garage | 7am-5pm | 8am-12pm | closed | closed | 3342 | 9.1 |
| Grocery | 7am-9pm | 7am-9pm | 9am-8pm | closed | 4814 | 13.2 |
| Healthcare Clinic | 7am-7pm | 9am-5pm | closed | closed | 3428 | 9.4 |
| High School | 8am-4pm (20% in summer) | closed | closed | closed | 1606 | 4.4 |
| Hospital | 24/7 | 24/7 | 24/7 | 24/7 | 8760 | 24.0 |
| Motel | 24/7 | 24/7 | 24/7 | 24/7 | 8760 | 24.0 |
| Manufacturing Facility (Light Industry) | Mfg: 6am-10pm, Office: 8am-5pm | Mfg: 6am-10pm, Office: closed | closed | closed | 4848 | 13.3 |
| Multi-Family Mid-Rise | 24/7; Reduced occupancy 7am - 5pm | 24/7; Reduced occupancy 9am - 3pm | 24/7; Reduced occupancy 9am - 3pm | 24/7; Reduced occupancy 9am - 3pm | 7038 | 19.3 |
| Multi-Family High-Rise | 24/7; Reduced occupancy 7am - 5pm | 24/7; Reduced occupancy 9am - 3pm | 24/7; Reduced occupancy 9am - 3pm | 24/7; Reduced occupancy 9am - 3pm | 7038 | 19.3 |
| Movie Theater | 10am-Midnight | 10am-Midnight | 10am-Midnight | 10am-Midnight | 5110 | 14.0 |
| Office - Low-rise | 8am-5pm | closed | closed | closed | 2259 | 6.2 |
| Office - Mid-rise | 8am-5pm | 20% 8am-noon | closed | closed | 2301 | 6.3 |
| Office - High-rise | 8am-5pm | 20% 8am-noon | closed | closed | 2301 | 6.3 |
| Religious Building | Office: 8am-5pm, other: closed | closed | 8am-1pm | closed | 260 | 0.7 |
| Restaurant | 7am-8pm | 7am-8pm | 7am-8pm | closed | 4615 | 12.6 |
| Retail - Department Store | 9am-9pm | 9am-9pm | 10am-5pm | 10am-5pm | 4070 | 11.1 |
| Retail - Strip Mall | 9am-9pm | 9am-9pm | 10am-5pm | 10am-5pm | 4070 | 11.1 |
| Warehouse (Conditioned Storage) | 7am-7pm | 7am-7pm (reduced occupancy) | closed | closed | 3324 | 9.1 |

µHeat			= Efficiency of heating system

= Actual

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-ERVE-V04-200101

###### Review Deadline: 1/1/2023

### Stack Economizer for Boilers Serving HVAC Loads

###### Measure Description

Stack economizers are designed to recover heat from hot boiler flue gasses. Recovered heat is used to preheat boiler feed water. This measure describes the retrofit of HVAC boilers with stack economizers. HVAC boilers are defined as those used for space heating applications. There is another, similar measure for boilers that serve process loads.

This measure was developed to be applicable to the following program types:  NC, TOS, RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify the economizer must be installed on a boiler exhaust stack. Heat captured by the economizer is to be used to pre-heat boiler feed water.

###### Definition of Baseline Equipment

The baseline boiler does not have an economizer installed.

###### Deemed Lifetime of Efficient Equipment

The measure life for the boiler stack economizer is 15 years.

###### Deemed Measure Cost

The incremental and full measure cost for this measure is custom.

###### Deemed O&M Cost Adjustments

The O&M cost for this measure is custom.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

Δtherms = SF * MBH_In * EFLH / 100

Where:

SF 	= Savings factor

= calculated custom as (T_existing – T_eff) / 40°F * TRE or when not possible a default value based on the table below

Where:

T_existing 	= Existing Full Fire Boiler Flue Gas Temperature as it exits the Stack

= 425F (water, 81.9% eff) or custom

= 480F (steam, 80.7% eff) or custom

T_eff 		= Efficient Full Fire Boiler Flue Gas Temperature as it exits the Stack

= 338°F (conventional economizer – Water Boiler) or custom

= 365°F (conventional economizer – Steam Boiler) or custom

= 280°F (condensing economizer – Water Boiler) or custom

= 308°F (condensing economizer – Steam Boiler) or custom

TRE 		= % efficiency increase for 40°F of stack temperature reduction

= 1%, or custom

Based on defaults provided above:

| Boiler Type | SF |  |
| --- | --- | --- |
|  | Conventional Economizer | Condensing Economizer |
| Hot Water Boiler | 2.19% average SF or custom | 3.63% average SF or custom |
| Steam Boiler | 2.88% average SF or custom | 4.31% average SF or custom |

MBH_In	= Rated boiler input capacity, in MBH

= Actual

EFLH	= Equivalent Full Load Hours for heating are provided in Section 4.4 HVAC End Use

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

Depending on design, stack economizers may require routine maintenance for optimal performance. A custom calculation should be used as necessary.

###### Measure Code: CI-HVC-BECO-V02-210101

###### Review Deadline: 1/1/2025

### Stack Economizer for Boilers Serving Process Loads

###### Measure Description

Stack economizers are designed to recover heat from hot boiler flue gasses. Recovered heat is used to preheat boiler feed water. This measure describes the retrofit of process boilers with stack economizers. Process boilers are defined as those used for industrial, manufacturing, or other non-HVAC applications. There is another, similar measure for boilers that serve HVAC loads.

This measure was developed to be applicable to the following program types:  NC, TOS, RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify the economizer must be installed on a boiler exhaust stack. Heat captured by the economizer is to be used to pre-heat boiler feed water.

###### Definition of Baseline Equipment

The baseline boiler does not have an economizer installed.

###### Deemed Lifetime of Efficient Equipment

The measure life for the boiler stack economizer is 15 years.

###### Deemed Measure Cost

The incremental and full measure cost for this measure is custom.

###### Deemed O&M Cost Adjustments

The O&M cost for this measure is custom.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

Δtherms 	= SF * MBH_In * 8766 * UF / 100

Where:

SF 	= (T_existing – T_eff)/40°F * TRE

= see default Savings Factor table below

T_existing 	= Existing Full Fire Boiler Flue Gas Temperature as it exits the Stack

= 425F (water, 81.9% eff per IL TRM) or custom

= 480F (steam, 80.7% eff per IL TRM) or custom

T_eff 		= Efficient Full Fire Boiler Flue Gas Temperature as it exits the Stack

= 338°F (conventional economizer – Water Boiler) or custom

= 365°F (conventional economizer – Steam Boiler) or custom

= 280°F (condensing economizer – Water Boiler) or custom

= 308°F (condensing economizer – Water Boiler) or custom

TRE 		= % efficiency increase for 40°F of stack temperature reduction

= 1%, or custom

Based on defaults provided above:

| Boiler Type | SF |  |
| --- | --- | --- |
|  | Conventional Economizer | Condensing Economizer |
| Hot Water Boiler | 2.19% average SF or custom | 3.63% average SF or custom |
| Steam Boiler | 2.88% average SF or custom | 4.31% average SF or custom |

MBH_In		= Rated boiler input capacity, in MBH

= Actual

8766		= Hours a year

UF		= Utilization Factor

= 41.9%, or custom

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-PECO-V02-220101

###### Review Deadline: 1/1/2026

### Notched V Belts for HVAC Systems

###### Measure Description

This measure is for replacement of smooth v-belts in non-residential package and split HVAC systems with notched v-belts or for installing new equipment with synchronous belts instead of smooth v-belts.  Typically there is a v-belt between the motor and the supply air fan and/or return air fan in larger package and split HVAC systems (RTU).

In general there are two styles of grooved v-belts, notched and synchronous.  The DOE defines each as follows;

Notched V-Belts - A notched belt has grooves or notches that run perpendicular to the belt’s length, which reduces the bending resistance of the belt. Notched belts can use the same pulleys as cross-section standard V-belts. They run cooler, last longer, and are about 2% more efficient than standard V-belts.

Synchronous Belts - Synchronous belts (also called cogged, timing, positive-drive, or high-torque drive belts) are toothed and require the installation of mating grooved sprockets. These belts operate with a consistent efficiency of 98% and maintain their efficiency over a wide load range.

Smooth v-belts are usually referred to in five basic groups:

- “L” belts are low end belts that are for small, fractional horsepower motors and these are not used in RTUs.

- “A” and “B” belts are the two types typically used in RTUs.  The “A” belt is a ½ inch width by 5/16 inch thickness and the “B” belt is larger, 21/32 inch wide and 12/32 inch thick so it can carry more power.  V-belts come in a wide variety of lengths where 20 to 100 inches is typical.

- “C” and “D” belts are primarily for industrial applications with high power transmission requirements.

- V-belts are provided by various vendors.  The notched version of these belts typically have an “X” added to the designation.  For this HVAC fans notched v-belt Replacement measure, only the “A” and “B” v-belts are considered.  A typical “A” v-belt is replaced by a notched “AX” v-belt and a “B” is replaced by a “BX.”  In general, smooth v-belts have an efficiency of 90% to 98% while notched v-belts have an efficiency of 95% to 98%.  Because notched v-belts are more flexible they work with smaller diameter pulleys and they have less resistance to bending.  Lower bending resistance increases the power transmission efficiency, lowers the waste heat, and allows the belt to last longer than a smooth belt.

Three research papers   show that the notched v-belt efficiency is 2% to 5% better than a typical smooth v-belt.  A fourth paper by USDOE’s Energy Efficiency and Renewable Energy  group reviewed most of the earlier literature and recommended using a conservative 2% efficiency improvement for energy savings for calculations.

For this measure it is assumed that upgrading a standard smooth v-belt with a new notched v-belt will result in a fan energy reduction of 2%.

###### Definition of Efficient Equipment

For the Notched V-Belt characterization to apply, the Efficient Equipment is HVAC RTUs that have notched v-belts installed on the supply and/or return air fans.  This can be done as a retrofit, TOS, or NC project.

For the Synchronous Belt characterization to apply, the Efficient Equipment is HVAC RTUs that have synchronous belts installed on the supply and/or return air fans. This can be done as a TOS or NC project. Retrofit projects can also claim savings, but costs should be verified independently (typically the cost of installing synchronous belts as a retrofit is not economically viable).

###### Definition of Baseline Equipment

The Baseline Equipment is HVAC RTUs that have smooth v-belts installed on the supply and/or return air fans (i.e., RTU does not already have a notched v-belt installed).

###### Deemed Lifetime of Efficient Equipment

A v-belt has a life based on fan run hours which varies by building type based primarily on occupancy schedule because the fans are required by code to operate continuously during occupied hours.  The supply and return fans will also run a few hours during unoccupied hours for heating and cooling as needed.  For the notched v-belt EUL calculation, the default hours in the following table are used for a variety of building types and HVAC applications.

EUL 	= Belt Life / Occupancy Hours per year

Where:

Belt Life 				= 24,000 hours

Occupancy Hours per year 	= values from Table below

The notched v-belt measure EUL is summarized by building type in the following table.

Notched v-belt Effective Useful Life (EUL)

| Building Type | Total Fan Run Hours | EUL (Years) | Model Source |
| --- | --- | --- | --- |
| Assembly | 7235 | 3.3 | eQuest |
| Assisted Living | 8760 | 2.7 | eQuest |
| Auto Dealership | 7451 | 3.2 | OpenStudio |
| College | 4836 | 5.0 | OpenStudio |
| Convenience Store | 7004 | 3.4 | eQuest |
| Drug Store | 7156 | 3.4 | OpenStudio |
| Elementary School | 3765 | 6.4 | OpenStudio |
| Emergency Services | 8760 | 2.7 | OpenStudio |
| Garage | 7357 | 3.3 | eQuest |
| Grocery | 8543 | 2.8 | OpenStudio |
| Healthcare Clinic | 4314 | 5.6 | OpenStudio |
| High School | 3460 | 6.9 | OpenStudio |
| Hospital - VAV econ | 4666 | 5.1 | OpenStudio |
| Hospital - CAV econ | 8021 | 3.0 | OpenStudio |
| Hospital - CAV no econ | 7924 | 3.0 | OpenStudio |
| Hospital - FCU | 4055 | 5.9 | OpenStudio |
| Manufacturing Facility | 8706 | 2.8 | eQuest |
| MF - High Rise | 8760 | 2.7 | OpenStudio |
| MF - Mid Rise | 8760 | 2.7 | OpenStudio |
| Hotel/Motel - Guest | 2409 | 10.0 | OpenStudio |
| Hotel/Motel - Common | 8683 | 2.8 | OpenStudio |
| Movie Theater | 7505 | 3.2 | eQuest |
| Office - High Rise - VAV econ | 2369 | 10.1 | OpenStudio |
| Office - High Rise - CAV econ | 2279 | 10.5 | OpenStudio |
| Office - High Rise - CAV no econ | 5303 | 4.5 | OpenStudio |
| Office - High Rise - FCU | 1648 | 14.6 | OpenStudio |
| Office - Low Rise | 6345 | 3.8 | OpenStudio |
| Office - Mid Rise | 3440 | 7.0 | OpenStudio |
| Religious Building | 7380 | 3.3 | eQuest |
| Restaurant | 7302 | 3.3 | OpenStudio |
| Retail - Department Store | 7155 | 3.4 | OpenStudio |
| Retail - Strip Mall | 6921 | 3.5 | OpenStudio |
| Warehouse | 6832 | 3.5 | OpenStudio |
| Unknown | 6241 | 3.8 | n/a |

The lifetime of a synchronous belt system is the same as the lifetime of the equipment it is installed on because it is a permanent upgrade, involving the installation of toothed pulleys. Typical HVAC RTU lifetime is 15 years, which applies to synchronous belts as well. This is not to suggest that the actual belt component has an equivalent lifetime because they do require replacement. However, their O&M cost savings (derived from not having to tension, etc.) are assumed to offset the replacement cost of the belt, resulting in a net cost of zero. As a result, neither a separate lifetime nor O&M savings are quantified for synchronous belts and lifetime can therefore be considered as the lifetime of the equipment they’re installed on because it would not be possible to install a traditional or notched belt on the synchronous pulleys.

###### Deemed Measure Cost

Costs of belts and pulleys are known to vary substantially based on belt length and pulley diameter. Two cost estimations are provided below; a fully deemed approach for applications such as an upstream program where limited information is known, and a semi-custom approach that is useful when more accurate cost estimates are desired.

Fully Deemed:

A review of the Grainger online pricing for “A,” “B,” “AX,” and “BX” v-belts revealed the incremental costs to upgrade to notched v-belts as summarized in the table below:

Notched V-belt Incremental Cost Summary

| Smooth V-Belt Industry Number | Outside Length (Inches) | Dayton Smooth V-Belt* | Notched V-belt Industry Number | Dayton Notched v-belt* | Price Increase | % Increase |
| --- | --- | --- | --- | --- | --- | --- |
| A30 (Item # 1A095) | 32 | $10.38 | AX30 (Item # 3GWU4) | $14.64 | $4.26 | 41% |
| B29 (Item # 6L208) | 32 | $14.38 | BX29 (Item # 5TXL4) | $20.80 | $6.42 | 45% |
| * Pricing based on Dayton Belts as found on Grainger Website 10/30/14 |  |  |  |  |  |  |

Note that the incremental cost for notched V-Belts assumes that the notched belt is purchased and installed instead of a smooth v-belt. There is no difference in the cost of installation, only the material.

Synchronous Belt Incremental Cost Summary

| Smooth V-Belt Industry Number | Smooth belt system Price* | Synchronous Belt Industry Number | Synchronous System Price* | Price Difference |
| --- | --- | --- | --- | --- |
| Belt A30 (Item # 1A095) | $10.38 | Belt 1DHL5 (Item # 322L050) | $15.37 | $4.99 |
| Gearbelt pulley BK47 (Item #5UHD5) | $47.98 | Gearbelt sprocket GTR-36G-8M-12 (Item # 2UWH6) | $113.91 | $65.93 |
| * Costs based on Grainger pricing. |  |  |  |  |

Incremental cost for a NC or TOS project is $136.85. This is the price of synchronous equipment (belt, two sprockets) subtract v-belt equipment (belt, two pulleys). Labor cost is assumed to be equal in the baseline and efficient cases.

Incremental cost for a RF project is $380.49. This is the price of synchronous equipment and labor to install it (not including a trip charge), less the cost of the v-belt (but not the pulleys).

Semi-Custom

Use the following relationships along with NC, TOS and RF assumptions outlined above to estimate semi-custom costs.

| Component | Type | Cost Function (per inch) | Inch Measurement |
| --- | --- | --- | --- |
| Standard V-Belt | A | $0.28/in + $0.96 | Outside Length |
| Standard V-Belt | B | $0.29/in + $9.15 | Outside Length |
| Standard Pulley | A, B, AX, BX | $11.85/in - $9.47 | Outside Diameter |
| Notched Belt | AX | $0.36/in + $1.07 | Outside Length |
| Notched Belt | BX | $0.49/in + $2.33 | Outside Length |
| Synchronous Belt | 1/2 inch | $0.58/in + $8.90 | Pitch Length |
| Synchronous Belt | 1 inch | $0.26/in + $5.67 | Pitch Length |
| Synchronous Pulley | for use with 1/2 inch belt | $27.20/in - $21.19 | Pitch Diameter |
| Synchronous Pulley | for use with 1 inch belt | $25.04/in - $27.23 | Pitch Diameter |

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

Loadshape C05 - Commercial Electric Heating and Cooling

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh  = kWconnected* Hours * ESF

Where:

kWConnected 	=kW of equipment is calculated using motor efficiency

= (HP * 0.746 kW/HP* Load Factor)/Motor Efficiency

Load Factor 	=Motors are assumed to have a load factor of 80% for calculating KW if actual values cannot be determined.  Custom load factor may be applied if known.

Motor Efficiency 	= Actual motor efficiency shall be used to calculate KW.  If not known a value from the motor efficiency refrence tables below should be used.  Default motor is a NEMA Premium Efficiency, ODP, 4-pole/1800 RPM fan motor.

| Baseline Motor Efficiencies (EPACT) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
|  | # of Poles |  |  |  |  |  |
|  | 6 | 4 | 2 | 6 | 4 | 2 |
|  | Speed (RPM) |  |  |  |  |  |
|  | 1200 | 1800 | 3600 | 1200 | 1800 | 3600 |
| 1/8 | - | 44.00% | - | - | - | - |
| 1/6 | 57.50% | 62.00% | - | - | - | - |
| 1/4 | 68.00% | 68.00% | - | 68.00% | 64.00% | - |
| 1/3 | 70.00% | 70.00% | 72.00% | 70.00% | 68.00% | 72.00% |
| 1/2 | 78.50% | 80.00% | 68.00% | 72.00% | 74.00% | 68.00% |
| 3/4 | 77.00% | 78.50% | 74.00% | 77.00% | 75.50% | 74.00% |
| 1 | 80.00% | 82.50% | 75.50% | 80.00% | 82.50% | 75.50% |
| 1.5 | 84.00% | 84.00% | 82.50% | 85.50% | 84.00% | 82.50% |
| 2 | 85.50% | 84.00% | 84.00% | 86.50% | 84.00% | 84.00% |
| 3 | 86.50% | 86.50% | 84.00% | 87.50% | 87.50% | 85.50% |
| 5 | 87.50% | 87.50% | 85.50% | 87.50% | 87.50% | 87.50% |
| 7.5 | 88.50% | 88.50% | 87.50% | 89.50% | 89.50% | 88.50% |
| 10 | 90.20% | 89.50% | 88.50% | 89.50% | 89.50% | 89.50% |
| 15 | 90.20% | 91.00% | 89.50% | 90.20% | 91.00% | 90.20% |
| 20 | 91.00% | 91.00% | 90.20% | 90.20% | 91.00% | 90.20% |
| 25 | 91.70% | 91.70% | 91.00% | 91.70% | 92.40% | 91.00% |

| Efficient Motor Efficiencies (NEMA Premium) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
|  | # of Poles |  |  | # of Poles |  |  |
|  | 2 | 4 | 6 | 2 | 4 | 6 |
|  | Speed (RPM) |  |  | Speed (RPM) |  |  |
|  | 1200 | 1800 (Default) | 3600 | 1200 | 1800 | 3600 |
| 0.125 * | - | 44.00% | - | - | - | - |
| 1/6 | 57.50% | 62.00% | - | - | - | - |
| 1/4 | 68.00% | 68.00% | - | 68.00% | 64.00% | - |
| 1/3 | 70.00% | 70.00% | 72.00% | 70.00% | 68.00% | 72.00% |
| 1/2 | 78.50% | 80.00% | 68.00% | 72.00% | 74.00% | 68.00% |
| 3/4 | 77.00% | 78.50% | 74.00% | 77.00% | 75.50% | 74.00% |
| 1 | 82.50% | 85.50% | 77.00% | 82.50% | 85.50% | 77.00% |
| 1.5 | 86.50% | 86.50% | 84.00% | 87.50% | 86.50% | 84.00% |
| 2 | 87.50% | 86.50% | 85.50% | 88.50% | 86.50% | 85.50% |
| 3 | 88.50% | 89.50% | 85.50% | 89.50% | 89.50% | 86.50% |
| 5 | 89.50% | 89.50% | 86.50% | 89.50% | 89.50% | 88.50% |
| 7.5 | 90.20% | 91.00% | 88.50% | 91.00% | 91.70% | 89.50% |
| 10 | 91.70% | 91.70% | 89.50% | 91.00% | 91.70% | 90.20% |
| 15 | 91.70% | 93.00% | 90.20% | 91.70% | 92.40% | 91.00% |
| 20 | 92.40% | 93.00% | 91.00% | 91.70% | 93.00% | 91.00% |
| 25 | 93.00% | 93.60% | 91.70% | 93.00% | 93.60% | 91.70% |

Hours 	= When available, actual hours should be used. If actual hours are not available, default hours are provided in table below for HVAC fan operation, which varies by building type:

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly | 7235 | eQuest |
| Assisted Living | 8760 | eQuest |
| Auto Dealership | 7451 | OpenStudio |
| College | 4836 | OpenStudio |
| Convenience Store | 7004 | eQuest |
| Drug Store | 7156 | OpenStudio |
| Elementary School | 3765 | OpenStudio |
| Emergency Services | 8760 | OpenStudio |
| Garage | 7357 | eQuest |
| Grocery | 8543 | OpenStudio |
| Healthcare Clinic | 4314 | OpenStudio |
| High School | 3460 | OpenStudio |
| Hospital - VAV econ | 4666 | OpenStudio |
| Hospital - CAV econ | 8021 | OpenStudio |
| Hospital - CAV no econ | 7924 | OpenStudio |
| Hospital - FCU | 4055 | OpenStudio |
| Manufacturing Facility | 8706 | eQuest |
| MF - High Rise | 8760 | OpenStudio |
| MF - Mid Rise | 8760 | OpenStudio |
| Hotel/Motel - Guest | 2409 | OpenStudio |
| Hotel/Motel - Common | 8683 | OpenStudio |
| Movie Theater | 7505 | eQuest |
| Office - High Rise - VAV econ | 2369 | OpenStudio |
| Office - High Rise - CAV econ | 2279 | OpenStudio |
| Office - High Rise - CAV no econ | 5303 | OpenStudio |
| Office - High Rise - FCU | 1648 | OpenStudio |
| Office - Low Rise | 6345 | OpenStudio |
| Office - Mid Rise | 3440 | OpenStudio |
| Religious Building | 7380 | eQuest |
| Restaurant | 7302 | OpenStudio |
| Retail - Department Store | 7155 | OpenStudio |
| Retail - Strip Mall | 6921 | OpenStudio |
| Warehouse | 6832 | OpenStudio |
| Unknown | 6241 | n/a |

ESF 		= Energy Savings Factor, the ESF for notched v-belt Installation is assumed to be 2%

= the ESF for notched Synchronous Belt Installation is assumed to be 3.1%

For example, a notched v-belt installation in an low rise office building RTU with a 5 HP NEMA premium efficiency motor  using the default hours of operation, motor load and 89.5% motor efficiency;

ΔkWh	= kWconnected* Hours * ESF

= ((HP * 0.746 kW/HP* Load Factor)/Motor Efficiency) * Hours * ESF

= ((5 HP * 0.746 kW/HP* 80%) / 89.5%) * 6288 * 2%

= 419 kWh Savings

Summer Coincident Peak Demand Savings

ΔkW  = kWconnected* ESF * CF

Where:

kWConnected  		= kW of equipment is calculated using motor efficiency.

= (HP *0 .746 kW/HP* Load Factor)/Motor Efficiency

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Variables as provided above

For example, an office building RTU with a 5 HP NEMA premium efficiency motor using the default motor load and 89.5% motor efficiency;

ΔkWSSP	= kWconnected* ESF * CF

= ((HP * 0.746 kW/HP* Load Factor)/Motor Efficiency) * ESF * CF

= ((5 HP * 0.746 kW/HP* 80%) / 89.5%) * 2% * 0.913

= 0.0609 kW Savings

###### Natural Gas Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-NVBE-V06-210101

###### Review Deadline: 1/1/2026

### Small Business Furnace Tune-Up

###### Description

This measure is for a natural gas Small Business furnace that provides space heating.  The tune-up will improve furnace performance by inspecting, cleaning and adjusting the furnace and appurtenances for correct and efficient operation.  Additional savings maybe realized through a complete system tune-up.

This measure was developed to be applicable to the following program types: Small business.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure an approved technician must complete the tune-up requirements listed below:

- Measure combustion efficiency using an electronic flue gas analyzer

- Check and clean blower assembly and components per manufacturer’s recommendations

- Where applicable Lubricate motor and inspect and replace fan belt if required

- Inspect for gas leaks

- Clean burner per manufacturer’s recommendations and adjust as needed

- Check ignition system and safety systems and clean and adjust as needed

- Check and clean heat exchanger per manufacturer’s recommendations

- Inspect exhaust/flue for proper attachment and operation

- Inspect control box, wiring and controls for proper connections and performance

- Check air filter and clean or replace per manufacturer’s

- Inspect duct work connected to furnace for leaks or blockages

- Measure temperature rise and adjust flow as needed

- Check for correct line and load volts/amps

- Check thermostat operation is per manufacturer’s recommendations (if adjustments made, refer to ‘Small Commercial Programmable Thermostat Adjustment’ measure for savings estimate)

- Perform Carbon Monoxide test and adjust heating system until results are within standard industry acceptable limits

###### Definition of Baseline Equipment

The baseline is furnace assumed not to have had a tune-up in the past 3 years.

###### Deemed Lifetime of Efficient Equipment

The measure life for the tune up is 3 years.

###### Deemed Measure Cost

The incremental cost for this measure should be the actual cost of tune up.

###### Deemed O&M Cost Adjustments

There are no expected O&M savings associated with this measure.

###### Loadshape

Loadshape C04 - Commercial Electric Heating

###### Coincidence Factor

N/A

Algorithms

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh		= ΔTherms * Fe * 29.3

Where:

ΔTherms 	= as calculated below

Fe		= Furnace Fan energy consumption as a percentage of annual fuel consumption

= 7.7%

29.3		= kWh per therm

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

ΔTherms 	= (Capacity * EFLH * (((Effbefore + Ei)/ Effbefore) – 1)) / 100,000

Where:

Capacity 	= Furnace gas input size (Btu/hr)

= Actual

EFLH       		=  Equivalent Full Load Hours for heating in Existing Buildings are provided 			in section 4.4 HVAC End Use

Effbefore	= Efficiency of the furnace before the tune-up

= Actual

Note: Contractors should select a mid-level firing rate that appropriately represents the average building operating condition over the course of the heating season and take readings at a consistent firing rate for pre and post tune-up.

EI            		= Efficiency Improvement of the furnace tune-up measure

= Actual

100,000 	= 	Converts Btu to therms

For example, a 200 kBtu furnace in a Rockford low rise office records an efficiency prior to tune up of 82% AFUE and a 1.8% improvement in efficiency are tune up:

Δtherms 		= (200,000 * 1428 * (((0.82 + 0.018)/ 0.82) – 1)) /100,000

= 62.3 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-FTUN-V04-220101

###### Review Deadline: 1/1/2023

### Combined Heat and Power

###### Description

During 2021, the TAC commenced discussions around updating this measure. Unfortunately, due to time constraints, an agreed approach was not determined and as such v10 is identical to v9. The TAC will work towards an update for v11.

The Combined Heat and Power (CHP) measure can provide energy savings within the State of Illinois through the development and operation of CHP projects. This measure is applicable for Conventional or Topping Cycle CHP systems, as well as Waste Heat-to-Power (WHP) or Bottoming Cycle CHP systems. The measure will reduce the total Btu’s of energy required to meet the end use needs of the facility.

It is recognized that CHP system design and configuration may be complex, and as such the calculation of energy savings may not be reducible to the equations within this measure. In such cases a more comprehensive engineering and financial analysis may be developed that more accurately incorporates the attributes of complex CHP configurations such as variable-capacity systems, and partial combined-cycle CHP systems. Where noted, the use of values that are determined through an external engineering analysis may be substituted by agreement between the participant, the program administrator and independent evaluator. This substitution of values does not eliminate ex post evaluation risk (retroactive adjustments to savings claims) that exists when using custom inputs.

This measure was developed to be applicable to the following program types: Retrofit (RF), New Construction (NC). If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Conventional or Topping Cycle CHP is defined as an integrated system that is located at or near the building or facility (on-site, on the customer side of the meter) that utilizes a prime mover (reciprocating engine, gas turbine, micro-turbine, fuel cell, boiler/steam turbine combination) for the purpose of generating electricity and useful thermal energy (such as steam, hot water, or chilled water) where the primary function of the facility where the CHP is located is not to generate electricity for use on the grid. An eligible system must demonstrate a minimum total system efficiency of 60% (HHV), with at least 20% of the system’s total useful energy output in the form of useful thermal energy on an annual basis.

Measuring and Calculating Conventional CHP Total System Efficiency:

CHP efficiency is calculated using the following equation:

CHP EfficiencyHHV= CHPthermal   kBtuyr+ ECHP  kWhyr*3.412 kBtukWhFtotalCHPkBtuyr

Where:

CHP thermal 	= Useful annual thermal energy output from the CHP system, defined as the annual thermal energy output of the CHP system that is actually recovered and utilized in the facility/process.

ECHP 	= Useful annual electricity output produced by the CHP system, defined as the annual electric energy output of the CHP system that is actually utilized to replace purchased electricity required to meet the requirements of the facility/process.

FtotalCHP 	= Total annual fuel consumed by the CHP system

For further definition of the terms, please see “Calculation of Energy Savings” Section below.

Waste Heat-to-Power or Bottoming Cycle CHP is defined as an integrated system that is located at or near the building or facility (on-site, on the customer side of the meter) that does one of the following:

- Utilizes exhaust heat from an industrial/commercial process to generate electricity (except for exhaust heat from a facility whose primary purpose is the generation of electricity for use on the grid); or

- Utilizes the pressure drop in an industrial/commercial facility to generate electricity through a backpressure steam turbine where the facility normally uses a pressure reducing valve (PRV) to reduce the pressure in their facility; or

- Utilizes the pressure reduction in natural gas pipelines (located at natural gas compressor stations) before the gas is distributed through the pipeline to generate electricity, provided that the conversion of energy to electricity is achieved without using additional fossil fuels.

Since these types of systems utilize waste heat as their fuel, they do not have to meet any specific total system efficiency level (assuming they use no additional fossil fuel in their operation) If additional fuel is used onsite, it should be accounted for using the following methodology:

- Treat the portion of Waste-Heat-to-Power that does not require any additional fuel using the Waste-Heat-to-Power methodology outlined in this document.

- Treat the portion of Waste-Heat-to-Power that requires additional fuel (if natural gas) using the Conventional CHP methodology outlined in this document. If the additional fuel is not natural gas, custom carbon equivalency calculations would be needed – refer to section “Calculation of Energy Savings” for more details.

- Add the energy savings together.

These systems may export power to the grid.

###### Definition of Baseline Equipment

Electric Baseline: The baseline facility would be a facility that purchases its electric power from the grid.

Heating Baseline (for CHP applications that displace onsite heat): The baseline equipment would be the boiler/furnace operating onsite, or a boiler/furnace meeting the baseline equipment defined in the High Efficiency Boiler (Section 4.4.10)/Furnace (Section 4.4.11) measures of this TRM.

Cooling Baseline (for CHP applications that displace onsite cooling demands): The baseline equipment would be the chiller (or chillers) operating onsite, or a chiller (or chillers) meeting the definition of baseline equipment defined in the Electric Chiller (Section 4.4.6) measure of this TRM.

Facilities that use biogas or waste gas: Facilities that use (but are not purchasing) biogas or waste gas that is not otherwise used, whether they are using biogas or waste gas only or a combination of biogas or waste gas and natural gas to meet their energy demands are also eligible for this measure. If additional fuel is purchased to power the CHP system, then the additional natural gas should be taken into account using the following methodology:

- Treat the portion of CHP system that does not require any additional fuel, or that requires additional fuel that would otherwise be wasted (e.g., flared), using the Waste-Heat-to-Power methodology outlined in this document.

- Treat the portion of CHP that requires additional fuel (if natural gas) using the Conventional CHP  methodology outlined in this document. If the additional fuel is not natural gas, custom carbon equivalency calculations would be needed – refer to section “Calculation of Energy Savings” for more details.

- Add the energy savings together.

Consumption of any biogas or waste gas that would not otherwise being wasted (e.g., flared) will be accounted for in the overall net BTU savings calculations the same as for purchased natural gas.

###### Deemed Lifetime of Efficient Equipment

Measure life is a custom assumption, dependent on the technology selected and the system installation.

###### Deemed Measure Cost

Custom installation and equipment cost will be used. These costs should include the cost of the equipment and the cost of installing the equipment. Equipment costs include, but are not limited to: prime mover, heat recovery system(s), exhaust gas treatment system(s), controls, and any interconnection/electrical connection costs.

The installations costs include labor and material costs such as, but not limited to: labor costs, materials such as ductwork, piping, and wiring, project and construction management, engineering costs, commissioning costs, and other fees.

Measure costs will also include the present value of expected maintenance costs over the life of the CHP system.

###### Loadshape

Use Custom Loadshape. The loadshape should be obtained from the actual CHP operation strategy, based on the On-Peak and Off-Peak Energy definitions specified in Table 3.3 of “Section 3.5 Electrical Loadshapes” of the TRM.

###### Coincidence Factor

Custom coincidence factor will be used. Actual value based on the CHP operation strategy will be used.

Algorithm

###### Calculation of Energy Savings

- Conventional or Topping Cycle CHP Systems:

Step 1: (Calculating Total Annual Source Fuel Savings in Btus)

The first step is to calculate the total annual source fuel savings associated with the CHP installation, in order to ensure the CHP project produces positive total annual source fuel savings (i.e., reduction in source Btus):

SFuelCHP 	= Annual fuel savings (Btu) associated with the use of a Conventional CHP system to generate the useful electricity output (kWh, converted to Btu) and useful thermal energy output (Btu) versus the use of the equivalent electricity generated and delivered by the local grid and the equivalent thermal energy provided by the onsite boiler/furnace.

= (Fgrid + FthermalCHP) – Ftotal CHP

Where:

Fgrid	= Annual fuel in Btu that would have been used to generate the useful electricity output of the CHP system if that useful electricity output was provided by the local utility grid.

= ECHP * Hgrid

Where:

ECHP  	= Useful annual electricity output produced by the CHP system, defined as the annual electric energy output of the CHP system that is actually utilized to replace purchased electricity required to meet the requirements of the facility/process.

= ( CHPcapacity * Hours  ) - EParasitic

CHPcapacity 	= CHP nameplate capacity

= Custom input

Hours 		= Annual operating hours of the system

= Custom input

Eparasitic 		= The electricity required to operate the CHP system that would otherwise not be required by the facility/process

= Custom input

Hgrid 	= Heat rate of the grid in Btu/kWh, based on the average fossil heat rate for the EPA eGRID subregion, adjusted to  take into account T&D losses.

For systems operating less than 6,500 hrs per year:

Use the Non-baseload heat rate provided by EPA eGRID for RFC West region for ComEd territory (including independent providers connected to RFC West), and SERC Midwest region for Ameren territory (including independent providers connected to SERC Midwest). Also include any line losses.

For systems operating more than 6,500 hrs per year:

Use the All Fossil Average heat rate provided by EPA eGRID for RFC West region for ComEd territory (including independent providers connected to RFC West), and SERC Midwest region for Ameren territory (including independent providers connected to SERC Midwest). Also include any line losses.

FthermalCHP 	= Annual fuel in Btu that would have been used on-site by a boiler/furnace to provide the useful thermal energy output of the CHP system.

= CHPthermal / Boilereff  (or CHPthermal / Furnaceeff)

CHPthermal 	= Useful annual thermal energy output from the CHP system, defined as the annual thermal energy output of the CHP system that is actually recovered and utilized in the facility/process.

= Custom input

Boilereff /Furnaceeff= Efficiency of the on-site Boiler/Furnace that is displaced by the CHP system or if unknown, the baseline equipment value stated in the High Efficiency Boiler (Section 4.4.10) measure or High Efficiency Furnace (Section 4.4.11) measure in this TRM.

= Custom input

Ftotal CHP 	= Total fuel in Btus consumed by the CHP system

= Custom input

Step 2: (Savings Allocation to Program Administrators for Purposes of Assessing Compliance with Energy Savings Goals (Not for Use in Load Reduction Forecasting))

Savings claims are a function of the electric output of the CHP system (ECHP), the used thermal output of the CHP system (FthermalCHP), and the CHP system efficiency (CHPEff(HHV)).  The percentages of electric output and used thermal output that can be claimed also differ slightly depending on whether the project was included in both electric and gas Energy Efficiency Portfolio Standard (EEPS) efficiency programs, only an electric EEPS program or only a gas EEPS program.  The tables below provide the specific percentages of electric and/or thermal output that can be claimed under each of those three scenarios.  These percentages apply only to cases in which natural gas is the fuel used by the CHP system.  Saving estimates for systems using other fuels should be calculated on a custom basis. If the waste heat recovered from the CHP system is offsetting electric equipment, such as an absorption chiller offsetting an electric chiller, then the net change in electricity consumption associated with the electric equipment should be added to the allocated electric savings.

1)      For systems participating in both electric EEPS and gas EEPS programs:

| CHP Annual System Efficiency (HHV) | Allocated Electric Savings | Allocated Gas Savings |
| --- | --- | --- |
| 60% | 65% of ECHP (kWh) | No gas savings |
| >60% to 65% | 65% of ECHP (kWh) + one percentage point increase for every one percentage point increase in CHP system efficiency (max 70% of ECHP in kWh) | No gas Savings |
| >65% | 70% of Echp (kWh) | 2.5% of Fthermal (Boiler Natural Gas offset by CHP thermal) for every one percentage point increase in CHP system efficiency above 65%. |

Example: System with measured annual system efficiency (HHV) of 70%:  Electric savings (kWh) = 70% of ECHP measured over 12 months, and Gas savings (therms) = 12.5% of Fthermal measured over 12 months (70% - 65% = 5 X 2.5% = 12.5%).

2)      For systems participating in only an electric EEPS program:

| CHP Annual System Efficiency (HHV) | Allocated Electric Savings | Allocated Gas Savings |
| --- | --- | --- |
| 60% | 65% of ECHP (useful electric output of CHP system in kWh) | No gas Savings |
| Greater than 60% | 65% + one percentage point increase for every one percentage point increase in CHP system efficiency (no max) | No gas Savings |

Example: System with measured annual fuel use efficiency of 75%:  Electric savings (kWh) = 65% + 15% = 80% of ECHP measured over 12 months (15% = 1% for every 1% increase in system efficiency). No gas savings (therms).

3)      For systems participating in only a gas EEPS program:

| CHP Annual System Efficiency (HHV) | Allocated Electric Savings | Allocated Gas Savings |
| --- | --- | --- |
| 60% or greater | No electric savings | 2.5% of Fthermal (Boiler Natural Gas offset by CHP thermal) for every one percentage point increase in CHP system efficiency above 60%. |

Example: System with measured annual system efficiency (HHV) of 70%:  No Electric savings (kWh). Gas savings (therms) = 25% of Fthermal measured over 12 months (70% - 60% = 10 X 2.5% = 25%).

Conventional or topping cycle CHP systems virtually always require an increase in the use of fuel on-site in order to produce electricity. Different jurisdictions and experts across the country have employed and/or put forward a variety of approaches to address how increased on-site fuel consumption should be reflected in the attribution of electric savings to CHP systems.  The approach reflected in the tables above is generally consistent – for CHP systems consuming natural gas – with approaches recently put forward by the Southwest Energy Efficiency Project (SWEEP) and Institute for Industrial Productivity (IIP) that determine reduced electric savings based on the equivalent amount of carbon dioxide generated from the increased fuel used.

There are a variety of ways one could treat the potential for gas utilities to claim savings from CHP projects in their EEPS portfolios.  For projects in which a natural gas  EEPS program is involved, the tables above treat savings from CHP installations in two steps:  (1) a fuel-switch from electricity to natural gas (i.e., using more natural gas to eliminate the need to generate as much electricity on the grid); and (2) possible increases in CHP efficiency above a “benchmark” level.  When both electric EEPS and natural gas EEPS programs are involved in a project, the program administrator claims all the electricity savings associated with a fuel-switch up to a “benchmark” 65% efficient CHP system.  All the savings associated with increasing CHP efficiencies above that benchmark level are allocated to natural gas (e.g., if the CHP efficiency is 75%, the natural gas savings associated with an increase in CHP efficiency from 65% to 75% are allocated to natural gas).  That is consistent with the notion that CHP efficiency typically increases primarily by increasing the use of the thermal output of the system (increasing the displacement of baseline gas use).  For projects that involve only a natural gas EEPS program, the “benchmark” above which the gas utility can claim savings is lowered to 60%.

- Waste-Heat-to-Power CHP Systems :

###### Electric Energy Savings:

ΔkWh 	= ECHP

Where:

ECHP	= Useful annual electricity output produced by the CHP system, defined as the annual electric energy output of the CHP system that is actually utilized to replace purchased electricity required to meet the requirements of the facility/process.

= Custom input

###### Summer Coincident Peak Demand Savings

ΔkW 	= CF * CHPcapacity

Where:

CF 	= Summer Coincidence factor. This factor should also consider any displaced chiller capacity.

= Custom input

CHPCapacity	= CHP  nameplate capacity

= Custom input

###### Natural Gas Energy Savings:

ΔTherms = FthermalCHP ÷ 100,000

Where:

FthermalCHP	= Net savings in annual purchased fuel in Btu, if any, that would have been used on-site by a boiler/furnace  to provide some or all of the useful thermal energy output of the CHP system.

100,000 	= Conversion factor for Btu to therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

Custom estimates of maintenance costs that will be incurred for the life of the measure will be used. Maintenance costs vary with type and size of the prime mover. These costs include, but are not limited to:

- Maintenance labor

- Engine parts and materials such as oil filters, air filters, spark plugs, gaskets, valves, piston rings, electronic components, etc. and consumables such as oil

- Minor and major overhauls

For screening purposes, the US EPA has published resource guides that provide average maintenance costs based on CHP technology and system size.

###### Cost-Effectiveness Screening and Load Reduction Forecasting

For the purposes of forecasting load reductions due to CHP projects, changes in site energy use at the customer’s meter – reduced consumption of utility provided electricity –  adjusted for utility line losses (at-the-busbar savings), customer switching estimates, NTG, and any other adjustment factors deemed appropriate, should be used.

For the purposes of screening a CHP measure application for cost-effectiveness, changes in site energy use – reduced consumption of utility provided electricity and the net change in consumption of fuel –  should be used.  In general, the benefit and cost components used in evaluating the cost-effectiveness of a CHP project would include at least the following terms:

Benefits: 	ECHP + ΔkW + Fthermal_CHP

Costs: 		Ftotal_CHP + CHPCOSTS +O&MCOSTS

Where:

CHPCosts 	= CHP equipment and installation costs as defined in the “Deemed Measure Costs” section

O&MCosts	= CHP operations and maintenance costs as defined in the “Deemed O&M Cost Adjustment Calculation” section

###### Measure Code: CI-HVC-CHAP-V06-220101

###### Review Deadline: 1/1/2023

### Industrial Air Curtain

###### Description

This measure applies to buildings with exterior entryways that utilize overhead doors. All other air curtain applications, such as through sliding door entryways or conventional foot-traffic entryways, require custom analysis as air curtain designs must often accommodate other factors that may change their effectiveness.

The use of overhead doors within exterior entryways during the heating season leads to the exfiltration of warm air from the upper portion of the door opening and the infiltration of colder air from the lower portion of the door opening. This results in increase heating energy use to compensate for heat losses every time a door is opened. By reducing heat losses, air curtains can also enhance the physical comfort of employees or customers near the entryway as there will be reduced temperature fluctuations when the door is opened and closed. In addition, in some cases excess heating capacity may be installed in buildings to meet this larger heating load. The addition of air curtains to exterior entryways that currently utilize overhead doors will result in energy savings and enhanced personal comfort, and also possibly in reduced equipment sizing and corresponding costs.

The primary markets for this measure are commercial and industrial facilities with overhead doors in exterior entryways, including but not limited to the following building types: retail, manufacturing, and warehouse (non-refrigerated).

Limitations

- For use in conditioned spaces with an overhead door in an exterior entryway. This measure does include other door types such doorways to commercial spaces such as retail.

- This measure should only be applied to spaces in which the overhead door separates a conditioned space and an unconditioned space.

- Installation must follow manufacturer recommendations to attain proper air velocity, discharge angle down to the floor level, and unit position.

- Certain heating systems may not be a good fit for air curtains, such as locations with undersized heating capacity. In these cases, the installation of an air curtain may not effectively reduce heating system cycling given the inappropriately sized heating capacity.

- Buildings with slightly positive to slightly negative (~5 Pa to -10 Pa). For all other scenarios, custom analysis is recommended.

- Measure assumes that wind speeds at near ground level are less than or equal to 12 mph for 90% of the heating or cooling season. For areas with more extreme weather, custom analysis is necessary.

- Note: for cost effectiveness, it is recommended that minimum door open times should be approximately 15 hours per week.

This measure was developed to be applicable to the following program types: NC, RF. If applied to other program types, the measure savings should be verified.

The following methodology is highly complex and requires significant data collection. It is hoped that simplifying steps can be made in future iterations based on continued metering and evaluation of installations. Also the data collected through implementing the measure in the way currently drafted will aid in simplifying efforts at a future date.

###### Definition of Efficient Equipment

Overhead air curtains designed for commercial and industrial applications that have been tested and certified in accordance with ANSI/AMCA 220 and installed following manufacturer guidelines. Measure is for standard models without added heating.

###### Definition of Baseline Equipment

No air curtain or other currently installed means to effectively reduce heat loss and air mixing during door openings, such as a vestibule or strip curtain.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years.

###### Deemed Measure Cost

The incremental capital cost for overhead air curtains for exterior entryways are as follows, with an added average installation cost approximately equal to the capital cost.

| Door Size | Capital Cost |
| --- | --- |
| 8’w x 8’h | $3,600 |
| 10’w x 10’h | $4,500 |
| 10’w x 12’h | $5,400 |
| 12’w x 14’h | $8,000 |
| 16’w x 16’h | $13,300 |

###### Loadshape

Heating Season: If electric heating, use Commercial Electric Heating Loadshape: C04. Otherwise, N/A

Cooling Season: Commercial Cooling Loadshape C03. Or, if applicable, use Commercial Electric Heating and Cooling Loadshape C05.

###### Coincidence Factor

CFSSP 	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

The following formulas provide a methodology for estimating cooling load (kWh) and heating load (therm) savings associated with the installation of air curtains on exterior entryways such as a single door or loading bay. This algorithm is based on the assumption that therm savings are directly related to the difference in cooling or heating losses due to infiltration or exfiltration through an entryway before and after the installation of an AMCA certified air curtain. Energy savings are assumed to be the result of a reduction of natural infiltration effects due to wind and thermal forces and follow the calculation methodology outlined by the ASHRAE Handbook. The calculation assumes that the air curtain is appropriately sized and commissioned to be effective in mitigating infiltration of winds of up to 12 mph for at a least 90% of the year (based on manufacturer literature and TMY3 wind speed ranges at near ground level for Illinois). Additionally, this measure assumes the HVAC systems are appropriately balanced such that the maximum pressure differential between indoor air and outdoor air is within the range of 5 Pa < P < -10 Pa. Custom analysis is necessary if building pressurization exceeds this range. However, while effectiveness decreases, some studies suggest that air curtains outperform vestibules and single door construction for negatively pressurized buildings with a P of above -30 Pa.

This algorithm allows either actual inputs or provides estimates if actual data is not available. All weather dependent values are derived from TMY3 data for the closest weather station to those locations defined elsewhere in the Illinois TRM (which are based on 30 year climate normals). If TMY3 weather station data was not available for the data used in the Illinois TRM, the next closest weather station was used. It is assumed that weather variations are negligible between the weather stations located within the same region. This approach was followed as the air curtain algorithm has a number of weather dependent variables, which are all calculated in relation to the heating season or cooling season as defined by the balance point temperature deemed appropriate for the facility. All weather dependent data is based on TMY3 data and is listed in tables by both climate zone and balance point temperature, which is then normalized to the Illinois TRM climate zoned HDD/CDD definitions unless otherwise noted.

###### Electric Energy Savings

kWhcooling	= [(Qtbc – Qtac) / EER – (HP * 0.7457)] * topen * CD

kWhHPheating	= [(Qtbc – Qtac) / HSPF – (HP * 0.7457)] * topen * HD

kWhGasheating	= - (HP * 0.7457) * topen * HD

Where:

Qtbc	= rate of total heat transfer through the open entryway, before air curtain (kBtu/hr)

Qtac	= rate of total heat transfer through the open entryway, after air curtain (kBtu/hr)

(see calculation in ‘Heat Transfer Through Open Entryway with/without Air Curtain’ sections  below)

EER	= energy efficiency ratio of the cooling equipment (kBtu/kWh)

= Actual. If unknown, use the table C403.2.3(2) in IECC 2012 (or IECC 2018 if through new construction) to assume values based on code estimates.

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

HP	= Input power for air curtain (hp)

= Actual value. If actual value not available, use the following estimates based on manufacturer specs

| Door Size | Fan HP |
| --- | --- |
| 8’w x 8’h | 1 |
| 10’w x 10’h | 1.5 |
| 10’w x 12’h | 4 |
| 12’w x 14’h | 6 |
| 16’w x 16’h | 12 |

0.7457	= unit conversion factor, brake horsepower to electric power (kW/HP)

topen	= average hours per day the door is open (hr/day)

= Actual or user defined estimated value.

CD	= cooling days per year, total days in year above balance point temperature (day)

= use table below to select the best value for location:

| . | CD (Balance Point Temperature) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 45 oF | 50 oF | 55 oF | 60 oF | 65 oF |
| 1 - Rockford AP / Rockford | 194 | 168 | 148 | 124 | 97 |
| 2 - Chicago O'Hare AP / Chicago | 194 | 173 | 153 | 127 | 95 |
| 3 - Springfield #2 / Springfield | 214 | 194 | 174 | 148 | 114 |
| 4 - Belleville SIU RSCH / Belleville | 258 | 229 | 208 | 174 | 138 |
| 5 - Carbondale Southern IL AP / Marion | 222 | 201 | 181 | 158 | 130 |

HSPF	= Heating System Performance Factor of heat pump equipment

= Actual. If unknown, use the table C403.2.3(2) in IECC 2012 (or IECC 2018 if through new construction) to assume values based on code estimates.

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

HD	= heating days per year, total days in year above balance point temperature (day)

= use table below to select an appropriate value:

|  | HD |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Climate Zone Weather Station/City | 45 oF | 50 oF | 55 oF | 60 oF | 65 oF |
| 1 - Rockford AP / Rockford | 142 | 160 | 183 | 204 | 228 |
| 2 - Chicago O'Hare AP / Chicago | 150 | 166 | 192 | 219 | 253 |
| 3 - Springfield #2 / Springfield | 125 | 142 | 167 | 194 | 230 |
| 4 - Belleville SIU RSCH / Belleville | 101 | 115 | 134 | 156 | 180 |
| 5 - Carbondale Southern IL AP / Marion | 103 | 123 | 148 | 174 | 205 |

Heat Transfer Through Open Entryway without Air Curtain (Cooling Season)

Qtbc		= 4.5 * CFMtot *(hoc – hic) / (1,000 Btu/kBtu)

Where:

4.5	= unit conversion factor with density of air: 60 min/hr * 0.075 lbm/ft3 (lb*min/(ft*hr))

CFMtot	= Total air flow through entryway (cfm), see calculation below

hoc	= average enthalpy of outside air during the cooling season (Btu/lb)

= use the below table to determine the approximate outdoor air enthalpy associated with an indoor temperature setpoint and climate zone.

|  | hoc |  |  |
| --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 67 oF | 72 oF | 77 oF |
| 1 - Rockford AP / Rockford | 31.6 | 33.0 | 35.3 |
| 2 - Chicago O'Hare AP / Chicago | 32.0 | 33.6 | 35.4 |
| 3 - Springfield #2 / Springfield | 32.9 | 34.6 | 36.6 |
| 4 - Belleville SIU RSCH / Belleville | 33.5 | 35.0 | 36.4 |
| 5 - Carbondale Southern IL AP / Marion | 34.6 | 36.2 | 37.7 |

hic	= average enthalpy of indoor air, cooling season (Btu/lb)

= use the below table to determine the approximate indoor air enthalpy associated with an indoor temperature setpoint in indoor relative humidity.

|  | hic |  |  |
| --- | --- | --- | --- |
| Relative Humidity (%) | 67 oF | 72 oF | 77 oF |
| 60 | 25.5 | 28.5 | 31.8 |
| 50 | 23.9 | 26.6 | 29.5 |
| 40 | 22.3 | 24.7 | 27.3 |

= an estimate 26.6 Btu/lb associated with the 72 oF and 50% indoor relative humidity case can be used as an approximation if no other data is available. For other indoor temperature setpoints and RH, enthalpies may be interpolated.

The total airflow through the entryway, CFMtot, includes both infiltration due to wind as well as thermal forces, as follows:

CFMtot		= sqrt[ (CFMw)2 + (CFMt2) ]

Where:

CFMw	= Infiltration due to the wind (cfm)

CFMt	= Infiltration due to thermal forces (cfm)

The infiltration due to the wind is calculated as follows:

CFMw 	= (vwc * Cwc)* Cv * Ad * (88 fpm/mph)

Where:

vwc	= average wind speed during the cooling season based on entryway orientation (mph)

= use the below table to for the wind speed effects based on climate zone and entryway orientation:

|  | Entryway Orientation |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station /City | N | E | S | W |
| 1 - Rockford AP / Rockford | 4.2 | 4.1 | 4.7 | 4.8 |
| 2 - Chicago O'Hare AP / Chicago | 4.7 | 4.5 | 5.4 | 4.6 |
| 3 - Springfield #2 / Springfield | 4.1 | 3.7 | 6.0 | 5.0 |
| 4 - Belleville SIU RSCH / Belleville | 3.3 | 2.7 | 3.8 | 4.2 |
| 5 - Carbondale Southern IL AP / Marion | 3.1 | 2.9 | 4.4 | 3.8 |

Cwc	= wind speed correction factor due to wind direction in cooling season (%)

= because wind direction is not constant, a wind speed correction factor is used to adjust for the amount of time during the cooling season prevailing winds can be expected to impact the entryway. Use the following table to determine the correct wind speed correction factor for cooling applications.

|  | Entryway Orientation |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | N | E | S | W |
| 1 - Rockford AP / Rockford | 0.18 | 0.13 | 0.30 | 0.31 |
| 2 - Chicago O'Hare AP / Chicago | 0.18 | 0.17 | 0.36 | 0.26 |
| 3 - Springfield #2 / Springfield | 0.17 | 0.12 | 0.46 | 0.21 |
| 4 - Belleville SIU RSCH / Belleville | 0.21 | 0.15 | 0.35 | 0.16 |
| 5 - Carbondale Southern IL AP / Marion | 0.18 | 0.15 | 0.37 | 0.11 |

Note that correction factors do not add up to 1 (100%). This is attributed to periods of calm winds.

Cv	= effectiveness of openings,

= 0.3, assumes diagonal wind

Ad	= area of the doorway (ft2)

= user defined

The infiltration due to thermal forces is calculated as follows:

CFMt	= Ad * Cdc * (60 sec/min) * sqrt[2 * g * H/2 * (Toc - Tic) / (459.7 + Toc)]

Where:

Cdc	= the discharge coefficient during the cooling season

= 0.4 + 0.0025 * |Tic – Toc|

= 0.42, Illinois average at indoor air temp of 72oF

Note, values for Cdc show little variation due to balance point temperature, indoor air temperature, and climate zone. As such, if estimating results, the Illinois average value may be used as a simplification.

g	= acceleration due to gravity

= 32.2 ft/sec2

H	= the height of the entryway (ft)

= user input

Tic	= Average indoor air temperature during cooling season

= User input, can assume indoor cooling temperature set-point

Toc	= Average outdoor temp during cooling season (oF)

= the average outdoor temperature is dependent on the CD period and zone. As such, the following table may be used for average outdoor temperature during the cooling period:

|  | Toc |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Climate Zone Weather Station/City | 62 oF | 67 oF | 72 oF | 77 oF | 82 oF |
| 1 - Rockford AP / Rockford | 72.9 | 76.0 | 79.2 | 82.5 | 85.5 |
| 2 - Chicago O'Hare AP / Chicago | 72.9 | 76.0 | 79.4 | 82.8 | 85.5 |
| 3 - Springfield #2 / Springfield | 73.7 | 76.7 | 79.9 | 83.4 | 86.4 |
| 4 - Belleville SIU RSCH / Belleville | 74.9 | 77.7 | 81.0 | 84.3 | 86.9 |
| 5 - Carbondale Southern IL AP / Marion | 75.1 | 77.7 | 80.9 | 84.7 | 87.4 |

459.7	= conversion factor from oF to oR

= calculation requires absolute temperature for values not calculated as a difference of temperatures.

Heat Transfer Through Open Entryway with Air Curtain (Cooling Season)

Qtac		= Qtbc * (1 – E)

Where:

E	= the effectiveness of the air curtain (%)

= 0.60

###### Summer Coincident Peak Demand Savings

ΔkW 		= (ΔkWhcooling / (CD *24)) * CF

Where:

CFSSP 	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

###### Natural Gas Savings

Natural gas savings, therms, associated with reduced infiltration through an entryway during the heating season are calculated by determining the difference between heat loss through the entryway before and after the installation of the air curtain.

therms		= (Qbc - Qac) * topen * HD / η

Where:

Qbc	= rate of sensible heat transfer through the open entryway, before air curtain (therm/hr)

Qac	= rate of sensible heat transfer through the open entryway, after air curtain (therm/hr)

topen	= average hours per day the door is open (hr/day)

= Actual or estimated user input value

HD	= heating days per year, total days in year above balance point temperature (day)

= use table below to select an appropriate value:

|  | HD |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Climate Zone - Weather Station/City | 45 oF | 50 oF | 55 oF | 60 oF | 65 oF |
| 1 - Rockford AP / Rockford | 142 | 160 | 183 | 204 | 228 |
| 2 - Chicago O'Hare AP / Chicago | 150 | 166 | 192 | 219 | 253 |
| 3 - Springfield #2 / Springfield | 125 | 142 | 167 | 194 | 230 |
| 4 - Belleville SIU RSCH / Belleville | 101 | 115 | 134 | 156 | 180 |
| 5 - Carbondale Southern IL AP / Marion | 103 | 123 | 148 | 174 | 205 |

η	= efficiency of heating equipment

= Actual. If unknown, assume 0.8

Heat Transfer Through Open Entryway without Air Curtain (Heating Season)

Qbc		= (1.08 Btu/(hr*oF*cfm)) * CFMtot * (Tih – Toh) / (100,000 Btu/therm)

Where:

1.08	= sensible heat transfer coefficient (specific heat of air and unit conversions)

CFMtot	= Total air flow through entryway (cfm)

Tih	= Average indoor air temperature during heating season

= User input, can assume indoor heating temperature set-point

Toh	= Average outdoor temp during heating season (oF)

= use table below, based on binned data from TMY3 & balance point temperature:

|  | Avg Outdoor Air Temp - Heating Season |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 45 oF | 50 oF | 55 oF | 60 oF | 65 oF |
| 1 - Rockford AP / Rockford | 26.3 | 28.8 | 31.6 | 34.2 | 37.3 |
| 2 - Chicago O'Hare AP / Chicago | 29.4 | 31.2 | 34.0 | 36.8 | 40.3 |
| 3 - Springfield #2 / Springfield | 29.4 | 31.5 | 34.6 | 37.7 | 41.6 |
| 4 - Belleville SIU RSCH / Belleville | 31.7 | 33.6 | 36.2 | 39.2 | 42.3 |
| 5 - Carbondale Southern IL AP / Marion | 32.5 | 34.9 | 37.8 | 40.7 | 44.0 |

The total airflow through the entryway, CFMtot, includes both infiltration due to wind as well as thermal forces, as follows:

CFMtot		= sqrt[(CFMw)2 + (CFMt2)]

Where:

CFMw	= Infiltration due to the wind (cfm)

CFMt	= Infiltration due to thermal forces (cfm)

The infiltration due to the wind is calculated as follows:

CFMw 	= (vwh * Cwh)* Cv * Ad * (88 fpm/mph)

Where:

vwh	= average wind speed during the heating season (mph)

= similar to cooling season wind speed assumptions, use the following table to determined average wind speed based on entryway orientation:

|  | Entryway Orientation |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/ City | N | E | S | W |
| 1 - Rockford AP / Rockford | 5.0 | 4.6 | 4.9 | 5.6 |
| 2 - Chicago O'Hare AP / Chicago | 5.5 | 5.2 | 4.9 | 5.1 |
| 3 - Springfield #2 / Springfield | 5.0 | 4.9 | 5.3 | 5.1 |
| 4 - Belleville SIU RSCH / Belleville | 4.3 | 3.4 | 3.5 | 5.3 |
| 5 - Carbondale Southern IL AP / Marion | 4.6 | 3.2 | 4.2 | 4.4 |

Cwh	= wind speed correction factor due to wind direction in heating season, (%)

= because wind direction is not constant, a wind speed correction factor is used to adjust for the amount of time during the heating season prevailing winds can be expected to impact the entryway. Use the following table to determine the correct wind speed correction factor for the heating applications.

|  | Entryway Orientation |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/ City | N | E | S | W |
| 1 - Rockford AP / Rockford | 0.18 | 0.13 | 0.30 | 0.31 |
| 2 - Chicago O'Hare AP / Chicago | 0.21 | 0.10 | 0.26 | 0.39 |
| 3 - Springfield #2 / Springfield | 0.21 | 0.14 | 0.27 | 0.34 |
| 4 - Belleville SIU RSCH / Belleville | 0.31 | 0.15 | 0.22 | 0.29 |
| 5 - Carbondale Southern IL AP / Marion | 0.31 | 0.11 | 0.27 | 0.18 |

Note that correction factors do not add up to 1 (100%). This is attributed to periods of calm winds.

Cv	= effectiveness of openings,

= 0.3, assumes diagonal wind

Ad	= area of the doorway (ft2)

= user input

The infiltration due to thermal forces is calculated as follows:

CFMt	= Ad * Cdh * (60 sec/min) * sqrt[2 * g * H/2 * (Tih – Toh) / (459.7 + Tih)]

Where:

Cdh	= the discharge coefficient during the heating season

= 0.4 + 0.0025 * |Tih – Toh|

= 0.49, Illinois average at indoor air temp of 72oF

Note, values for Cdh show little variation due to balance point temperature, indoor air temperature, and climate zone. As such, if estimating results, the Illinois average value may be used as a simplification.

g	= acceleration due to gravity

= 32.2 ft/sec2

H	= the height of the entryway (ft)

= user defined

Heat Transfer Through Open Entryway without Air Curtain (Heating Season)

Qac		= Qbc * (1 – E)

Where:

E	= the effectiveness of the air curtain (%)

= 0.60

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

The air curtain would need to be regularly serviced and commissioned to ensure that it is appropriately operating. This is estimated at a cost of $150.

###### Measure Code: CI-HVC-AIRC-V04-220101

###### Review Deadline: 1/1/2024

### Destratification Fan

###### Description

This measure applies to buildings with high bay ceiling construction without fans currently installed for the purpose of destratifying air. There is also a separate measure for destratification fans as applied to agricultural settings (“High Volume Low Speed Fans”). All other destratification fan applications require custom analysis.

Air stratification leads to higher temperatures at the ceiling and lower temperatures at the ground. During the heating season, destratification fans improve air temperature distribution in a space by circulating warmer air from the ceiling back down to the floor level, thereby enhancing comfort and saving energy. Energy savings are realized by a reduction of heat loss through the roof-deck and walls as a result of a smaller temperature differential between indoor temperature and outdoor air.

Note that further, but limited, empirical evidence suggests that improved air mixing due to destratification would also result in shorter heating system runtimes due to warmer air reaching the thermostat level sooner, and possibly even allow a facility to lower the thermostat set point while maintaining a similar level of occupant comfort. This is supported by measured data in which an increase in temperatures was observed at the thermostat (5 foot level) level when air is destratified, resulting in an approximate temperature increase at the 5 foot level in the range of 1 - 3oF. This measure does not currently attempt to quantify the potential impacts of air mixing from destratification; however, it should be noted that additional therms savings may be possible.

This measure was developed to be applicable to the following program types: NC, RF. If applied to other program types, the measure savings should be verified.

Limitations

- For use in conditioned, high bay structures. Recommended minimum ceiling height of 20 ft.

- This measure should only be applied to spaces in which the ceiling is subject to heat loss to outdoor air (i.e., single story or top floor spaces) and where there is sufficient space to allow for appropriate spacing of the fans. Other applications require custom analysis.

- Installation must follow manufacturer recommendations sufficient to effectively destratify the entire space. Please see calculation of effective area, Aeff, in the therms savings algorithm as a check if this criteria is met. Otherwise, custom calculation is necessary.

- Measure does not currently support facilities with night setbacks on heating equipment. Custom analysis is needed in this case.

- Certain heating systems may not be a good fit for destratification fans, such as locations with: high velocity vertical throw unit heaters, radiant heaters, and centralized forced air systems. In these cases, measured evidence of stratification should be confirmed, and custom analysis may be necessary.

###### Definition of Efficient Equipment

High Volume, Low Speed (HVLS) fans with a minimum diameter of 14 ft with Variable Speed Drive (VSD) installed.

Note that bell-shaped fans are currently excluded from this measure due to limited validation of the technology available. Further verification of effectiveness compared to HVLS is needed. A manufacturer of bell-shaped fans indicates that four bell-shaped fans provide an equivalent effective area as a typical HVLS fan. However, there is a need for further review of bell-shaped fan field test data supporting manufacturer claims regarding comparable effectiveness to HVLS technologies.

###### Definition of Baseline Equipment

No destratification fans or other means to effectively mix indoor air.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

###### Deemed Measure Cost

The incremental measure cost = [equipment cost of HVLS fans] + [installation costs (including materials and labor)]

Since installation cost is dependent on a variety of factors, actual costs should be used if known. The default incremental measure cost for HVLS fans are as follows:

| Fan Diameter (ft) | Incremental Cost |
| --- | --- |
| 14 | $6,600 |
| 16 | $6,650 |
| 18 | $6,700 |
| 20 | $6,750 |
| 22 | $6,800 |
| 24 | $6,850 |

###### Loadshape

Loadshape C04: Commercial Electric Heating.

###### Coincidence Factor

There are no summer coincident peak demand savings for this measure due to no savings attributable to cooling during the summer peak period.

Algorithm

###### Calculation of Savings

The following formulas provide a methodology for estimating heating load savings associated with destratification fan use. This algorithm is based on the assumption that savings are directly related to the difference in heat loss through the envelope before and after destratification.

###### Electric Energy Savings

The algorithm for this measure was developed for natural gas heating applications, however, for electric heating applications, the same methodology presented in the Natural Gas Savings Section may be used with the standard conversion factor from therms to kWh of 29.31 kWh/therm and an equipment efficiency as follows:

| System Type | Cooling Capacity of Equipment | Age of Equipment | HSPF Estimate | η (Effective COP Estimate) (HSPF/3.413) |
| --- | --- | --- | --- | --- |
| Heat Pump | All | Before 2009 | 6.8 | 2.0 |
|  | < 65,000 Btu/h | 2009 - 2017 | 7.7 | 2.3 |
|  |  | 2017 on | 8.2 | 2.40 |
|  | ≥ 65,000 Btu/h and < 135,000 Btu/h | 2010 on | 11.3 | 3.3 |
|  | ≥ 135,000 Btu/h and < 240,000 Btu/h | 2010 on | 10.9 | 3.2 |
|  | ≥ 240,000 Btu/h and < 760,000 Btu/h | 2010 on | 10.9 | 3.2 |
| Resistance | N/A | N/A | N/A | 1 |

Regardless of how the building is heated, the energy consumption of the fans must be accounted for. If the building is electrically heated, fan energy shall be subtracted from the savings as calculated above. If the building is heated with natural gas, this shall represent an electric penalty, i.e., an increase in consumption. This is calculated as follows:

∆kWh 		= - (Wfan * Nfan) * teff

Wfan	= fan input power (kW)

Nfan	= number of fans

teff 	= effective annual operation time, based on balance point temperature (hr)

= see table below in Natural Gas Savings section for further detail

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

∆Therms 	= [(∆Qr + ∆Qw) * teff] / (100,000 * η)

Where:

Qr 	= the heat loss reduction through the roof due to the destratification fan (Btu/hr)

= See calculation section below

Qw 	= the heat loss reduction through the exterior walls due to destratification fan (Btu/hr)

= See calculation section below

teff	= effective annual operation time, based on balance point temperature (hr)

= use table below to select an appropriate value:

| Climate Zone -Weather Station/City | teff |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 45 oF | 50 oF | 55 oF | 60 oF | 65 oF |
| 1 - Rockford AP / Rockford | 3810 | 4226 | 4880 | 5571 | 6436 |
| 2 - Chicago O'Hare AP / Chicago | 3593 | 3986 | 4603 | 5254 | 6070 |
| 3 - Springfield #2 / Springfield | 3038 | 3370 | 3891 | 4442 | 5131 |
| 4 - Belleville SIU RSCH / Belleville | 2243 | 2488 | 2873 | 3280 | 3789 |
| 5 - Carbondale Southern IL AP / Marion | 2271 | 2519 | 2909 | 3320 | 3836 |

100,000	= conversion factor (1 therm = 100,000 Btu)

η	= thermal efficiency of heating equipment

For example, for a warehouse facility located in Rockford, IL, installing destratification fans could reduce heat loss through the roof of 95,000 Btu/hr and a reduced heat loss through the wall of 51,228 Btu/hr. Assuming a balance point of 55oF the therms savings for the facility would be estimated as:

∆Therms 		= [(∆Qr + ∆Qw) * teff] / (100,000 * η)

= [(95,000 Btu/hr + 51,282 Btu/hr) * 4880 hr] / [(100,000 Btu/therm) * 0.8)]

=  8,923 therms

= Actual. If unknown, assume 0.8.

Heat loss reduction through the roof

∆Qr	= Qr,s – Qr,d

= (1/Rr) * Ar * [(Tr,s – Toa) – (Tr,d – Toa)]

= (1/Rr) * Ar * (Tr,s – Tr,d)

Where:

Qr,s	=  roof heat loss for stratified space

Qr,d	= roof heat loss for destratified space

Rr	= overall thermal resistance through the roof (hr * ft2 * oF / Btu)

= Actual or estimated based on construction type. If unknown, assume the following:

| Thermal Resistance Factor (R-Factor) for Roof | Retrofit | New Construction |
| --- | --- | --- |
| Rr | 15.0 (hr * ft2 * oF / Btu) | 30.0 (hr * ft2 * oF / Btu) |

Ar	= roof area (ft2)

= user input

= can be approximated with floor area

Toa	= outside air temperature, note: therm savings calculations are actually independent of outside air because this term drops out of the heat loss reduction equation

Tr,s	= indoor temperature at roof deck, stratified case (oF)

= Actual. If unknown, use the following equation

= ms * hr + Tf,s

hr	= ceiling height/roof deck (ft)

ms	= estimated heat gain per foot elevation, stratified case (oF/ft)

= 0.8 oF/ft

= Professional judgement used to define value based on result from a Nicor Gas ETP Pilot field testing results and the Ansley article below., Estimates from these sources fall on the conservative side of the industry rule of thumb range of 1-2 oF/ft heat gain.

Tf,s	= estimated floor temperature, stratified case (oF)

= Ttstat – ms * htstat

= Ttstat – 4 oF

Ttstat 	= temperature set point at the thermostat

htstat	= vertical distance between the floor and the thermostat, assumed 5ft

Tr,d	= indoor temp at roof, destratified case

= actual value, or may be estimated using the following:,

For example, for a 50,000 ft2 warehouse built in 1997 with 30 ft ceilings and a thermostat set point of 65 oF. No further measured values available.

∆Qr 	= (1/Rr) * Ar * (Tr,s – Tr,d) = (1/Rr) * Ar * [(ms * hr + Ttstat – 4 oF) – (Ttstat + 1 oF)]

= (1/Rr) * Ar * [(0.8oF/ft * hr) – 5 oF]

= 1/(10 hr * ft2 * oF / Btu) * (50,000 ft2) * [(0.8oF/ft * 30 ft) – 5 oF]

=  95,000 Btu/hr

= Ttstat + 1 oF

Heat loss reduction through exterior walls

Note: a conservative estimate for therms savings would neglect the impact of heat loss through the walls. However, Ansley suggests that estimates based on the roof deck losses alone underestimate actual savings by up to 46%.

∆Q_w	= Qw,s – Qw,d

= (1/Rw) * Aw * (Tw,s – Tw,d)

Where:

Rw	= overall thermal resistance through the exterior walls (hr * ft2* oF / Btu)

= Actual or estimated based on construction type. If unknown, assume the following:

| Thermal Resistance Factor (R-Factor) for Wall | Retrofit | New Construction (2010 or newer) |
| --- | --- | --- |
| Rw | 6.5 (hr * ft2 * oF / Btu) | 13.0 (hr * ft2 * oF / Btu) |

Aw	= area of exterior walls (ft2)

= user input

Tw,s	= average indoor air temperature for wall heat loss, stratified case

= If actual Tr,s measurement is available

= [(Tr,s * ha) + (Ttstat * hb)] / hr

ha	= vertical distance between the heat source and the ceiling

hb	= vertical distance between the floor and the heat source

= Otherwise, use the linear stratification equation at average space height, see definition above.

= ms * (hr / 2) + Tf,s

= ms* (hr / 2) + (Ttstat – 4)

Tw,d	= average indoor air temperature for wall heat loss, destratified case

= Ttstat + 0.5

For example, for a 50,000 ft2 warehouse built in 1997 with 1200 ft length of perimeter wall and 30 ft ceilings and a thermostat set point of 65 oF and a measured temperature at the ceiling of 85 oF and unit heaters located 10 feet from the roof:

∆Qw 	= (1/Rw) * Aw * (Tw,s – Tw,d)

= (1/Rw) * Aw * [([(Tr,s * ha) + (Ttstat * hb)] / hr) – (Ttstat + 0.5 oF)]

= 1/(6.5 hr*ft2*oF/Btu) * (1200 * 30) * [([(85oF * 10ft) + (65 oF * 20ft)] / 30ft) – (65 + 0.5 oF)]

= 1/(6.5 hr*ft2*oF/Btu) * (36,000ft2) * (71.7 oF – 65.5 oF)

= 34,338 Btu/hr

= conservative estimate using engineering judgment based on the same assumption used for Tr,f estimate.

Measure eligibility check

Use the following algorithm to verify a fan system is sufficiently sized to destratify air across the entire area.

Effective area, Aeff, is the area over which a fan or a group of fans can be expected to effectively destratify a space. If Aeff is less than the roof area, Ar, a custom analysis approach should be followed to account for the change in the effectiveness of the system. In lieu of more detailed studies, effective area is defined based on the measured results from an Enbridge Gas field study in which the area a fan was expected to effectively destratify was equal to 5 times the fan diameter. Effective area, is calculated as follows:

Aeff	= [π * (5*Dfan)2) / 4] * Nfan

= 6.25 * π * Dfan2 * Nfan

Where:

Aeff	= the effective area fan area on the floor (ft2)

Dfan	= fan diameter

Nfan 	= the number of fans

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-DSFN-V05-210101

###### Review Deadline: 1/1/2024

### Economizer Repair and Optimization

###### Description

Economizers are designed to use unconditioned outside air (OSA) instead of mechanical cooling to provide cooling when exterior conditions permit.  When the OSA temperature is less than the changeover temperature (determined by a static setpoint or a reference return air sensor) up to 100% OSA is supplied to help meet the facility’s cooling needs, thus reducing mechanical cooling energy and saving energy.  An economizer that is not working or is not properly adjusted can waste energy and cause comfort issues.  This HVAC Economizer Optimization measure involves the repair and optimization of common economizer problems such as adjusting changeover setpoint, repairing damper motors & linkages and replacing non-working sensors and/or controllers.  These repairs and adjustments result in proper operation which maximizes both occupant comfort and energy savings.

This measure is only appropriate for single zone packaged rooftop units. Custom calculations are required for savings for multi-zone systems.

In general the HVAC Economizer Optimization measure may involve both repair and/or optimization, as below.

Economizer Repair – The Economizer repair work is preformed to ensure that the existing economizer is working properly.  This allows the system to take advantage of free cooling and ensure that the system is not supplying an excess amount of outside air (OSA) during non-economizing periods.

- Replace Damper Motor – If the existing damper motor is not operational, the unit will be replaced with a functioning motor to allow proper damper modulation.

- Repair Damper linkage – If the existing linkage is broken or not adjusted properly, the unit will be replaced or adjusted to allow proper damper modulation.

- Repair Economizer Wiring – If the existing economizer is not operational due to a wiring issue, the issue will be repaired to allow proper economizer operation.

- Reduce Over Ventilation – If the unit is supplying excess OSA, the OSA damper position will be adjusted to meet minimum ventilation requirements.

- Economizer Sensor Replacement – If the unit is equipped with a nonadjustable dry bulb (i.e. snapdisk) or malfunctioning analog sensor, the sensor is replaced with a new selectable sensor.

- Economizer Control Replacement – If the existing economizer controller is not operational, the unit will be replaced or upgraded to allow for proper economizer operation.

Economizer Optimization- The economizer optimization work is preformed to ensure that the existing economizer system is set up properly to maximize use of free cooling for units located in a particular climate zone.

- Economizer Changeover Setpoint Adjustment – If the unit is equipped with a fully operational economizer, the controller is adjusted to the appropriate changeover setpoint based on ASHRAE 90.1 (Figure 1 - Table 6.5.1.1.3 High-Limit Shutoff Control Settings for Air Economizers) for the corresponding climate zone.

- Enable Integrated Operation – If the unit is equipped with a fully operational economizer and is not set up to allow a minimum of two stages of cooling (1st stage – Economizer Only & 2nd Stage – Economizer & Mechanical cooling), the unit will be wired to allow two stage cooling

This measure was developed to be applicable to the following program types:  RF, DI.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment condition is defined by fully functional economizer that is programmed to meet ASHRAE 90.1 economizer changeover setpoint requirements for the facility’s climate zone and changeover control type (Figure 1 - Table 6.5.1.1.3 High-Limit Shutoff Control Settings for Air Economizers).

Figure 1 – Baseline ASHRAE High-Limit Shutoff Control Settings

Figure 2 – ASHRAE Climate Zone Map

###### Definition of Baseline Equipment

The baseline for this measure is an existing economizer installed on a packaged single zone rooftop HVAC unit. The existing economizer system is currently not operating as designed due to mechanical and/or control problems, and/or is not optimally adjusted.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 5 years.

###### Deemed Measure Cost

The cost for this measure can vary considerably depending upon the existing condition of the economizer and the work required to achieve the required efficiency levels. Measure cost should be determined on a site-specific basis.

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

The savings calculation methodology uses a regression equation to calculate the energy savings for a variety of common situations. The equation variables are limited to the ranges listed; if the actual conditions fall outside of these ranges custom calculations are required.

###### Electric Energy Savings

∆kWh	= [Baseline Energy Use (kWh/Ton) – Proposed Energy Use (kWh/Ton)] * Cooling Capacity (Tons)

The following equations are used to calculate baseline and proposed electric energy use.

Electric Energy Use Equations (kWh / ton)

| Building Type | Changeover Type | Equation |
| --- | --- | --- |
| Assembly | Fixed Dry-Bulb (DB) | cz+CSP*-2.021+EL*-16.362+OAn*1.665+OAx*-3.13 |
|  | Dual Temperature Dry-Bulb (DTDB) | cz+EL*-11.5+OAn*1.635+OAx*-2.817 |
|  | Dual Temperature Enthalpy (DTEnth) | cz+EL*-17.772+OAn*1.853+OAx*-3.044 |
|  | Fixed Enthalpy (Enth) | cz+CSP*-5.228+EL*-17.475+OAn*1.765+OAx*-3.003 |
|  | Analog ABCD Economizers (ABCD) | cz+CSP*-2.234+EL*-16.394+OAn*1.744+OAx*-3.01 |
| Convenience Store | DB | cz+CSP*-3.982+EL*-27.508+OAn*2.486+OAx*-4.684 |
|  | DTDB | cz+EL*-20.798+OAn*2.365+OAx*-3.773 |
|  | DTEnth | cz+EL*-30.655+OAn*2.938+OAx*-4.461 |
|  | Enth | cz+CSP*-8.648+EL*-25.678+OAn*2.092+OAx*-3.754 |
|  | ABCD | cz+CSP*-3.64+EL*-24.927+OAn*2.09+OAx*-3.788 |
| Office - Low Rise | DB | cz+CSP*-0.967+EL*-6.327+OAn*2.87+OAx*-1.047 |
|  | DTDB | cz+OAn*2.968+OAx*-0.943 |
|  | DTEnth | cz+EL*-9.799+OAn*3.106+OAx*-1.085 |
|  | Enth | cz+CSP*-2.773+EL*-7.392+OAn*2.941+OAx*-0.974 |
|  | ABCD | cz+CSP*-1.234+EL*-7.229+OAn*2.936+OAx*-0.995 |
| Religious Facility | DB | cz+CSP*-1.131+OAn*3.542+OAx*-1.01 |
|  | DTDB | cz+EL*-10.198+OAn*4.056+OAx*-1.279 |
|  | DTEnth | cz+OAn*3.775+OAx*-1.031 |
|  | Enth | cz+CSP*-2.13+OAn*3.317+OAx*-0.629 |
|  | ABCD | cz+CSP*-0.95+OAn*3.313+OAx*-0.647 |
| Restaurant | DB | cz+CSP*-2.243+EL*-21.523+OAx*-1.909 |
|  | DTDB | cz+EL*-14.427+OAn*0.295+OAx*-1.451 |
|  | DTEnth | cz+EL*-25.99+OAn*0.852+OAx*-1.951 |
|  | Enth | cz+CSP*-4.962+EL*-16.868+OAn*-0.12+OAx*-1.418 |
|  | ABCD | cz+CSP*-2.115+EL*-16.15+OAn*-0.125+OAx*-1.432 |
| Retail - Department Store | DB | cz+CSP*-1.003+OAn*3.765+OAx*-0.938 |
|  | DTDB | cz+OAn*3.688+OAx*-0.676 |
|  | DTEnth | cz+OAn*4.081+OAx*-1.072 |
|  | Enth | cz+CSP*-2.545+OAn*3.725+OAx*-0.788 |
|  | ABCD | cz+CSP*-1.175+OAn*3.708+OAx*-0.809 |
| Retail - Strip Mall | DB | cz+CSP*-1.192+EL*-5.62+OAn*3.353+OAx*-1.142 |
|  | DTDB | cz+OAn*3.355+OAx*-0.915 |
|  | DTEnth | cz+EL*-9.202+OAn*3.642+OAx*-1.215 |
|  | Enth | cz+CSP*-2.997+EL*-5.938+OAn*3.312+OAx*-0.964 |
|  | ABCD | cz+CSP*-1.36+EL*-5.884+OAn*3.3+OAx*-0.987 |

Where:

CZ	= Climate Zone Coefficient

= Depends on Building Type and Changover Type (see table below)

|  |  | Electric Climate Zone Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Building Type | Changeover Type | CZ1 (Rockford) | CZ2 (Chicago) | CZ3 (Springfield) | CZ4 (Belleville) | CZ5 (Marion) |
| Assembly | DB | 874.07 | 886.73 | 1043.38 | 1071.48 | 1072.20 |
|  | DTDB | 698.45 | 711.89 | 870.13 | 899.51 | 903.10 |
|  | DTEnth | 702.06 | 715.42 | 873.43 | 902.76 | 906.50 |
|  | Enth | 851.95 | 865.43 | 1020.65 | 1047.10 | 1053.32 |
|  | ABCD | 884.19 | 897.63 | 1053.12 | 1080.58 | 1086.35 |
| Convenience Store | DB | 1739.12 | 1787.09 | 2128.78 | 2206.65 | 2245.93 |
|  | DTDB | 1389.28 | 1436.30 | 1780.99 | 1863.45 | 1904.89 |
|  | DTEnth | 1398.42 | 1446.82 | 1789.71 | 1869.89 | 1912.59 |
|  | Enth | 1643.51 | 1691.34 | 2032.83 | 2112.21 | 2157.63 |
|  | ABCD | 1692.80 | 1740.62 | 2082.35 | 2162.73 | 2207.68 |
| Office - Low Rise | DB | 674.06 | 687.17 | 899.17 | 993.84 | 989.16 |
|  | DTDB | 583.62 | 597.02 | 811.39 | 907.61 | 903.58 |
|  | DTEnth | 588.94 | 602.11 | 816.02 | 912.49 | 908.26 |
|  | Enth | 668.83 | 682.23 | 893.61 | 987.52 | 986.59 |
|  | ABCD | 690.27 | 703.52 | 915.27 | 1009.94 | 1008.59 |
| Religious Facility | DB | 613.26 | 630.50 | 853.53 | 923.99 | 931.74 |
|  | DTDB | 518.40 | 535.45 | 760.76 | 832.57 | 840.72 |
|  | DTEnth | 513.59 | 531.20 | 756.26 | 829.13 | 837.26 |
|  | Enth | 576.94 | 594.17 | 817.64 | 888.37 | 897.18 |
|  | ABCD | 593.78 | 611.04 | 834.69 | 905.83 | 914.27 |
| Restaurant | DB | 1397.27 | 1430.45 | 1763.21 | 1837.63 | 1872.18 |
|  | DTDB | 1191.82 | 1225.12 | 1558.32 | 1633.95 | 1669.13 |
|  | DTEnth | 1192.84 | 1226.77 | 1559.41 | 1635.13 | 1671.11 |
|  | Enth | 1343.56 | 1377.52 | 1710.11 | 1783.66 | 1821.67 |
|  | ABCD | 1373.72 | 1407.70 | 1740.43 | 1814.74 | 1852.55 |
| Retail - Department Store | DB | 717.89 | 730.07 | 968.85 | 1034.78 | 1035.06 |
|  | DTDB | 628.83 | 641.70 | 883.37 | 951.09 | 951.33 |
|  | DTEnth | 629.35 | 641.90 | 882.84 | 951.33 | 951.44 |
|  | Enth | 705.06 | 717.99 | 956.42 | 1020.57 | 1024.45 |
|  | ABCD | 728.60 | 741.47 | 980.19 | 1045.30 | 1048.57 |
| Retail - Strip Mall | DB | 800.69 | 818.68 | 1070.39 | 1129.87 | 1133.84 |
|  | DTDB | 692.97 | 711.31 | 965.63 | 1026.68 | 1030.41 |
|  | DTEnth | 698.12 | 716.34 | 970.06 | 1031.78 | 1035.72 |
|  | Enth | 784.54 | 803.35 | 1054.37 | 1112.72 | 1120.74 |
|  | ABCD | 810.10 | 828.86 | 1080.11 | 1139.39 | 1146.95 |

CSP	= Economizer Changeover Setpoint (°F or Btu/lb) (actual in ranges below)

| Economizer Control Type |  | Economizer Changeover Setpoint |
| --- | --- | --- |
| Dry-Bulb |  | 60°F - 80°F |
| Dual Temperature Dry-Bulb |  | 0°F -5°F delta |
| Dual Temperature Enthalpy |  | 0 Btu/lb -5 Btu/lb delta |
| Enthalpy |  | 18 Btu/lb – 28 Btu/lb |
| Analog ABCD Economizers | A | 73°F |
|  | B | 70°F |
|  | C | 67°F |
|  | D | 63°F |
|  | E | 55°F |

EL	= Integrated Economizer Operation (Economizer Lockout)

= 1 for Economizer w/ Integrated Operation (Two Stage Cooling)

= 0 for Economizer w/ out Integrated Operation (One Stage Cooling)

Oan	= Minimum Outside Air (%OSA * 100)

= Actual. %OSA must be between 15% -70%. If unknown, assume:

Functional Economizer – 30%

Non functional Economizer (Damper failed closed) – 15%

Non functional Economizer (Damper failed open) – 30% (Assume Minimum Ventilation (Three Fingers))

Note: the actual integer Oan value (e.g. 30) should be used in the regression algorithm, not the percentage (e.g. 0.3).

Oax	= Maximum Outside Air (%)

= Actual. Must be between 15% -70%. If unknown, assume:

Functional Economizer – 70%

Non functional Economizer (Damper failed closed) – 15%

Non functional Economizer (Damper failed open) – 30% (Assume Minimum Ventilation (Three Fingers))

For example, a low rise office building in Rockford (Climate Zone 1) is heated and cooled with a packaged Gas (92 kBtu output) / DX (5 Ton) RTU.  The RTU is equipped with a fixed dry-bulb outside air economizer and is programed for integrated operation.  When the technician inspects the RTU they find that the changeover setpoint is programmed to 62°F, which does not meet ASHRAE economizer high limit shut off air economizer recommendations.  After further investigation it is found that the OSA damper motor is not operational and is providing 30% outside air.

The technician replaces the damper motor and allow for proper OSA damper modulation (30% Min OSA & 70% Max OSA).  They also adjust the fixed dry-bulb changeover setpoint to meet the ASHRAE economizer high limit shut off air economizer recommendation of 70°F.

∆kWh	= [Baseline Energy Use (kWh/Ton) – Proposed Energy Use (kWh/Ton)] * Cooling Capacity (Tons)

Baseline Energy Use (kWh/Ton) = Equation for Office Low Rise

= cz+CSP*-0.967+EL*-6.327+OAn*2.87+OAx*-1.047

= 674.06+62*-0.967+0*-6.327+30*2.87+30*-1.047

= 668.8  kWh/Ton

Proposed Energy Use (kWh/Ton) = Equation for Office Low Rise

= cz+CSP*-0.967+EL*-6.327+OAn*2.87+OAx*-1.047

= 674.06+70*-0.967+0*-6.327+ 30*2.87+70*-1.047

= 619.2 kWh/Ton

∆kWh	= [668.8 (kWh/Ton) – 619.2 (kWh/Ton)] * 5 Tons

= 49.6 kWh/Ton * 5 Tons

= 248.08 kWh

###### Summer Coincident Peak Demand Savings

N/A - It is assumed that repair or optimization of the economizer will not typically have a significant impact summer peak demand.

###### Natural Gas Savings

∆Therms = [Baseline Energy Use (Therms/kBtuh) – Proposed Energy Use (Therms/kBtuh)] * Output Heating Capacity (kBtuh)

The following equations are used to calculate baseline and proposed electric energy use.

Natural Gas Energy Use Equations (therms / kbtu output)

| Building Type | Changeover Type | Equation |
| --- | --- | --- |
| Assembly | Fixed Dry-Bulb (DB) | cz+OAn*0.0853 |
|  | Dual Temperature Dry-Bulb (DTDB) | cz+OAn*0.0866 |
|  | Dual Temperature Enthalpy (DTEnth) | cz+OAn*0.0866 |
|  | Fixed Enthalpy (Enth) | cz+OAn*0.0855 |
|  | Analog ABCD Economizers (ABCD) | cz+OAn*0.0855 |
| Convenience Store | DB | cz+OAn*0.26 |
|  | DTDB | cz+OAn*0.263 |
|  | DTEnth | cz+OAn*0.263 |
|  | Enth | cz+OAn*0.261 |
|  | ABCD | cz+OAn*0.261 |
| Office - Low Rise | DB | cz+OAn*0.3 |
|  | DTDB | cz+OAn*0.301 |
|  | DTEnth | cz+OAn*0.301 |
|  | Enth | cz+OAn*0.3 |
|  | ABCD | cz+OAn*0.3 |
| Religious Facility | DB | cz+OAn*0.35 |
|  | DTDB | cz+OAn*0.348 |
|  | DTEnth | cz+OAn*0.348 |
|  | Enth | cz+OAn*0.349 |
|  | ABCD | cz+OAn*0.349 |
| Restaurant | DB | cz+OAn*0.0867 |
|  | DTDB | cz+OAx*-0.038+OAn*OAx*0.00149 |
|  | DTEnth | cz+OAx*-0.038+OAn*OAx*0.00149 |
|  | Enth | cz+OAn*0.0878 |
|  | ABCD | cz+OAn*0.0878 |
| Retail - Department Store | DB | cz+OAn*0.319 |
|  | DTDB | cz+OAn*0.318 |
|  | DTEnth | cz+OAn*0.318 |
|  | Enth | cz+OAn*0.318 |
|  | ABCD | cz+OAn*0.318 |
| Retail - Strip Mall | DB | cz+OAn*0.215 |
|  | DTDB | cz+OAn*0.216 |
|  | DTEnth | cz+OAn*0.216 |
|  | Enth | cz+OAn*0.215 |
|  | ABCD | cz+OAn*0.215 |

Where:

CZ	= Climate Zone Coefficient

= Depends on Building Type and Changover Type (see table below)

|  |  | Natural Gas Climate Zone Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Building Type | Changeover Type | CZ1 (Rockford) | CZ2 (Chicago) | CZ3 (Springfield) | CZ4 (Belleville) | CZ5 (Marion) |
| Assembly | DB | -0.03 | -0.55 | -1.06 | -1.28 | -1.71 |
|  | DTDB | -0.02 | -0.57 | -1.11 | -1.34 | -1.79 |
|  | DTEnth | -0.02 | -0.57 | -1.11 | -1.34 | -1.79 |
|  | Enth | -0.03 | -0.55 | -1.06 | -1.29 | -1.72 |
|  | ABCD | -0.03 | -0.55 | -1.06 | -1.29 | -1.72 |
| Convenience Store | DB | 2.95 | 0.50 | -1.48 | -2.96 | -5.56 |
|  | DTDB | 3.06 | 0.52 | -1.56 | -3.11 | -5.81 |
|  | DTEnth | 3.06 | 0.52 | -1.56 | -3.11 | -5.81 |
|  | Enth | 2.96 | 0.50 | -1.49 | -2.98 | -5.59 |
|  | ABCD | 2.96 | 0.50 | -1.49 | -2.98 | -5.59 |
| Office - Low Rise | DB | 5.83 | 3.02 | 0.46 | -0.92 | -4.13 |
|  | DTDB | 5.98 | 3.08 | 0.41 | -1.03 | -4.36 |
|  | DTEnth | 5.98 | 3.08 | 0.41 | -1.03 | -4.36 |
|  | Enth | 5.85 | 3.03 | 0.46 | -0.93 | -4.16 |
|  | ABCD | 5.85 | 3.03 | 0.46 | -0.93 | -4.16 |
| Religious Facility | DB | 9.23 | 6.71 | 3.75 | 2.40 | -0.80 |
|  | DTDB | 9.41 | 6.83 | 3.77 | 2.39 | -0.86 |
|  | DTEnth | 9.41 | 6.83 | 3.77 | 2.39 | -0.86 |
|  | Enth | 9.25 | 6.73 | 3.75 | 2.40 | -0.80 |
|  | ABCD | 9.25 | 6.73 | 3.75 | 2.40 | -0.80 |
| Restaurant | DB | 8.30 | 6.54 | 4.94 | 4.00 | 1.95 |
|  | DTDB | 10.51 | 8.71 | 7.07 | 6.10 | 4.00 |
|  | DTEnth | 10.51 | 8.71 | 7.07 | 6.10 | 4.00 |
|  | Enth | 8.28 | 6.51 | 4.91 | 3.96 | 1.90 |
|  | ABCD | 8.28 | 6.51 | 4.91 | 3.96 | 1.90 |
| Retail - Department Store | DB | 8.20 | 5.86 | 3.19 | 1.25 | -2.59 |
|  | DTDB | 8.35 | 5.94 | 3.18 | 1.18 | -2.75 |
|  | DTEnth | 8.35 | 5.94 | 3.18 | 1.18 | -2.75 |
|  | Enth | 8.21 | 5.87 | 3.18 | 1.24 | -2.61 |
|  | ABCD | 8.21 | 5.87 | 3.18 | 1.24 | -2.61 |
| Retail - Strip Mall | DB | 6.40 | 4.35 | 2.07 | 0.49 | -2.18 |
|  | DTDB | 6.51 | 4.38 | 2.03 | 0.39 | -2.34 |
|  | DTEnth | 6.51 | 4.38 | 2.03 | 0.39 | -2.34 |
|  | Enth | 6.41 | 4.35 | 2.06 | 0.48 | -2.20 |
|  | ABCD | 6.41 | 4.35 | 2.06 | 0.48 | -2.20 |

For example, a low rise office building in Rockford (Climate Zone 1) is heated and cooled with a packaged Gas (92 kBtu output) / DX (5 Ton) RTU.  The RTU is equipped with a fixed dry-bulb outside air economizer and is programed for integrated operation.  When the technician inspects the RTU they find that the changeover setpoint is programmed to 62°F, which does not meet ASHRAE economizer high limit shut off air economizer recommendations.  After further investigation it is found the OSA damper motor is not operational and is providing 30% outside air.

The technician replaces the damper motor and allow for proper OSA damper modulation (30% Min OSA & 70% Max OSA).  They also adjust the fixed dry-bulb changeover setpoint to meet the ASHRAE economizer high limit shut off air economizer recommendation of 70°F.

∆Therms = [Baseline Energy Use (Therms/kBtuh) – Proposed Energy Use(Therms/kBtuh)] * Output Heating Capacity (kBtuh)

Baseline Energy Use (Therms/kBtuh) = Equation for Office Low Rise

= cz+OAn*0.3

= 5.83+30*.3

=14.8 Therms/kBtuh output

Proposed Energy Use (Therms/kBtuh) = Equation for Office Low Rise

= cz+OAn*0.3

= 5.83+30*.3

=14.8 Therms/kBtuh output

∆Therms = [14.8(Therms/kBtuh output) – 14.8 (Therms/kBtuh output)] * 92kBtuh output

= 0.0 (Therms/kBtuh output) * 92kBtuh output

= 0 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-ECRP-V04-220101

###### Review Deadline: 1/1/2023

### Multi-Family Space Heating Steam Boiler Averaging Controls

###### Description

This measure covers multi-family space heating boiler averaging controls. Temperature sensors are placed in interior spaces to monitor the average temperature of the building. At minimum a sensor must be placed at each corner and at one central location. Additionally, a temperature sensor must monitor the outside air temperature. These sensors shall provide data to the averaging controls. The averaging controls will adjust the boiler operation based upon an average of the indoor sensors and the outside air temperature. These controls shall also incorporate a night-time setback capability. Buildings utilizing thermostatic radiator valves, or other modulating control valves or sequences to control the temperature in individual spaces are not eligible.

This measure was developed to be applicable to the following program types:  RF.

###### Definition of Efficient Equipment

To qualify the boiler(s) must incorporate an averaging control system utilizing at least 4 indoor sensors and 1 outdoor sensor. The controls shall have the capability to incorporate a nighttime setback throughout the building.

###### Definition of Baseline Equipment

The baseline is a boiler system without averaging controls or other steam supply modulating controls. Current boiler control system can utilize a single thermostat or aquastat and timer.

###### Deemed Lifetime of Efficient Equipment

The measure life for the domestic hot water boilers is 20 years.

###### Deemed Measure Cost

As a retrofit measure, the actual installed cost should be used for screening purposes. A deemed retrofit measure cost of $5,060 can be used if the actual installed cost is unknown.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

ΔTherms =  Capacity * EFLH * SF / 100,000

Where:

Capacity		= Boiler gas input size (Btu/h)

= Actual

EFLH	= Effective Full Load Hours for heating in Existing Buildings are provided in section 4.4. HVAC End Use

SF 		= Savings Factor

= 10.2%, or custom if savings can be substantiated

For example, a 1,000,000 btu/h steam boiler in a Mid-Rise Multi-Family building in Chicago has averaging controls installed.

ΔTherms   	 = 1,000,000 * 1,685 * 0.102 / 100,000

= 1,719 therms

100,000 		= converts Btu/h to therm

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-SBAC-V02-190101

###### Review Deadline: 1/1/2023

### Unitary HVAC Condensing Furnace

###### Description

Condensing furnaces recover energy in combustion exhaust flue gasses that would otherwise simply be vented to the atmosphere, making them more efficient than non-condensing furnaces. This measure applies to a constant volume (CV), dedicated outside air system (DOAS), make-up air system (MUAS), or any unitary HVAC system that is utilizing an indirect gas fired process to heat 100% OA to provide ventilation or make-up air to commercial and industrial (C&I) building spaces. The unitary package must contain an indirect gas-fired, warm air furnace section, but the unitary package can be with or without an electric air conditioning section. The unitary package can be either a single package or split system that is applied indoors (non-weatherized) or outdoors (weatherized).

This measure excludes demand control ventilation, condensing unit heaters, and high efficiency (condensing) furnaces with annual fuel utilization efficiency (AFUE) ratings (for furnaces with less than 225,000 Btu/hr input capacity), which are covered by other measures for the C&I sector in the Technical Reference Manual (TRM).

This measure was developed to be applicable to the following program types: TOS, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure, the efficient unitary equipment must contain a condensing, warm air furnace with a natural gas thermal efficiency (TE) rating of 90% or higher, or alternatively, the unitary package must have equipment nameplate information for natural gas that identifies a heating output and heating input rating that has an output over input ratio of 0.90 or higher. These ratings must be certified by a recognized testing laboratory in accordance with American National Standards Institute (ANSI) Standard Z21.47 for Gas-Fired Central Furnaces. The furnace must be vented and condensate disposed of in accordance with the equipment manufacturer installation instructions and applicable codes.

###### Definition of Baseline Equipment

The baseline equipment is expected to be unitary equipment that contains a non-condensing, warm air furnace with a natural gas thermal efficiency (TE) rating of 80%, or alternatively, the unitary package will have equipment nameplate information for natural gas that identifies a heating output and heating input rating that has an output over input ratio of 0.80. These ratings must be certified by a recognized testing laboratory in accordance with American National Standards Institute (ANSI) Standard Z21.47 for Gas-Fired Central Furnaces.

Note the current Department of Energy (DOE) federal minimum efficiency standard is 80% for 225,000 Btu/hr and higher input capacity furnaces per the Energy Conservation Standard for Commercial Warm Air Furnaces. In the American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE) Standard 90.1 Energy Standard for Buildings Except Low-Rise Residential Buildings that minimum TE requirement is extended below 225,000 Btu/hr input capacity to require all commercial warm air furnaces and combination warm air furnace/air conditioning units to meet the minimum 80% TE.

Note: new Federal Standards applicable to all gas furnaces become effective January 1, 2023.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years, which is consistent with the established TRM measure life for single-package and split system unitary air conditioners, since in colder climates these unitary packages typically contain a gas-fired, warm air furnace section, with an electric air conditioning section.

###### Deemed Measure Cost

The actual incremental equipment and installation costs should be used, if available. If not, the incremental cost of $5.42 per 1000 Btu/hr of output capacity should be used for the condensing furnace equipment (as part of a unitary package) and its installation (including the combustion condensate drainage and disposal system). This incremental cost is from the DOE Technical Support Document for the Notice of Proposed Rulemaking (NOPR) for the Commercial Warm Air Furnace Standard. Per the DOE documentation, it is based on their representative 250,000 Btu/hr input capacity furnace at a 92% TE.

###### Loadshape

Loadshape C23 - Commercial Ventilation

###### Coincidence Factor

The coincidence factor is assumed to be 1.0 – that is, building ventilation will always be provided during peak periods.

Algorithm

###### Calculation of Savings

The following methodology provides formulas for estimating gas heating savings associated with condensing furnaces in unitary HVAC packages when applied as a CV, DOAS, MUAS, or any RTU that is indirectly heating 100% outside air (OA). These types of HVAC systems typically run continuously during the HVAC operating schedule to provide building ventilation and maintain indoor air quality or to compensate for exhaust and maintain neutral or slightly positive building pressurization. The algorithm estimates the gas use reduction resulting from utilizing condensing heating of 90% or higher thermal efficiency (TE) in place of the federal minimum TE of 80% (or other user defined baseline TE) for commercial warm air furnaces.

The methodology provides a representative group of operating schedules for the market sector applications highlighted earlier based on DOE commercial reference building models. Heating loads during the operating schedule are determined based on hourly differences between a range of supply air (SA) heated to temperatures and the OA temperature using Typical Meteorological Year (TMY3) weather data. These hourly heating loads are generated for all hours when the OA temperature is below the base temperature of 55 oF for heating in C&I settings per the TRM. To accommodate the variability in heating base temperatures in C&I settings, these hourly heating loads are also generated for base temperatures of 45 oF and 65 oF for heating. The hourly heating loads are then summed for the entire year. The annual heating loads are calculated in this manner for the climate zone 2 weather station (Chicago O’Hare Airport), which is then normalized to its National Climatic Data Center (NCDC) 30-year (1981-2010) weather average by multiplying by the heating degree day (HDD) ratio of the NCDC/TRM HDD55 over the TMY3 HDD55 (HDD at base temperature of 55 oF), and likewise for the annual heating loads for HDD45 (HDD at base temperature of 45 oF) and HDD65 (HDD at base temperature of 65 oF), using the values in Table 1 and Table 2. Since detailed hourly weather data is not available for all 5 of the TRM climate zone weather stations, the annual heating loads for the other climate zones are determined by multiplying the climate zone 2 annual heating loads by the ratio of the other climate zone NCDC HDD over the climate zone 2 NCDC HDD, using the values in Table 1.

These annual heating loads on a per unit airflow basis are then used in conjunction with the actual airflow of the 100% OA system and its condensing efficiency to calculate the gas heating savings versus the baseline (non-condensing) heating efficiency. This measure results in additional electric use by the unitary HVAC package due to the additional pressure drop of the condensing heat exchanger of the warm air furnace section.

Table 1. NCDC/TRM HDD Values for All Climate Zones

| Climate Zone - Weather Station/City | NCDC 30 Year Average HDD458 | NCDC 30 Year Average HDD551,8 | NCDC 30 Year Average HDD658 |
| --- | --- | --- | --- |
| 1 - Rockford AP / Rockford | 2495 | 4272 | 6569 |
| 2 - Chicago O'Hare AP / Chicago | 2263 | 4029 | 6340 |
| 3 - Springfield #2 / Springfield | 1812 | 3406 | 5495 |
| 4 - Belleville SIU RSCH / Belleville | 1197 | 2515 | 4379 |
| 5 - Carbondale Southern IL AP / Marion | 1183 | 2546 | 4477 |

Table 2. TMY3 HDD Values for Climate Zone 2

| Climate Zone - Weather Station/City | TMY3 HDD457 | TMY3 HDD557 | TMY3 HDD657 |
| --- | --- | --- | --- |
| 2 - Chicago O'Hare AP / Chicago | 2422 | 4188 | 6497 |

###### Electric Energy Savings

As noted previously, this measure results in additional SA fan electric use by the unitary HVAC system due to the additional pressure drop of the condensing heat exchanger of the warm air furnace section.

∆kWh 		= - (tFAN * cfm * P) / (FAN/MOTOR * 8520)

Where:

tFAN	= annual fan runtime (hr), refer to Tables 1 through 4

cfm	= airflow (cfm), use actual or rated system airflow

P	= incremental pressure drop (inch W.G.), assume 0.15 if actual value not known

FAN/MOTOR	 = combined fan and motor efficiency, assume 0.60 if actual value not known

8520	= conversion factor (fan horsepower – HP – calculation constant of 6356 for standard air conditions adjusted by 1 HP = 0.746 kW, or 6356/ 0.746 = 8520 for this kW calculation)

###### Summer Coincident Peak Demand Savings

For example, for a “big box” retail store operating 24 hours a day and 7 days a week (8760 hours per year) with a 5000 cfm DOAS that has an incremental pressure drop of 0.15 inch W.G. and a combined fan and motor efficiency of 0.6 has annual kWh savings of:

∆kWh 	= - (tFAN * cfm * P) / (FAN/MOTOR * 8520)

= - (8760 * 5000 * 0.15) / (0.6 * 8520)

= - 1285 kWh

The additional SA fan electric use by the unitary HVAC system will typically result in a modest electric demand increase.

kW		=  (kWh / tFAN) * CF

Where:

Continuing the previous example:

∆kW 	= (kWh / tFAN) * CF

= (- 1285 / 8760) * 1.0

= - 0.15 kW

CF = 1.0

###### Natural Gas Energy Savings

∆Therms 	= [QOA * cfm * (1/TENC - 1/TEC)]/ 100,000

Where:

QOA 	= annual outside air (OA) heating load per cfm of OA (Btu/cfm)

First, select the most representative operating schedule for the application from among the four (4) scenarios listed below and its set of three (3) applicable tables. Second, select the table in that set with the most representative HDD base temperature – the base temperature for OA below which heating is required. If that base temperature is not readily determined, select the TRM default base temperature of 55 oF (HDD55) for heating in C&I settings.    Third, select the climate zone within that table. Fourth, select an appropriate heated to supply air (SA) temperature within that table. Use the resulting QOA value, with linear interpolation allowed between SA temperatures.

The four (4) scenarios available are indicative of the following building applications and operating schedules:

- 24 hour a day and 7 day a week (24/7) operation, with HVAC operating schedule of 8760 hours per year, typical of large retail stores with DOAS, hotel/multifamily buildings with corridor MUAS, and healthcare facilities with DOAS. Use Table 3 through Table 5.

- 6:00 AM to 1:00 AM every day operation, with HVAC operating schedule of 7300 hours per year, typical of full service and quick service restaurants with kitchen MUAS. Use Table 6 through Table 8.

- 7:00 AM to 9:00 PM Monday-Friday, 7:00 AM to 10:00 PM Saturday, and 9:00 AM to 7:00 PM Sunday operations, with HVAC operating schedule of 5266 hours per year, typical of non-24/7 retail stores with DOAS. Use Table 9 through Table 11.

- 7:00 AM to 9:00 PM Monday-Friday operation, with HVAC operating schedule of 3911 hours per year, typical of school buildings with DOAS. Use Table 12 through Table 14.

TENC	= non-condensing thermal efficiency (TE), use federal minimum TE of 80% (0.80) or actual TE if known

TEC	= condensing thermal efficiency (TE), use actual TE or if unknown assume 90% (0.90)

Continuing the previous example: for a climate zone 2 (Chicago O'Hare AP / Chicago) application using a 90% TE condensing DOAS with a supply air temperature from the DOAS of 95 oF:

∆Therms = [QOA * cfm * (1/TENC - 1/TEC)]/ 100,000

=  303,268 * 5,000 * (1/0.80 – 1/0.90)/100,000

=  2,106 therms

100,000	= conversion factor (1 therm = 100,000 Btu)

8760 Hour Annual Operation Scenario

Table 3. 8760 Hour Annual Operation Scenario for HDD45

| Supply Air Fan Runtime = 8760 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone - Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 189,343 | 230,897 | 272,451 | 314,004 |
| 2 - Chicago O'Hare AP / Chicago | 171,737 | 209,427 | 247,116 | 284,806 |
| 3 - Springfield #2 / Springfield | 137,511 | 167,689 | 197,868 | 228,046 |
| 4 - Belleville SIU RSCH / Belleville | 90,839 | 110,775 | 130,711 | 150,647 |
| 5 - Carbondale Southern IL AP / Marion | 89,777 | 109,479 | 129,182 | 148,885 |

Table 4. 8760 Hour Annual Operation Scenario for HDD55

| Supply Air Fan Runtime = 8760 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone - Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 216,145 | 268,852 | 321,559 | 374,266 |
| 2 - Chicago O'Hare AP / Chicago | 203,850 | 253,559 | 303,268 | 352,977 |
| 3 - Springfield #2 / Springfield | 172,329 | 214,351 | 256,374 | 298,397 |
| 4 - Belleville SIU RSCH / Belleville | 127,248 | 158,278 | 189,307 | 220,337 |
| 5 - Carbondale Southern IL AP / Marion | 128,817 | 160,229 | 191,641 | 223,053 |

Table 5. 8760 Hour Annual Operation Scenario for HDD65

| Supply Air Fan Runtime = 8760 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone - Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 239,158 | 308,050 | 376,942 | 445,834 |
| 2 - Chicago O'Hare AP / Chicago | 230,820 | 297,311 | 363,802 | 430,292 |
| 3 - Springfield #2 / Springfield | 200,056 | 257,685 | 315,314 | 372,943 |
| 4 - Belleville SIU RSCH / Belleville | 159,426 | 205,351 | 251,276 | 297,200 |
| 5 - Carbondale Southern IL AP / Marion | 162,994 | 209,947 | 256,899 | 303,852 |

7300 Hour Annual Operation Scenario

Table 6. 7300 Hour Annual Operation Scenario for HDD45

| Supply Air Fan Runtime = 7300 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 151,914 | 185,369 | 218,823 | 252,278 |
| 2 - Chicago O'Hare AP / Chicago | 137,788 | 168,132 | 198,476 | 228,819 |
| 3 - Springfield #2 / Springfield | 110,328 | 134,624 | 158,921 | 183,217 |
| 4 - Belleville SIU RSCH / Belleville | 72,882 | 88,932 | 104,982 | 121,033 |
| 5 - Carbondale Southern IL AP / Marion | 72,030 | 87,892 | 103,755 | 119,617 |

Table 7. 7300 Hour Annual Operation Scenario for HDD55

| Supply Air Fan Runtime = 7300 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 173,511 | 215,950 | 258,389 | 300,828 |
| 2 - Chicago O'Hare AP / Chicago | 163,641 | 203,666 | 243,691 | 283,716 |
| 3 - Springfield #2 / Springfield | 138,338 | 172,174 | 206,010 | 239,846 |
| 4 - Belleville SIU RSCH / Belleville | 102,149 | 127,133 | 152,118 | 177,103 |
| 5 - Carbondale Southern IL AP / Marion | 103,408 | 128,701 | 153,993 | 179,286 |

Table 8. 7300 Hour Annual Operation Scenario for HDD65

| Supply Air Fan Runtime = 7300 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 191,803 | 247,046 | 302,288 | 357,531 |
| 2 - Chicago O'Hare AP / Chicago | 185,117 | 238,434 | 291,750 | 345,067 |
| 3 - Springfield #2 / Springfield | 160,444 | 206,655 | 252,866 | 299,076 |
| 4 - Belleville SIU RSCH / Belleville | 127,859 | 164,685 | 201,510 | 238,336 |
| 5 - Carbondale Southern IL AP / Marion | 130,720 | 168,370 | 206,020 | 243,670 |

5266 Hour Annual Operation Scenario

Table 9. 5266 Hour Annual Operation Scenario for HDD45

| Supply Air Fan Runtime = 5266 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 104,175 | 127,350 | 150,524 | 173,699 |
| 2 - Chicago O'Hare AP / Chicago | 94,488 | 115,508 | 136,527 | 157,547 |
| 3 - Springfield #2 / Springfield | 75,657 | 92,488 | 109,319 | 126,149 |
| 4 - Belleville SIU RSCH / Belleville | 49,979 | 61,097 | 72,215 | 83,334 |
| 5 - Carbondale Southern IL AP / Marion | 49,394 | 60,383 | 71,371 | 82,359 |

Table 10. 5266 Hour Annual Operation Scenario for HDD55

| Supply Air Fan Runtime = 5266 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 118,320 | 147,406 | 176,492 | 205,578 |
| 2 - Chicago O'Hare AP / Chicago | 111,590 | 139,021 | 166,452 | 193,884 |
| 3 - Springfield #2 / Springfield | 94,335 | 117,524 | 140,714 | 163,904 |
| 4 - Belleville SIU RSCH / Belleville | 69,657 | 86,780 | 103,904 | 121,027 |
| 5 - Carbondale Southern IL AP / Marion | 70,516 | 87,850 | 105,184 | 122,519 |

Table 11. 5266 Hour Annual Operation Scenario for HDD65

| Supply Air Fan Runtime = 5266 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 130,903 | 168,718 | 206,532 | 244,347 |
| 2 - Chicago O'Hare AP / Chicago | 126,339 | 162,836 | 199,333 | 235,829 |
| 3 - Springfield #2 / Springfield | 109,501 | 141,133 | 172,765 | 204,398 |
| 4 - Belleville SIU RSCH / Belleville | 87,262 | 112,470 | 137,678 | 162,886 |
| 5 - Carbondale Southern IL AP / Marion | 89,215 | 114,987 | 140,759 | 166,531 |

3911 Hour Annual Operation Scenario

Table 12. 3911 Hour Annual Operation Scenario for HDD45

| Supply Air Fan Runtime = 3911 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 75,029 | 91,729 | 108,428 | 125,128 |
| 2 - Chicago O'Hare AP / Chicago | 68,053 | 83,199 | 98,346 | 113,492 |
| 3 - Springfield #2 / Springfield | 54,490 | 66,618 | 78,746 | 90,874 |
| 4 - Belleville SIU RSCH / Belleville | 35,996 | 44,008 | 52,019 | 60,031 |
| 5 - Carbondale Southern IL AP / Marion | 35,575 | 43,493 | 51,411 | 59,329 |

Table 13. 3911 Hour Annual Operation Scenario for HDD55

| Supply Air Fan Runtime = 3911 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 85,672 | 106,825 | 127,979 | 149,132 |
| 2 - Chicago O'Hare AP / Chicago | 80,799 | 100,749 | 120,699 | 140,649 |
| 3 - Springfield #2 / Springfield | 68,305 | 85,170 | 102,035 | 118,901 |
| 4 - Belleville SIU RSCH / Belleville | 50,436 | 62,890 | 75,343 | 87,797 |
| 5 - Carbondale Southern IL AP / Marion | 51,058 | 63,665 | 76,272 | 88,879 |

Table 14. 3911 Hour Annual Operation Scenario for HDD65

| Supply Air Fan Runtime = 3911 Hours | Qoa (Annual Btu/cfm) At Supply Air Temperature Of |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone -Weather Station/City | 75oF | 85oF | 95oF | 105oF |
| 1 - Rockford AP / Rockford | 95,460 | 123,294 | 151,128 | 178,963 |
| 2 - Chicago O'Hare AP / Chicago | 92,132 | 118,996 | 145,860 | 172,724 |
| 3 - Springfield #2 / Springfield | 79,853 | 103,136 | 126,420 | 149,703 |
| 4 - Belleville SIU RSCH / Belleville | 63,635 | 82,190 | 100,745 | 119,299 |
| 5 - Carbondale Southern IL AP / Marion | 65,059 | 84,029 | 102,999 | 121,969 |

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

The actual incremental annual maintenance costs should be used, if available. If not, the incremental cost of $0.05 per 1000 Btu/hr of output capacity should be used for maintaining the combustion condensate disposal system yearly. This incremental cost is from the DOE Technical Support Document for the Notice of Proposed Rulemaking (NOPR) for the Commercial Warm Air Furnace Standard. Per the DOE documentation, it is based on their representative 250,000 Btu/hr input capacity furnace at a 92% TE.

###### Measure Code: CI-HVC-DSFN-V03-220101

###### Review Deadline: 1/1/2023

### Covers and Gap Sealers for Room Air Conditioners

###### Description

Room air conditioners (window ACs, through-the-wall or sleeve ACs, PTACs or PTHPs) constitute a permanent or semi-permanent penetration through the building’s envelope. These units are often poorly installed, resulting in gaps that act like air leakage pathways through the building’s envelope. The uncontrolled movement of air across the gaps in the envelope (infiltration) increases the building’s winter heating requirements and reduces its overall energy performance.

The heat loss and infiltration can be reduced by installing a rigid or flexible insulated cover on the inside of a room AC. These covers should be maintained by building staff and should remain installed through the heating season. Simple uninsulated cloth covers with no sealing at edges do not qualify for this measure.

There are several types of AC covers available that may be eligible for this measure:

- If the room AC is left in the window or sleeve, a rigid cover that covers the indoor side of the AC unit with foam gaskets to seal the edges may be installed.

- If the room AC is absent or is removed during the heating months, a rigid cover that fits inside the sleeve with foam gaskets along the edges for proper air sealing may be installed.

- Flexible covers that are well insulated and perfectly cover the indoor side of the AC unit may also be eligible for this measure.

This measure was developed to be applicable to the following program types: RF, DI.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The installed equipment is a rigid cover that fits inside the empty sleeve or completely covers the indoor side of a window AC unit, with foam gaskets sealing the edges. A flexible insulated cover that perfectly covers the indoor side of the unit and seals gaps may also be installed. Covers should remain installed throughout the winter heating season.

###### Definition of Baseline Equipment

The baseline equipment is a room AC (window AC, through-the-wall or sleeve AC, PTAC or PTHP) that is poorly installed with gaps around the edges and does not use AC covers or gap sealers during the winter heating months.

###### Deemed Lifetime of Efficient Equipment

The estimated useful life of typical AC covers is 5 years.

###### Deemed Measure Cost

The measure cost is the full cost of installing AC covers. Actual installation costs (material and labor) should be used if available. In actual costs are unknown, assume material cost of $24 (flexible covers) up to $119, depending on size of the AC unit. The install time per unit is 15 to 30 minutes at assumed labor rate of $20/hour.

###### Loadshape

Loadshape C04 – Commercial Electric Heating

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

If the building is electrically heated, electric energy savings are calculated as follows:

ΔkWh = (Qinfiltration * 1.08 * (TSA – TOA)  * EFLHheat) / (3,412 * COP)

Where:

Qinfiltration 	= Air infiltration (CFM) due to poor installation of window or through-the-wall AC

= ELA * 0.000645* (fs2 * (TSA – TOA) + fw2 * U2)1/2 *2118.88

Where:

ELA	= Effective Leakage Area (sq. in.)

= Can be collected on site; if unknown, assume 6 sq. in.

0.000645= Converts square inches to square meters

fs	= Stack Coefficient

= 1/3 * (9.81 * Height * 0.3048 / TOA)0.5

fw	= Wind Coefficient

= A * B * (Height * 0.3048 / 10)C

Where:

9.81		= Acceleration due to gravity (m/s2)

Height 	= Height of the location of the leakage area in feet

= Assume 8 ft per floor

0.3048	= Converts feet to meters

TOA	= Average Outside Air Temperature during heating period. Use values from table below, based on facility location. This figure must be in Kelvin to determine Stack Coefficient (fs) and infiltration (Qinfiltration), but in Fahrenheit to determine energy savings (ΔkWh, ΔTherms).

| Zone | TOA (°F) | TOA (K) |
| --- | --- | --- |
| Zone 1 (Rockford) | 31.63 | 272.94 |
| Zone 2 (Chicago) | 33.99 | 274.26 |
| Zone 3 (Springfield) | 34.58 | 274.58 |
| Zone 4 (Belleville) | 36.24 | 275.51 |
| Zone 5 (Marion) | 39.07 | 277.08 |

A, B and C 	= Constants based on the facility site’s shielding and terrain parameters. Use values from the tables below:

| Shielding Class | Shielding Type | Shielding Description | A |
| --- | --- | --- | --- |
| 1 | None | No obstructions or local shielding whatsoever (i.e. isolated building) | 0.324 |
| 2 | Light | Light local shielding with few obstructions (e.g. A few trees or a shed in the vicinity) | 0.285 |
| 3 | Moderate | Moderate local shielding; some obstructions within two house heights (e.g. Thick hedge fence on fence and nearby building) | 0.24 |
| 4 | Heavy | Heavy shielding; obstructions around most of perimeter buildings or trees within five building heights in most directions (e.g. Well developed/dense tract house) | 0.185 |
| 5 | Very Heavy | Very heavy shielding, large obstruction surrounding perimeter within two house heights (e.g. Typical downtown area) | 0.102 |

| Terrain Class | Terrain Type | Terrain Description | B | C |
| --- | --- | --- | --- | --- |
| 1 | None | Ocean or other body of eater with at least 5 km of unrestricted space | 1.3 | 0.1 |
| 2 | Light | Flat terrain with some isolated obstacles (e.g. Buildings or trees well separated from each other) | 1 | 0.15 |
| 3 | Moderate | Rural areas with low buildings, trees etc. | 0.85 | 0.2 |
| 4 | Heavy | Urban, industrial or forest areas | 0.67 | 0.25 |
| 5 | Very Heavy | Center of large city (e.g. Manhattan) | 0.47 | 0.35 |

0.3048		= Converts feet to meters

TSA	= Average Indoor Air Temperature during heating period. This figure will need to be in Kelvin to calculate infiltration (Qinfiltration) and Fahrenheit to calculate energy savings (ΔkWh, ΔTherms).

= Collected on site. If unknown, assume 72°F (295 K). If known, convert °F to K by using the following equation: K = (°F + 459.67) * (5/9).

U	= Average Wind Speed (m/s) during heating period.  Use table below, based on facility location.

| Zone | U (m/s) |
| --- | --- |
| Zone 1 (Rockford) | 4.50 |
| Zone 2 (Chicago) | 4.67 |
| Zone 3 (Springfield) | 4.60 |
| Zone 4 (Belleville) | 3.92 |
| Zone 5 (Marion) | 3.07 |

2118.88 		 = Converts m3/s to CFM

1.08 		= Sensible heat transfer constant (Btu/hr.CFM.°F)

EFLHheat	= Equivalent Full Load Hours for heating in Existing Buildings from section 4.4 HVAC End Use

3,412		= Converts Btus to kWh

COP		= Coefficient of Performance of the heating unit

= Collected on site.  If unknown assume 2.6 for PTHP

Deemed per-unit savings for the Multi-Family Building type for Shielding Class 3 and Terrain Class 3 are as follows:

| Multi-Family - Electric Savings per Unit (kWh/unit) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Floor | Height | Rockford | Chicago | Springfield | Belleville | Marion |
| 1 | 8 | 55.18 | 53.16 | 45.70 | 31.09 | 25.67 |
| 2 | 16 | 68.19 | 65.31 | 56.17 | 38.72 | 32.66 |
| 3 | 24 | 77.92 | 74.34 | 63.96 | 44.45 | 37.97 |
| 4 | 32 | 86.04 | 81.85 | 70.44 | 49.25 | 42.44 |
| 5 | 40 | 93.15 | 88.42 | 76.11 | 53.46 | 46.37 |
| 6 | 48 | 99.56 | 94.34 | 81.22 | 57.26 | 49.93 |
| 7 | 56 | 105.44 | 99.76 | 85.90 | 60.75 | 53.20 |
| 8 | 64 | 110.91 | 104.80 | 90.25 | 63.99 | 56.24 |
| 9 | 72 | 116.04 | 109.53 | 94.33 | 67.04 | 59.11 |
| 10 | 80 | 120.89 | 114.00 | 98.19 | 69.92 | 61.81 |
| 12 | 96 | 129.92 | 122.31 | 105.36 | 75.29 | 66.85 |
| 14 | 112 | 138.21 | 129.94 | 111.95 | 80.22 | 71.49 |
| 16 | 128 | 145.93 | 137.04 | 118.08 | 84.81 | 75.82 |
| 18 | 144 | 153.19 | 143.72 | 123.84 | 89.13 | 79.88 |
| 20 | 160 | 160.05 | 150.03 | 129.29 | 93.21 | 83.72 |
| 22 | 176 | 166.59 | 156.03 | 134.47 | 97.10 | 87.38 |
| 24 | 192 | 172.83 | 161.77 | 139.42 | 100.82 | 90.88 |
| 26 | 208 | 178.82 | 167.28 | 144.18 | 104.38 | 94.23 |
| 28 | 224 | 184.58 | 172.57 | 148.75 | 107.81 | 97.46 |
| 30 | 240 | 190.15 | 177.69 | 153.17 | 111.12 | 100.58 |

For example, a mid-rise multi-family building located in the moderate terrain class and shielding class of Chicago, has 16 rooms on the 10th floor (80 feet high) with PTHPs that get covered with a cover and foam gasket during the heating months. The indoor temperature during the heating months is maintained at 74°F.  The air infiltration and the related energy savings from the AC covers and seals are calculated as follows -

For Shielding Class 3 and Terrain Class 3,

A = 0.24, B = 0.85 and C = 0.2

Therefore,

fs = 1/3 * (9.81 m/s2 * 80 ft * 0.3048 m/ft / 274.26 K)0.5 = 0.3 m/K½.s

fw = 0.24 * 0.85 * (80 ft * 0.3048 m/ft / 10 m)0.2 = 0.24

Total effective leakage area (ELA) = 16 units * 6 sq. in. = 96 sq. in.

Qinfiltration = ELA * 0.000645* (fs2 * (TSA – TOA) + fw2 * U2)1/2 * 2118.88

= 96 * 0.000645 * (0.32 * (296.48 K – 274.26 K) + 0.242 * 4.672)1/2 * 2118.88

= 237 CFM

∆kWh = (237 * 1.08 Btu/hr.CFM.°F * (74°F – 33.99°F)  * 1,685) / (3,412 Btu/kWh* 2.6)

= 1,945 kWh

###### Summer Coincident Peak Demand Savings

As the savings occur during the winter season (non-peak), there are no demand savings associated with this measure.

###### Natural Gas Savings

If the building is heated with gas, the natural gas savings are calculated as follows:

ΔTherms = (Qinfiltration * 1.08 Btu/hr.CFM.°F * (TSA – TOA)  * EFLHheat) / (100,000 Btu/therm * η)

Where,

η	= Efficiency of heating equipment.

= Collected on site. If unknown, assume 80%.

100,000	= Converts Btus to therms

Other factors as defined above

Deemed per-unit savings per unit for the Multi-Family Building type for Shielding Class 3 and Terrain Class 3 are as follows:

| Multi-Family - Gas Savings per Unit (Therms/Unit) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Floor | Height | Rockford | Chicago | Springfield | Belleville | Marion |
| 1 | 8 | 6.12 | 5.90 | 5.07 | 3.45 | 2.85 |
| 2 | 16 | 7.56 | 7.24 | 6.23 | 4.29 | 3.62 |
| 3 | 24 | 8.64 | 8.24 | 7.09 | 4.93 | 4.21 |
| 4 | 32 | 9.54 | 9.08 | 7.81 | 5.46 | 4.71 |
| 5 | 40 | 10.33 | 9.81 | 8.44 | 5.93 | 5.14 |
| 6 | 48 | 11.04 | 10.46 | 9.01 | 6.35 | 5.54 |
| 7 | 56 | 11.69 | 11.06 | 9.53 | 6.74 | 5.90 |
| 8 | 64 | 12.30 | 11.62 | 10.01 | 7.10 | 6.24 |
| 9 | 72 | 12.87 | 12.15 | 10.46 | 7.43 | 6.55 |
| 10 | 80 | 13.41 | 12.64 | 10.89 | 7.75 | 6.85 |
| 12 | 96 | 14.41 | 13.56 | 11.68 | 8.35 | 7.41 |
| 14 | 112 | 15.33 | 14.41 | 12.41 | 8.90 | 7.93 |
| 16 | 128 | 16.18 | 15.20 | 13.09 | 9.40 | 8.41 |
| 18 | 144 | 16.99 | 15.94 | 13.73 | 9.88 | 8.86 |
| 20 | 160 | 17.75 | 16.64 | 14.34 | 10.34 | 9.28 |
| 22 | 176 | 18.47 | 17.30 | 14.91 | 10.77 | 9.69 |
| 24 | 192 | 19.16 | 17.94 | 15.46 | 11.18 | 10.08 |
| 26 | 208 | 19.83 | 18.55 | 15.99 | 11.57 | 10.45 |
| 28 | 224 | 20.47 | 19.14 | 16.50 | 11.96 | 10.81 |
| 30 | 240 | 21.09 | 19.70 | 16.98 | 12.32 | 11.15 |

For example, a gas-heated mid-rise multi-family building located in the moderate terrain class and shielding class of Chicago, has 16 rooms on the 10th floor (80 feet high) with room air conditioners that get covered with an AC cover and foam gasket during the heating months. The indoor temperature during the heating months is maintained at 74°F.  The air infiltration and the related therm savings from the AC covers and seals are calculated as follows:

For Shielding Class 3 and Terrain Class 3,

A = 0.24, B = 0.85 and C = 0.2

Therefore,

fs = 1/3 * (9.81 m/s2 * 80 ft * 0.3048 m/ft / 274.26 K)0.5 = 0.3 m/K½.s

fw = 0.24 * 0.85 * (80 ft * 0.3048 m/ft / 10 m )0.2 = 0.24

Total effective leakage area (ELA) = 16 units * 6 sq.in = 96 sq. in

Qinfiltration = ELA * 0.000645* (fs2 * (TSA – TOA) + fw2 * U2)1/2 *2118.88

= 96 * 0.000645 * (0.32 * (296.48 K – 274.26 K) + 0.242 * 4.672)1/2 * 2118.88

= 237 CFM

∆Therms = (237 * 1.08 Btu/hr.CFM.°F * (74°F – 33.99°F)  * 1,685) / (100,000 Btu/therm * 80%)

= 216 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-CRAC-V02-200101

###### Review Deadline: 1/1/2023

### High Temperature Heating and Ventilation (HTHV) Direct Fired Heater

###### Description

This measure applies to 100% outside air, high temperature heating and ventilation (HTHV) direct fired gas heaters. These units replace unit heaters (indirect gas fired or steam coil) or rooftop units in warehouses which suffer from extreme temperature stratification, minimal controls and reduced heating efficiencies.

Warehouses have high ceilings (~30 ft high), and suffer from stratification of air. The warm air rises and remains near the roof, which keeps the thermostat from reaching its desired setpoint. This increases the run hours of the heating unit and causes discomfort among the occupants. The HTHV units have high pressure fans that direct high temperature and high velocity air towards the floor and thus help minimize temperature stratification. On average, a 30 ft high warehouse could reduce its linear stratification from 0.53°F/ft to 0.13°F/ft, thus maintaining a more uniform temperature in the room and reducing the operating hours of the heating unit.

Since the HTHV units are direct fired, they also have improved efficiencies of 92% compared to 80% for a typical indirect fired unit heater or rooftop unit. They transfer the latent heat of the flue gases into the space instead of venting it out.

This measure only applies to high ceiling warehouses that do not have any other destratification technologies installed (i.e., destratification fans, air rotation units, etc.). New HTHV units must be the warehouse’s primary heat source.

This measure was developed to be applicable to the following program types: RF, TOS, NC.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment must be a 100% outside air, HTHV direct fired gas heater, with a discharge temperature greater than or equal to 150°F, a temperature rise greater than or equal to 140°F, and an efficiency exceeding 92%.

###### Definition of Baseline Equipment

The baseline equipment must be an indirect fired gas or steam unit heater or a rooftop unit used as the primary space heating source. Warehouses with existing destratification technologies (high volume, low speed fans or air turnover units) do not qualify for this measure.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 15 years.

###### Deemed Measure Cost

The measure cost should be based on a contractor’s evaluation of the project scope and may vary significantly on a project to project basis. If unknown, for early replacement or retrofit projects, assume $14.50/MBtu/hr (material cost for an HTHV unit) or $26/MBTUh (sum of material and installation cost).

The incremental measure cost, assuming a baseline of standard efficiency unit heaters, is $7.43/MBtu/hr (material cost).

###### Loadshape

Loadshape C04: Commercial Electric Heating

###### Coincidence Factor

Assumed to be 0.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

HTHV units may increase the facility’s electric energy consumption due to high pressure motors that supply air at higher velocity.

ΔkWh 	= - kWh/HDD * HDD

Where:

kWh/HDD 	= increase in electric energy consumption due to HTHV fan motor

= 1.04

HDD 		= heating degree days

| Zone | City | HDD55 | ΔkWh |
| --- | --- | --- | --- |
| 1 | Rockford | 4,272 | (4,443) |
| 2 | Chicago | 4,029 | (4,190) |
| 3 | Springfield | 3,406 | (3,542) |
| 4 | Belleville | 2,515 | (2,616) |
| 5 | Marion | 2,546 | (2,648) |

Although HTHV fan motors have a higher power draw, they also result in decreased heating equipment operating time, potentially offsetting some of the increase in electrical energy consumption. Therefore, if replacing heating equipment other than unit heaters, a custom evaluation may be necessary to determine if there is an increase in electrical energy consumption.

###### Summer Coincident Peak Demand Savings

Since HTHV units operate during the winter (non-peak) season, there are no demand savings associated with this measure.

###### Natural Gas Savings

Custom calculation below, otherwise use a deemed savings factor from the table that follows.

ΔTherms = (FLHbase * Capbase /(ηbase * 100)) – (FLHeff * Capeff / (ηeff * 100))

Where:

FLHbase 	= LFbase * Hours

FLHeff	 = LFeff * Hours

Hours	 = Annual operating hours of the unit, calculated as total number of hours when outside air temperature is less than 55°F. This can be adjusted based on the facility’s occupancy schedule.

LFbase 	= load factor of baseline unit heater

= (Qinf,base + Qw,base + Qr,base)/(Capbase*100)

LFeff	= load factor of HTHVheater

= (Qinf,eff + Qw,eff + Qr,eff)/(Capeff*100)

Capbase 	= existing heating unit input capacity (MBtu/hr)

= can be collected on site, or assumed to be the same as HTHV unit capacity, Capeff

Capeff	 = HTHV unit input capacity (MBtu/hr)

= can be collected on site or from specification sheets

ηbase 	= efficiency of existing heating unit

= collected from equipment nameplate or assumed as70% for steam unit heaters, 80% for gas fired unit heaters, and 84% for rooftop units

ηeff 	= efficiency of HTHV unit

= collected from equipment nameplate or assumed as 92%

100	= converts MBtu to therms

See table below for savings inputs.

| Parameter | Existing Unit | Proposed (Efficient) Unit |
| --- | --- | --- |
| Temperatures |  |  |
| Setpoint Temperature (°F) | Tsetpoint = collected on site, or assumed as 65°F |  |
| Ceiling Temperature (°F) | Either collected on site when the existing unit is in operation with an infrared gun, or assumed as: Tc,base= Tsetpoint + 0.53°F/ft * Height | Either collected on site when the proposed unit is in operation with an infrared gun, or assumed as: Tc,eff = Tsetpoint + 2 to 4°F |
| Average Room Temperature (°F) | Tr,base= (Tsetpoint + Tc,base)/2 | Tr,eff= (Tsetpoint + Tc,eff)/2 |
| Outside Air Temperature (°F) | TOA , from local weather data |  |
| Heat Loads |  |  |
| Infiltration Load: | Qinf,base= 0.04CFM/ft2 * (Wall Surface Area + Roof Surface Area) * 1.08 * (Tr,base - TOA) | Qinf,eff= 0.04CFM/ft2 * (Wall Surface Area + Roof Surface Area) * 1.08 * (Tr,eff - TOA) |
| Wall Conduction Load: | Qw,base = 1/R-valuewall * (Wall Surface Area * 1.08 * (Tr,base - TOA) Where R-valuewall = the insulation value of the wall. It can be collected on site, or assumed as R-15. | Qw,eff = 1/R-valuewall * (Wall Surface Area * 1.08 * (Tr,eff - TOA) Where R-valuewall = the insulation value of the wall. It can be collected on site, or assumed as R-15. |
| Roof Conduction Load: | Qr,base = 1/R-valueroof * (Roof Surface Area * 1.08 * (Tr,base - TOA) Where R-valueroof = the insulation value of the roof. It can be collected on site, or assumed as R-20. | Qr,eff = 1/R-valueroof * (Roof Surface Area * 1.08 * (Tr,eff - TOA) Where R-valueroof = the insulation value of the roof. It can be collected on site, or assumed as R-20. |
| Surface Areas |  |  |
| Roof Surface Area: | Collected on site or assumed as: = facility area in sq.ft. If facility area is unknown, assume facility area = 41.4 sq. ft./MBtu/hr * Capeff |  |
| Wall Surface Area: | Collected on site or assumed as: = (Height * Length + Height * Width) * 2 Where: Length, Height and Width (feet) of the facility can be collected on site. If unknown, assume: Length = Width = (Facility Area)1/2 and Height = 25 ft If facility area is unknown, assume facility area = 41.4 sq. ft./MBtu/hr * Capeff |  |

The default values from the table above were used to calculate the deemed savings values in the table below. Savings are provided for various rated input capacity ranges and weather stations.

| Capeff (MBtu/hr) | Average Capeff (MBtu/hr) | Nearest Weather Station | ΔTherms (Baseline Equipment: Steam Fired Unit Heaters ) | ΔTherms (Baseline Equipment: Gas Fired Unit Heaters) | ΔTherms (Baseline Equipment: Rooftop Units) |
| --- | --- | --- | --- | --- | --- |
| 300 > Capeff ≥ 500 | 400 | Rockford | 3,120 | 1,996 | 1,620 |
| 500 > Capeff ≥ 900 | 757 | Rockford | 5,208 | 3,346 | 2,725 |
| 900 > Capeff ≥ 1,000 | 950 | Rockford | 6,280 | 4,047 | 3,297 |
| 1,000 > Capeff ≥ 1,400 | 1,200 | Rockford | 7,656 | 4,932 | 4,020 |
| 1,400 > Capeff ≥ 1,600 | 1,499 | Rockford | 9,249 | 5,966 | 4,872 |
| 1,600 > Capeff ≥ 2,100 | 1,850 | Rockford | 11,100 | 7,160 | 5,865 |
| 2,100 > Capeff ≥ 2,400 | 2,200 | Rockford | 12,914 | 8,338 | 6,820 |
| Capeff ≥ 2,400 | 2,718 | Rockford | 15,547 | 10,084 | 8,236 |
| 300 > Capeff ≥ 500 | 400 | Chicago | 2,820 | 1,824 | 1,488 |
| 500 > Capeff ≥ 900 | 757 | Chicago | 4,709 | 3,058 | 2,506 |
| 900 > Capeff ≥ 1,000 | 950 | Chicago | 5,681 | 3,696 | 3,031 |
| 1,000 > Capeff ≥ 1,400 | 1,200 | Chicago | 6,924 | 4,512 | 3,696 |
| 1,400 > Capeff ≥ 1,600 | 1,499 | Chicago | 8,364 | 5,456 | 4,482 |
| 1,600 > Capeff ≥ 2,100 | 1,850 | Chicago | 10,046 | 6,549 | 5,384 |
| 2,100 > Capeff ≥ 2,400 | 2,200 | Chicago | 11,682 | 7,634 | 6,292 |
| Capeff ≥ 2,400 | 2,718 | Chicago | 14,079 | 9,214 | 7,583 |
| 300 > Capeff ≥ 500 | 400 | Springfield | 2,452 | 1,588 | 1,300 |
| 500 > Capeff ≥ 900 | 757 | Springfield | 4,095 | 2,665 | 2,188 |
| 900 > Capeff ≥ 1,000 | 950 | Springfield | 4,950 | 3,221 | 2,651 |
| 1,000 > Capeff ≥ 1,400 | 1,200 | Springfield | 6,024 | 3,936 | 3,240 |
| 1,400 > Capeff ≥ 1,600 | 1,499 | Springfield | 7,285 | 4,767 | 3,912 |
| 1,600 > Capeff ≥ 2,100 | 1,850 | Springfield | 8,732 | 5,717 | 4,718 |
| 2,100 > Capeff ≥ 2,400 | 2,200 | Springfield | 10,164 | 6,666 | 5,500 |
| Capeff ≥ 2,400 | 2,718 | Springfield | 12,258 | 8,045 | 6,632 |
| 300 > Capeff ≥ 500 | 400 | Belleville | 2,456 | 1,604 | 1,320 |
| 500 > Capeff ≥ 900 | 757 | Belleville | 4,103 | 2,687 | 2,218 |
| 900 > Capeff ≥ 1,000 | 950 | Belleville | 4,950 | 3,249 | 2,689 |
| 1,000 > Capeff ≥ 1,400 | 1,200 | Belleville | 6,036 | 3,972 | 3,276 |
| 1,400 > Capeff ≥ 1,600 | 1,499 | Belleville | 7,300 | 4,812 | 3,972 |
| 1,600 > Capeff ≥ 2,100 | 1,850 | Belleville | 8,751 | 5,772 | 4,773 |
| 2,100 > Capeff ≥ 2,400 | 2,200 | Belleville | 10,186 | 6,732 | 5,566 |
| Capeff ≥ 2,400 | 2,718 | Belleville | 12,285 | 8,127 | 6,713 |
| 300 > Capeff ≥ 500 | 400 | Marion | 2,180 | 1,444 | 1,200 |
| 500 > Capeff ≥ 900 | 757 | Marion | 3,649 | 2,430 | 2,021 |
| 900 > Capeff ≥ 1,000 | 950 | Marion | 4,408 | 2,936 | 2,442 |
| 1,000 > Capeff ≥ 1,400 | 1,200 | Marion | 5,364 | 3,576 | 2,988 |
| 1,400 > Capeff ≥ 1,600 | 1,499 | Marion | 6,491 | 4,332 | 3,613 |
| 1,600 > Capeff ≥ 2,100 | 1,850 | Marion | 7,789 | 5,217 | 4,348 |
| 2,100 > Capeff ≥ 2,400 | 2,200 | Marion | 9,064 | 6,072 | 5,082 |
| Capeff ≥ 2,400 | 2,718 | Marion | 10,926 | 7,339 | 6,116 |

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-HTHV-V01-180101

###### Review Deadline: 1/1/2023

### Gas High Efficiency Single Package Vertical Air Conditioner

###### Description

This measure covers the installation of a single package vertical air conditional with a high efficiency gas furnace, referred to here as a through the wall (TTW) condensing gas furnace, instead of a standard efficiency gas furnace. The primary market served by TTWs are multifamily housing and hospitality in a new construction application. High efficiency gas furnaces achieve savings through the utilization of a sealed, super insulated combustion chamber, more efficient burners, and multiple heat exchangers that remove a significant portion of the waste heat from the flue gases. Because multiple heat exchangers are used to remove waste heat from the escaping flue gases, most of the flue gases condense and must be drained. Management of the acidic condensate is currently a major limiting factor for retrofit application, making the new construction the best initial market point until the industry develops better strategies for condensate management for retrofit applications. Also, TTWs are normally installed at the exterior wall to access outside air to reject heat in the cooling cycle. Placement of TTWs near the exterior might be prohibitive in retrofit applications.  Furnaces equipped with ECM fan motors and with above code EER ratings provide an opportunity for additional electric energy savings.

This measure assumes unit size less than or equal to 65,000 Btu/hr.

This measure was developed to be applicable to the following program types: NC, TOS. If applied to other program types such as RF, the measure savings should be verified via a custom measure.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be an TTW condensing system with code minimum 9.0 EER cooling system (minimum code scheduled to increase to 11.0 EER on September 23, 2019) and a high-efficiency gas furnace with an annual fuel utilization efficiency (AFUE) of 90% or greater. Fan electrical efficiency must exceed the program requirements.

###### Definition of Baseline Equipment

Baseline equipment for this measure are units with a cooling system that meets the current code minimum 9.0 EER efficiency rating and a heating unit with an AFUE rating of 80% or less.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 16.5 years.

###### Deemed Measure Cost

The incremental capital cost for this measure depends on efficiency as listed below:

| AFUE | Incremental Cost Premium |
| --- | --- |
| 80% | $400 |
| 90% | $400 |
| 95% | $500 |

###### Loadshape

Loadshape R08 – Residential Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.

CFSSP 	= Summer System Peak Coincidence Factor for Central A/C (during utility peak hour)

= 68%

CFPJM 	= PJM Summer Peak Coincidence Factor for Central A/C (average during PJM peak period)

= 46.6%

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Electric savings come from a high efficiency cooling unit. In some instances, the TTW unit provided by the manufacturer may not have higher efficiency cooling and fan blower motor systems integrated in to the TTW design; in these cases, electric energy savings will be zero for those components.

ΔkWhEER	= FLHcool * Capacity * (1/EERbase - 1/EEReff) / 1000

Where:

FLHcool	= Full load hours for cooling:

| Climate Zone (City based upon) | FLHcool (multifamily) |
| --- | --- |
| 1 (Rockford) | 467 |
| 2 (Chicago) | 506 |
| 3 (Springfield) | 663 |
| 4 (Belleville) | 940 |
| 5 (Marion) | 820 |
| Weighted Average | 564 |

Capacity	= Cooling capacity of the efficient unit in Btu/hr

= Actual installed

EEReff	= Energy efficiency ratio of the efficient equipment

= Actual installed rating

EERbase		= Energy efficiency ratio of the baseline equipment – Presently, the federal minimum efficiency level is 9.0 EER, increasing to 11.0 EER on September 23, 2019.

= 9.0

For example, for a Rockford non-weatherized multifamily unit conditioned by a SPVAC with a 2-ton (24,000 Btu/hr) cooling capacity, a rated EER of 11.0, and an ECM fan blower motor installed. ΔkWh = [467 * 24,000 * (1/9.0 – 1/11.0) / 1000] = 958 kWh

###### Summer Coincident Peak Demand Savings

ΔkW = CF * Capacity * (1/EERbase - 1/EEReff) / 1000

Where:

CFSSP 	= Summer System Peak Coincidence Factor for Central A/C (during utility peak hour)

= 68%

CFPJM 	= PJM Summer Peak Coincidence Factor for Central A/C (average during PJM peak period)

= 46.6%

###### Natural Gas Savings

ΔTherms 	= EFLHheat * Capacity * (AFUEeff – AFUEbase) / AFUEbase / (100,000 Btu/Therm)

Where

EFLHheat	=  Equivalent Full Load Hours for heating:

| Climate Zone (City based upon) | EFLHheat (general multifamily) |
| --- | --- |
| 1 (Rockford) | 1,742 |
| 2 (Chicago) | 1,704 |
| 3 (Springfield) | 1,498 |
| 4 (Belleville) | 1,208 |
| 5 (Marion) | 1,429 |

Capacity	= Nominal heating input capacity furnace size (Btu/hr) for efficient unit

= Actual

AFUEeff 	= Efficient furnace annual fuel utilization efficiency rating

= Actual installed rating

AFUEbase	= Baseline furnace annual fuel utilization efficiency rating

= 80%

For example, for a Chicago non-weatherized multifamily unit heated by an SPVAC with a 40 kBtu/hr capacity and a rated AFUE of 93%.

ΔTherms 	= 1,704 * 40,000 * [(0.93 – 0.8)/0.8] / (100,000 Btu/Therm) = 111 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC -SPVA-V01-190101

###### Review Deadline: 1/1/2023

### Advanced Rooftop Controls (ARC)

###### Description

The Advanced Rooftop Controls (ARC) measure installs demand-controlled ventilation with optional supply-fan speed control via a variable-frequency drive to a single-zone, packaged HVAC unit with a functioning integrated economizer already installed. The demand-controlled ventilation modulates the outside air damper based on CO2 concentration in the conditioned space. The supply-fan speed control options consist of setting the fan speed to 40% in ventilation mode and to 90% in heating and cooling modes, or of setting the fan speed to 40% in ventilation mode, to 75% in 1st stage heating and 1st stage cooling modes, and to 90% in 2nd stage heating and 2nd stage cooling modes. The measure results in fan, cooling, and heating savings compared to a baseline scenario of constant-volume, constant-ventilation operation typical of single-zone, packaged HVAC units. There are a number of off-the-shelf products available for the packaged HVAC unit market that support these control sequences, and the energy savings potential of these strategies has been studied and reported on.

Demand-controlled ventilation modulates the percentage of outside air that is delivered to a space and its occupants by controlling the position of the outside air damper. The outside air damper is set to the minimum position required for the space, and is opened further when CO2 concentration in the conditioned space increases, which indicates an increase in occupancy. The damper also opens to provide 100% outside air cooling (i.e., the unit economizes) when conditions permit. This portion of the measure saves energy by minimizing the energy required to unnecessarily heat and cool outside air. Demand-controlled ventilation can also be combined with the installation of a variable-frequency drive on the supply fan. This drive is used to reduce the speed of the supply fan when the full design airflow is not required. When the unit is only providing ventilation air (i.e., not heating or cooling), the airflow is reduced substantially, but not below the required minimum ventilation rate. The flow for heating and cooling can also be reduced a small amount in most cases. Per the fan affinity laws, the reduction in flow correlates to a near cubic reduction in fan power. In these ways, this measure is able to achieve cooling, heating, and fan energy reduction.

This measure is intended for commercial buildings served by single-zone, packaged HVAC units. This measure was developed to be applicable to the following program types: RF, DI

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is a single-zone, packaged HVAC unit (with an existing functional integrated economizer) that has been retrofitted with demand-controlled ventilation controls with optional supply-fan speed control via a variable-frequency drive.

###### Definition of Baseline Equipment

The baseline equipment is a single-zone, packaged HVAC unit (with an existing functional integrated economizer) that lacks demand-controlled ventilation controls and lacks supply-fan speed control via a variable-frequency drive.

###### Deemed Lifetime of Efficient Equipment

The deemed measure life is 10 years and based on CO2 sensor estimated life.

###### Deemed Measure Cost

Actual measure costs should be used if available. If costs are not available, the deemed measure cost below can be used.

Table 1 – Deemed Measure Cost Details

| Measure | Material Unit (Each) | Material Cost / Unit | Labor Unit (Hours) | Labor Rate/ Unit | Total Cost |
| --- | --- | --- | --- | --- | --- |
| DCV | 1 | $1,663.90 | 3 | $96.67 | $1,953.91 |
| DCV and VFD with two speed modes (40% ventilating & 90% heating/cooling) | 1 | $3,025.38 | 4 | $96.67 | $3,412.06 |
| DCV and VFD with three speed modes (40% ventilating, 75% 1st stage heating/cooling & 90% 2nd stage heating/cooling) | 1 | $3,487.00 | 4 | $96.67 | $3,873.68 |

###### Loadshape

Commercial ventilation C23

###### Coincidence Factor

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

To determine the savings associated with the Advanced Rooftop Controls (ARC) measure we utilized the available IL TRM prototype eQuest models which were initially created by the Energy Center of Wisconsin but modified by VEIC in 2014 as part of the IL TRM v4.0 Equivalent Full Load Hours (EFLH) update.  For each building type we used the most recent versions of the models for our baseline models (Assembly was not part of EFLH update). These models which were used are the most up-to-date versions and are readily available on the VEIC SharePoint site, under the TRM Reference Documents Section.

Upon examination of the ComEd building prototype models we found several of the baseline models did not have packaged single zone (PSZ) units. This measure is targeting packaged single zone HVAC systems.  Therefore, as a basis for savings calculations, we chose only models that: 1) utilized PSZ HVAC systems, and 2) aligned with the small commercial building type applicable to this measure.  Once the ComEd baseline models were selected, we determined several modifications were necessary to the prototype models in order to represent the baseline scenario for this measure:

- Multistage PSZ HVAC System with Constant Volume Supply Fan

- Optimized Economizer Controls by Climate Zone

  - Economizer Changeover Type – Set to fixed Dry Bulb

  - Economizer High-Limit Control Setpoints – Setpoints based on ASHRAE Climate Zones Fixed Dry Bulb Temperature recommendations.

  - Enable Integrated Operation – Allows economizer to operate simultaneously with mechanical cooling

Additionally, a number of the building prototype models were found to have supply fan total static pressure modeled inputs that seem excessive and atypical for packaged single zone rooftop units – these included Convenience Store (5 in. wc), Manufacturing Facility (5 in. wc), Office Low Rise (5 in. wc), Religious Building (5 in. wc), and Restaurant (5 in. wc). The remaining models had supply fan total static pressure inputs more in line with what we would expect to find for packaged single zone rooftop units, ranging from 1.3 to 2 in. wc. For each model having a supply fan total static pressure above 2 in. wc, model inputs were adjusted to set these to 2 in. wc. To implement the modifications shown above, changes were made to eQUEST keywords in the ComEd prototype models as shown in the following table. Hard-coded system capacities and supply airflows can be found in the attached “Advanced Rooftop Controls_End Use Analysis_IL TRM.xlsx” spreadsheet.

Table 2 – Prototype Modifications to eQuest Keywords

| Component Adjusted | eQuest Keyword | IL TR Value | Modified Prototype Value |
| --- | --- | --- | --- |
| System - System Type | SYSTEM:TYPE | PSZ | PVVT |
| System - Airflow and Temperature Control | SYSTEM:AIR/TEMP-CONTROL | N/A | STAGED-VOLUME |
| System – Supply Fan Total Static Pressure | SYSTEM:SUPPLY-STATIC | Varies | If >2: 2 Else: IL TR Value |
| System - Cooling and Heating Capacities | SYSTEM:COOLING-CAPACITY SYSTEM:HEATING-CAPACITY | Auto-sized | Hard-coded (after retrieving auto-sized outputs) |
| System - Supply Fan Control | SYSTEM:FAN-CONTROL | Varies | CONSTANT-VOLUME |
| System - Supply Fan Ratios | SYSTEM:MIN-FLOW-RATIO SYSTEM:CMIN-FLOW-RATIO SYSTEM:HMIN-FLOW-RATIO SYSTEM:-MAX-FAN-RATIO | N/A | 1 |
| System - Supply Airflow | SYSTEM:SUPPLY-FLOW | Auto-sized | Hard-coded (after retrieving auto-sized outputs) |
| Economizer - Changeover Type | SYSTEM:OA-CONTROL | Fixed | Single Dry-Bulb |
| Economizer - Changeover Setpoint | SYSTEM-ECONO-LIMIT-T | Varies | ASHRAE 90.1-2013 – High-Limit Shutoff Control Settings: ASHRAE CLIMATE ZONE – 4A = 65°F ASHRAE CLIMATE ZONE – 5A = 70°F |
| Economizer - Integrated Operation | SYSTEM:ECONO-LOCKOUT | Yes | No |

Further modifications were then made to these baseline models in order to simulate the following measure scenarios:

- Demand-controlled ventilation (DCV) controls

- DCV and supply fan variable frequency drive (VFD) with two fan speed modes

  - 40% fan speed for ventilating

  - 90% fan speed for heating and cooling

- DCV and supply fan VFD with three fan speed modes

  - 40% fan speed for ventilating

  - 75% fan speed for 1st stage heating and cooling

  - 90% fan speed for 2nd and higher stage heating and cooling

The eQuest modifications from the baseline models to represent these measure scenarios are shown in the following table. Full modeled energy end use and savings summaries can be found in the attached “Advanced Rooftop Controls_End Use Analysis_IL TRM.xlsx” spreadsheet.

Table 3 – Baseline and Measure Scenario eQuest Keywords

| Component Adjusted | eQuest Keyword | Baseline Value | Measure Scenario Values |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 1 | 2 | 3 |
| System - Minimum Outside Air Control | SYSTEM:MIN-OA-METHOD | Fraction of Design Flow | DCV Return Sensor | DCV Return Sensor | DCV Return Sensor |
| System - Supply Airflow | SYSTEM:SUPPLY-FLOW | Hard-coded | 1.0 × Hard-coded value | 0.9 × Hard-coded value | 0.9 × Hard-coded value |
| System - Supply Fan Control | SYSTEM:FAN-CONTROL | CONSTANT-VOLUME | CONSTANT-VOLUME | FAN-EIR-FPLR | FAN-EIR-FPLR |
| System - Supply Fan Ratios | SYSTEM:MIN-FLOW-RATIO SYSTEM:CMIN-FLOW-RATIO SYSTEM:HMIN-FLOW-RATIO SYSTEM:-MAX-FAN-RATIO | 1 1 1 1 | 1 1 1 1 | 0.44* 1 1 1 | 0.44* 0.83** 0.83** 1 |

*Since the total supply flow is limited by 0.9 of the baseline, a value of 0.44 for the minimum flow ratio results in a 40% fan speed: 0.4/0.9=0.44
** Since the total supply flow is limited by 0.9 of the baseline, a value of 0.83 for the minimum heating/cooling flow ratios results in a 75% fan speed: 0.75/0.9=0.83

With these modifications in place each scenario was simulated in eQuest for each chosen IL TRM prototype building type across the five TRM climate zones. Whole building electric and gas savings were determined from the simulation output and are presented in the following sections. Electric savings have been normalized by cooling tons and heating savings by furnace kBtuh output.

###### Electric Energy Savings

ΔkWh = (CapacityCool * Normalized Electric Cooling Energy Savings) + (CapacityHeat * Normalized Electric Heating Energy Savings)

Where:

CapacityCool	= capacity of the cooling equipment in tons (nominal tonnage may be used).

=Actual

Normalized Electric Cooling Energy Savings

= kWh/ton savings value for the appropriate combination of building type, climate zone, and measure scenario per Table 4 – Electric Cooling Energy Savings Summary (kWh/ton)

Table 4 – Electric Cooling Energy Savings Summary (kWh/ton)

CapacityHeat	= capacity of the heating equipment in tons (nominal tonnage may be used).

=Actual

Normalized Electric Heating Energy Savings

= kWh/ton savings value for the appropriate combination of building type, climate zone, and measure scenario per Table 5 – Electric Energy Heating Savings Summary (kWh/ton)

Table 5 – Electric Heating Energy Savings Summary (kWh/ton)

|  | Rockford - Zone 1 |  |  | Chicago - Zone 2 |  |  | Springfield - Zone 3 |  |  | Mt Vernon/Belleville - Zone 4 |  |  | Marion - Zone 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Measure Scenario: 1 - DCV 2 - DCV and VFD w/2-speed fan control 3- DCV and VFD w/3-speed fan control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Building Type | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 |
| Assembly | 868.6 | 893.1 | 893.1 | 868.6 | 893.1 | 893.1 | 746.3 | 795.2 | 783.0 | 734.0 | 783.0 | 770.7 | 734.0 | 807.4 | 795.2 |
| Assisted Living | 119.3 | 59.6 | 23.9 | 95.4 | 47.7 | 11.9 | 83.5 | 35.8 | 11.9 | 83.5 | 59.6 | 23.9 | 71.6 | 59.6 | 23.9 |
| College | 880.8 | 831.9 | 807.4 | 770.7 | 734.0 | 709.6 | 648.4 | 611.7 | 599.5 | 526.1 | 513.8 | 489.3 | 342.5 | 330.3 | 318.1 |
| Conditioned Storage | 305.8 | 171.3 | 146.8 | 269.1 | 134.6 | 110.1 | 244.7 | 110.1 | 85.6 | 232.4 | 97.9 | 73.4 | 183.5 | 48.9 | 36.7 |
| Convenience Store | 587.2 | 464.9 | 440.4 | 526.1 | 403.7 | 379.2 | 452.6 | 342.5 | 330.3 | 428.2 | 330.3 | 305.8 | 354.8 | 269.1 | 244.7 |
| Garage | 59.6 | 47.7 | 35.8 | 47.7 | 35.8 | 35.8 | 47.7 | 35.8 | 23.9 | 47.7 | 35.8 | 23.9 | 47.7 | 35.8 | 35.8 |
| Grocery | 894.6 | 835.0 | 811.1 | 799.2 | 739.5 | 727.6 | 703.7 | 656.0 | 632.2 | 632.2 | 596.4 | 584.5 | 489.0 | 453.3 | 441.3 |
| Manufacturing Facility | 59.6 | 47.7 | 35.8 | 47.7 | 35.8 | 35.8 | 47.7 | 35.8 | 23.9 | 35.8 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 |
| Office - Low Rise | 334.0 | 143.1 | 119.3 | 298.2 | 107.4 | 83.5 | 238.6 | 95.4 | 71.6 | 214.7 | 71.6 | 59.6 | 155.1 | 23.9 | 23.9 |
| Religious Building | 107.4 | 131.2 | 155.1 | 95.4 | 107.4 | 131.2 | 83.5 | 95.4 | 107.4 | 71.6 | 95.4 | 107.4 | 71.6 | 71.6 | 83.5 |
| Restaurant | 345.9 | 262.4 | 226.6 | 298.2 | 214.7 | 190.8 | 262.4 | 190.8 | 167.0 | 238.6 | 190.8 | 155.1 | 202.8 | 155.1 | 131.2 |
| Retail - Department Store | 298.2 | 178.9 | 167.0 | 274.3 | 155.1 | 131.2 | 238.6 | 131.2 | 119.3 | 214.7 | 131.2 | 107.4 | 178.9 | 107.4 | 95.4 |
| Retail - Strip Mall | 286.3 | 226.6 | 202.8 | 250.5 | 190.8 | 178.9 | 214.7 | 167.0 | 155.1 | 202.8 | 167.0 | 155.1 | 178.9 | 143.1 | 131.2 |

For example, a 10-ton rooftop heat pump on an office low rise building in Chicago installs DCV with 2-speed supply fan control (operating at 40% in ventilating mode and 90% in heating and cooling modes):

ΔkWh 	= (CapacityCool * Normalized Electric Cooling Energy Savings) + (CapacityHeat * Normalized Electric Heating Energy Savings)

= (10 tons × 1,065.8 kWh/ton) + (10 tons * 107.4)

= 11,732 kWh

###### Summer Coincident Peak Demand Savings

ΔkWssp	= (tons) × Normalized Electric Cooling Peak Demand Savings × CFssp

ΔkWpjm	= (tons) × Normalized Electric Cooling Peak Demand Savings × CFpjm

Where:

tons 	= capacity of the cooling equipment in tons (nominal tonnage may be used).

=Actual

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Normalized Electric Peak Demand Savings

= kW/ton savings value for the appropriate combination of building type, climate zone, and measure scenario per Table 6 – Electric Peak Demand Savings Summary (kW/ton)

Table 6 – Electric Peak Demand Savings Summary (kW/ton)

For example, a 10-ton rooftop air conditioner on an office low rise building in Chicago installs DCV with 2-speed supply fan control (operating at 40% in ventilating mode and 90% in heating and cooling modes) using the Summer System Peak Coincidence Factor:

ΔkW  = (10 tons) × (0.346 kW/ton) × 91.3%

= 3.159 kW

###### Natural Gas Savings

ΔTherms = (kBtuh output) × Normalized Gas Energy Savings

Where:

kBtuh 	= heating output of the gas furnace in kBtuh

= Actual

Normalized Gas Energy Savings

= Therms/kBtuh output savings value for the appropriate combination of building type, climate zone, and measure scenario per Table 7 – Gas Energy Savings Summary (Therms/kBtuh output)

Table 7 – Gas Energy Savings Summary (Therms/kBtuh output)

For example, a rooftop unit with a 148 kBtuh output gas furnace on an office low rise building in Chicago installs DCV with 2-speed supply fan control (operating at 40% in ventilating mode and 90% in heating and cooling modes):

ΔTherms 	= (148 kBtuh) × (0.9 Therms/kBtuh output)

= 133.2 Therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-ARTC-V02-200101

###### Review Deadline: 1/1/2023

### Advanced Thermostats for Small Commercial – Retired 12/31/2019. Replaced with 4.4.48 Small Commercial Thermostats

### Packaged RTU Sealing

###### Description

The HVAC Packaged RTU Sealing Measure targets areas of the RTU that are readily accessible and can be easily sealed.  By sealing the following areas, the amount of uncontrolled infiltration will be reduced leading to increased occupant comfort and an overall reduction in energy use.

The measure seeks to target the following three areas for sealing.

- Economizer Hood – Seal the interior and exterior seams that connect the economizer to the RTU using UL listed metal tape and/or silicone caulking.

- RTU Curb – Seal supply and return duct seams inside of RTU with mastic along with any leaks that are found around the perimeter of the roof to RTU connection using UL listed metal tape and/or silicone caulking.

- Non-Removable Cabinet Panels – Seal all cabinet seams that are not typically removed during basic service (i.e. control panel) using UL listed metal tape and/or silicone caulking.

Uncontrolled infiltration of non-conditioned outside air (OSA) is a known issue for packaged rooftop units (RTU). This leakage can occur thru the curb, economizer assembly connection and cabinet panels.  This leakage not only influences occupant comfort but also increases energy usage by increasing the heating and cooling loads while also reducing the unit’s operating energy efficiency.

Prior to a recently released laboratory and field study developed by Robert Mowris & Associates, Inc., the energy effects of uncontrolled infiltration through cabinet leakage were difficult to quantify. However, this study determined that uncontrolled OSA infiltration not only increases the amount of energy to condition the excess air but also reduces the unit’s operating efficiency (sensible EER) by 5.4%.  By reducing the amount of uncontrolled OSA infiltration through RTU sealing the unit’s operating efficiency (EER) can be increased reducing the amount of cooling energy. (Note: The referenced study quantifies improvements only from sealing the economizer hood – sealing the curb and non-access panels are recommended practice here but savings have not been quantified for these actions and may be in a future revision.)

This measure is only appropriate for packaged single zone rooftop units. Custom calculations are required for savings for built up air handling units or packaged multizone systems.

###### Definition of Efficient Equipment

The efficient equipment condition is assumed to be a packaged HVAC system that has had the economizer hood, curb and non-access cabinet panels sealed.

###### Definition of Baseline Equipment

The baseline equipment condition is assumed to be an operational packaged HVAC system that has not been previously sealed.  The packaged HVAC systems must be single zone and must have a functioning economizer.

###### Deemed Lifetime of Efficient Equipment

Because the measure targets existing packaged RTU units, the deemed lifetime of the measure is assumed to be 5 years.

###### Deemed Measure Cost

Actual measure costs should be used if available. If costs are not available the deemed measure cost below listed below can be used. The deemed measure costs are detailed for each individual RTU.

| Measure | Material Unit | Material Cost / Unit | Labor Unit (Hours) | Labor Rate / Unit | Total Cost |
| --- | --- | --- | --- | --- | --- |
| HVAC Packaged RTU Sealing | 1 | $48.99 | 1.5 | $97 | $194.49 |

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

To determine the savings associated with the Packaged RTU Sealing measure available IL TRM prototype eQuest models, which were initially created by the Energy Center of Wisconsin but modified by VEIC in 2014 as part of the IL TRM v4.0 Equivalent Full Load Hours (EFLH) update, were utilized. For each building type we used the most recent versions of the models for our baseline models (Assembly was not part of EFLH update).

This measure is targeting packaged single zone HVAC systems.  Therefore, as a basis for savings calculations, only models that had the following characteristics were chosen: 1) Packaged-Single Zone (PSZ) HVAC systems; and 2) aligned with the small commercial building type applicable to this measure.  Several modifications to the models were necessary in order to simulate a functioning airside economizer, which is assumed to be present in the baseline scenario for this measure:

- Optimized Economizer Controls by Climate Zone

  - Economizer Changeover Type – Set to fixed Dry Bulb

  - Economizer High-Limit Control Setpoints – Setpoints based on ASHRAE Climate Zones Fixed Dry Bulb Temperature recommendations.

  - Enable Integrated Operation – Allows economizer to operate simultaneously with mechanical cooling

To determine the energy use associated with an unsealed RTU, the prototype models were modified using the associated reduction in efficiency reported in a Robert Mowris and Associates, Inc. study that was performed for the California Public Utilities Commission in 2016. For further detail on the full modeled energy end use and savings summaries, see: “Packaged RTU Sealing_End Use Analysis_IL TRM 09042018.xlsx” spreadsheet.

After analyzing the modeled cooling annual energy usage for both the baseline (unsealed) and measure (sealed) model scenarios it was determined that the building type and climate zone variables had a minimal impact on the overall energy savings associated with the measure. As a result, the overall average savings factor of 4.67% was deemed applicable for any small commercial building type across all climate zones. This single savings value used in conjunction with the energy and demand savings calculations listed in the following sections will allow the savings to be calculated based on the unit size and equivalent full load hours listed in the Illinois Technical Resource Manual (TRM).

###### Electric Energy Savings

ΔkWh = (kBtu/hr) / EERbefore * EFLH * %Savings

Where:

kBtu/hr 	= rated capacity of the cooling equipment actually installed in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr).

=Actual

EERbefore	= Energy Efficiency Ratio (EER) of the baseline equipment

=Actual

%Savings 	= Deemed savings percentage

= 4.67%

EFLHcooling 	= IL TRM v6 Equivalent Full Load Hours (EFLH) for cooling are provided in the following table

| Building Type | Cooling EFLH |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Assembly | 725 | 796 | 937 | 1,183 | 932 |
| Assisted Living | 1,475 | 1,457 | 1,773 | 2,110 | 1,811 |
| College | 475 | 481 | 662 | 746 | 806 |
| Conditioned Storage (Warehouse) | 357 | 338 | 422 | 647 | 533 |
| Convenience Store | 1,088 | 1,067 | 1,368 | 1,541 | 1,371 |
| Garage | 934 | 974 | 1,226 | 1,582 | 1,383 |
| Grocery | 1,033 | 1,000 | 1,236 | 1,499 | 1,286 |
| Manufacturing Facility | 1,010 | 1,055 | 1,209 | 1,453 | 1,273 |
| Office - Low Rise | 949 | 1,010 | 1,182 | 1,452 | 1,281 |
| Religious Building | 861 | 817 | 967 | 1,159 | 1,067 |
| Restaurant | 1,074 | 1,134 | 1,279 | 1,627 | 1,325 |
| Retail - Department Store | 949 | 889 | 1,124 | 1,367 | 1,157 |
| Retail - Strip Mall | 950 | 919 | 1,149 | 1,351 | 1,215 |

For example, a 12 EER 5-ton rooftop air conditioner on a department store in Rockford receives packaged RTU sealing:

ΔkWh 	= (5*12) / 12 * 949 * 4.67%

= 221.6 kWh

###### Summer Coincident Peak Demand Savings

ΔkWssp	= (kBtu/hr) / EERbefore * %Savings * CFssp

ΔkWpjm	= (kBtu/hr) / EERbefore * %Savings * CFpjm

Where:

kBtu/hr 	= Capacity of the cooling equipment actually installed in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr).

=Actual

EERbefore	= Energy Efficiency Ratio (EER) of the baseline equipment

=Actual

%Savings 	= Deemed savings percentage

= 4.67%

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

For example, a 12 EER 5-ton rooftop air conditioner using the Summer System Peak Coincidence Factor receives RTU sealing:

ΔkW 	= (5*12) / 12 *  4.67% * 91.3%

= 0.213 kW

###### Natural Gas Savings

ΔTherm = (kBtu/hr) / 100 / Efficiencybefore * EFLH * %Savings

Where:

kBtu/hr 	= rated capacity of the heating equipment actually installed in kBtu per hour

=Actual

100	= Converts kBtu/hr to Therms/hr

Efficiencybefore	= Efficiency of the baseline equipment (rated)

=Actual

%Savings 	= Deemed savings percentages by building type and climate zone are provided in the following table

| Building Type | Savings Percentage |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Assembly | 2.84% | 2.86% | 2.86% | 2.98% | 2.94% |
| Assisted Living | 4.01% | 4.15% | 4.35% | 4.64% | 5.44% |
| College | 3.86% | 3.88% | 3.97% | 4.09% | 5.10% |
| Conditioned Storage (Warehouse) | 0.92% | 0.90% | 0.87% | 1.00% | 1.23% |
| Convenience Store | 3.07% | 3.20% | 3.43% | 3.70% | 4.63% |
| Garage | 0.20% | 0.21% | 0.22% | 0.23% | 0.29% |
| Grocery | 3.38% | 3.49% | 3.60% | 3.79% | 4.57% |
| Manufacturing Facility | 0.18% | 0.16% | 0.16% | 0.16% | 0.16% |
| Office - Low Rise | 2.19% | 2.23% | 2.37% | 2.46% | 2.96% |
| Religious Building | 0.28% | 0.28% | 0.30% | 0.31% | 0.37% |
| Restaurant | 2.76% | 2.83% | 2.96% | 3.11% | 3.58% |
| Retail - Department Store | 1.87% | 1.91% | 2.00% | 2.14% | 2.88% |
| Retail - Strip Mall | 2.06% | 2.12% | 2.29% | 2.46% | 3.17% |

EFLHheating 	= IL TRM v6 Equivalent Full Load Hours (EFLH) for heating are provided in the following table

| Building Type | Heating EFLH |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Assembly | 1,787 | 1,831 | 1,635 | 1,089 | 1,669 |
| Assisted Living | 1,683 | 1,646 | 1,446 | 1,063 | 1,277 |
| College | 1,530 | 1,430 | 1,276 | 709 | 849 |
| Conditioned Storage (Warehouse) | 1,338 | 1,098 | 976 | 771 | 810 |
| Convenience Store | 1,481 | 1,368 | 1,214 | 871 | 973 |
| Garage | 985 | 969 | 852 | 680 | 752 |
| Grocery | 1,608 | 1,602 | 1,404 | 876 | 1,047 |
| Manufacturing Facility | 1,048 | 1,013 | 939 | 567 | 634 |
| Office - Low Rise | 1,428 | 1,425 | 1,132 | 692 | 793 |
| Religious Building | 1,603 | 1,504 | 1,440 | 1,054 | 1,205 |
| Restaurant | 1,350 | 1,354 | 1,216 | 920 | 1,091 |
| Retail - Department Store | 1,123 | 979 | 852 | 697 | 689 |
| Retail - Strip Mall | 1,332 | 1,233 | 1,090 | 751 | 810 |

For example, a packaged RTU with an 80% efficient 150-kBtu/hr gas furnace on a department store in Rockford receives packaged RTU sealing:

ΔTherm 	= (150 / 100 ) / 80% * 1,123 * 1.87%

= 39.4 Therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-PRTU-V01-190101

###### Review Deadline: 1/1/2023

### Commercial Ground Source and Ground Water Source Heat Pump

###### Description

This measure characterizes the installation of a Ground Source Heat Pump under the following scenarios:

- New Construction:

  - The installation of a new Ground Source Heat Pump system meeting ENERGY STAR efficiency standards presented below in a new C&I building.

  - Note the baseline in this case should be determined via EM&V and the algorithms are provided to allow savings to be calculated from any baseline condition.

- Time of Sale:

  - The planned installation of a new Ground Source Heat Pump system meeting ENERGY STAR efficiency standards presented below to replace an existing system(s) that does not meet the criteria for early replacement described in section C below.

  - Note the baseline in this case is an equivalent replacement system to that which exists currently in the building.  Where unknown, the baseline should be determined via EM&V and the algorithms are provided to allow savings to be calculated from any baseline condition. The calculation of savings is dependent on whether an incentive for the installation has been provided by both a gas and electric utility, only an electric utility or only a gas utility.

  - DHW savings are calculated based upon the fuel type and efficiency of the existing unit.

- Early Replacement/Retrofit:

  - The early removal of functioning electric or gas space heating and/or cooling systems from service, prior to the natural end of life, and replacement with a new high efficiency Ground Source Heat Pump system.

  - Note the baseline in this case is the existing equipment being replaced. The calculation of savings is dependent on whether an incentive for the installation has been provided by both a gas and electric utility, only an electric utility or only a gas utility. DHW savings are calculated based upon the fuel and efficiency of the existing unit.

  - Early Replacement determination will be based on meeting the following conditions:

    - The existing unit is operational when replaced, or

    - The existing unit requires minor repairs to be operational, defined as costing less than:

| Existing System | Maximum repair cost |
| --- | --- |
| Air Source Heat Pump | $263/ton |
| Chiller | $308/ton |
| Boiler (Steam) | $3.87/ kBtu |
| Boiler (Hot Water) | $4.25/ kBtu |
| Furnace | $2.49/ kBtu |
| Ground Source Heat Pump | $2,185/ton |

    - All other conditions will be considered Time of Sale.

The Baseline efficiency of the existing unit replaced:

    - Use actual existing efficiency whenever possible.

    - If the efficiency of the existing unit is unknown, use assumptions based on the federal minimum standards provided in tables below.

    - If the operational status or repair cost of the existing unit is unknown use time of sale assumptions.

The installation of the GSHP should meet the following design parameters to ensure a properly sized circulation pump.  If the GSHP design does not meet the following parameters, a custom calculation should be performed to account for the motor energy consumed by the circulation pump.  Optimal design parameters are:

- Circulation pump is included in the manufacturer assembly of the GSHP system

Or;

- Circulation pump flow rate less than or equal to 3.0 GPM per system ton

- Variable flow controls on pumps serving systems greater than 10 tons.  Variable flow controls include one of the following:

  - A variable speed system pump controlled from differential pressure and 2-way water flow control valves on each heat pump.

  - Individual on/off pumps on each heat pump controlled by heat pump demand.  The heat pumps may be decoupled from the ground heat exchanger using a separate variable speed pump controlled by differential temperature across the ground loop.

- On/off or variable flow controls on pumps for systems less than 10 tons.  On/off pump controls shall operate only when heat pump(s) are running.

- System pumping head less than 80 feet.  For systems 10 tons or smaller system pumping head should not exceed 40 feet.

This measure was developed to be applicable to the following program types:  TOS, NC, EREP.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

For these products, the baseline equipment includes Air Conditioning, Space Heating and Domestic Hot Water Heating.

New Construction:

To calculate savings with an electric baseline, the baseline equipment is assumed to be an Air Source Heat Pump meeting the Federal Standard efficiency level as outlined in Table 2 (effective 1/1/2016 to 6/30/2019) or Table 7 (effective 7/1/2019); and a Federal Standard electric hot water heater efficiency level as outlined in Table 6 (effective 1/1/2016 to 6/30/2019) or Table 11 (effective 7/1/2019).

To calculate savings with a chiller/unitary cooling systems and boiler/furnace baseline, the baseline equipment is assumed to meet the minimum standard efficiencies as outlined in the Table 3 (effective 1/1/2016 to 6/30/2019) or Table 8 (effective 7/1/2019)

for chillers/unitary cooling systems, and Table 4 (effective 1/1/2016 to 6/30/2019) or Table 9 (effective 7/1/2019) for boilers or Table 5 (effective 1/1/2016 to 6/30/2019) or Table 10 (effective 7/1/2019) for furnaces. If a desuperheater is installed, the domestic hot water heater minimum standard efficiency is calculated as per Table 6 (effective 1/1/2016 to 6/30/2019) or Table 11 (effective 7/1/2019) below.

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

Table2: IECC 2015 ASHP Minimum Efficiency Requirements (effective 1/1/2016 to 6/30/2019):

Table 3: IECC 2015 Electric Chillers, Air-Cooled and Water-Cooled minimum efficiencies (effective 1/1/2016 to 6/30/2019)

Table 4: IECC 2015 Boiler minimum efficiency requirements (effective 1/1/2016 to 6/30/2019)

Table 5: IECC 2015 Warm-air Furnace minimum efficiency standards (effective 1/1/2016 to 6/30/2019)

Table 6: IECC 2015 Water Heaters mininmum performance (effective 1/1/2016 to 6/30/2019)

Table7: IECC 2018 ASHP Minimum Efficiency Requirements (effective 7/1/2019)

Table 7 continued:

Table 8: IECC 2018 Electric Chillers, Air-Cooled and Water-Cooled minimum efficiencies (effective 7/1/2019)

Table 9: IECC 2018 Boiler minimum efficiency requirements (effective 7/1/2019)

Note Code of Federal Regulations for gas -fired hot water boilers manufactured after January 15, 2021 require <300,000Btuh hot water boilers to be 84% AFUE and <300,000 Btuh steam boilers to be 82% AFUE (10 CFR 432(e)(3)). This should be assumed baseline from 1/1/2022.

Table 10: IECC 2018 Warm-air Furnace minimum efficiency standards (effective 7/1/2019)

Table 11: IECC 2018 Water Heaters mininmum performance (effective 7/1/2019)

Time of Sale: The baseline for this measure is a new replacement unit of the same system type as the existing unit, meeting the minimum standard efficiencies provided above.

Early replacement / Retrofit: The baseline for this measure is the efficiency of the existing heating, cooling and hot water equipment for the assumed remaining useful life of the existing unit, and a new baseline heating and cooling system for the remainder of the measure life (as provided in table above).

###### Deemed Lifetime of Efficient Equipment

The expected measure life of the ground source heat pump is assumed to be 25 years.

The expected measure life of the ground loop field is assumed to be 50 years.

For early replacement, the remaining life of existing equipment is assumed to be 6 years for ASHP and Central AC, 7 years for furnace, 8 years for boilers and GSHP, and 25 years for electric resistance.

###### Deemed Measure Cost

New Construction and Time of Sale: Incremental costs of the Ground Source Heat Pump should be used. This would be the actual installed cost of the Ground Source Heat Pump, well drilling, building retrofit, and system commissioning costs (default of $10,923 per ton), minus the assumed installation cost of the baseline equipment ($1,316 per ton for ASHP, or $12.43 per kBtu capacity for a new baseline efficient furnace or $19.33 per kBtu capacity for a new efficient steam boiler or $21.27 per kBtu capacity for a new efficient hot water boiler, and $1,539 per ton for new baseline chiller replacement).

Early Replacement: The actual installed cost of the Ground Source Heat Pump should be used (default cost for total system retrofit provided above). The assumed deferred cost (after 8 years) of replacing existing equipment with a new baseline unit is assumed to be $1,316 per ton for a new baseline Air Source Heat Pump, or $12.43 per kBtu capacity for a new baseline efficient furnace or $19.33 per kBtu capacity for a new efficient steam boiler or $21.27 per kBtu capacity for a new efficient hot water boiler and $1,539 per ton for new baseline chiller replacement. This future cost should be discounted to present value using the nominal societal discount rate.

###### Loadshape

Loadshape C04 – Commercial Electric Heating (if replacing building with no existing cooling)

Loadshape C05 - Commercial Electric Heating and Cooling

Note for the purpose of cost effectiveness screening for a fuel switch scenario, the heating kWh increase and cooling kWh decrease should be calculated separately such that the appropriate loadshape (i.e., Loadshape C04 - Commercial Electric Heating and Loadshape C03 – Commercial Cooling respectively) can be applied.

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.  Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings and Natural Gas Savings

Non-fuel switch measures:

ΔkWh 	= [Cooling savings] + [Heating savings] + [DHW savings]

Cooling Savings = (Capacitycool * EFLHCool * (1/EERbase – 1/EERGSHP))/1000

Heating Savings = (CapacityHeat * EFLHHeat * (1/HSPFbase – 1/(COPGSHP * 3.412)))/1000

DHW Savings = ElecDHW * (%DHW * ((1/EFelecbase) * HotWaterUseGallon * γWater * (Tout – Tin) * 1/3412))

Fuel switch measures:

Fuel switch measures must produce positive total lifecycle fuel savings (i.e., reduction in Btus at the premises) in order to qualify. This is determined as follows (note for early replacement measures the lifetime savings should be calculated by calculating savings for the remaining useful life of the existing equipment and for the remaining measure life):

SiteEnergySavings (MMBTUs)	= GasHeatReplaced + FurnaceFanSavings – GSHPSiteHeatConsumed + GSHPSiteCoolingImpact + GSHPSiteWaterImpact

GasHeatReplaced			= (HeatLoad * 1/AFUEbase) / 1,000,000

FurnaceFanSavings	= (FurnaceFlag * HeatLoad * 1/AFUEbase * Fe) / 1,000,000

GSHPSiteHeatConsumed	= (HeatLoad * 1/COPGSHP)/ 1,000,000

GSHPSiteCoolingImpact 	= (EFLHcool * CapacityCool * (1/EERbase– 1/EERGSHP)/1000 * 3412)/ 1,000,000

GSHPSiteWaterImpactGas = (%DHWDisplaced * ((1/EFGas * GPD * Household * 365.25 * γWater * (TOUT – Tin) * 1.0) / 1,000,000

GSHPSiteWaterImpactElectric =  (%DHWDisplaced * ((1/EFElec * GPD * Household * 365.25 * γWater * (TOUT – Tin) * 1.0 * 3412)/ 1,000,000

If SiteEnergySavings calculated above is positive, the measure is eligible.

The appropriate savings claim is dependent on which utilities are supporting the measure as provided in a table below:

| Measure supported by: | Electric Utility claims (kWh): | Gas Utility claims (therms): |
| --- | --- | --- |
| Electric utility only | SiteEnergySavings * 1,000,000/3,412 | N/A |
| Electric and gas utility (Note utilities may make alternative agreements to how savings are allocated as long as total MMBtu savings remains the same). | %IncentiveElectric * SiteEnergySavings * 1,000,000/3,412 | %IncentiveGas * SiteEnergySavings * 10 |
| Gas utility only | N/A | SiteEnergySavings * 10 |

Note for Early Replacement measures, the efficiency terms of the existing unit should be used for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 6 years for furnace, 8 years for boilers or GSHP, 15 years for electric resistance), and the efficiency terms for a new baseline unit should be used for the remaining years of the measure. See assumptions below.

Where:

Capacitycool 	= Cooling Output Capacity of Ground Source Heat Pump (Btu/hr)

= Actual installed

EFLHcool 		= Cooling Equivalent Full Load Hours

Dependent on building type and Existing Buildings or New Construction, provided in section 4.4 HVAC End Use

EERBase		= Energy Efficiency Ratio (EER) of existing cooling unit (kBtu/hr / kW).

For early replacement, use actual EER rating for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 8 years for GSHP). If EER unknown but SEER available, convert using the equation: EERexist = (-0.02 * SEERexist2) + (1.12 * SEERexist).

For TOS, NC, and the remaining measure life of early replacement, use minimum standard efficiencies as specified in tables in ‘Definition of Baseline Equipment’ section.

EERGSHP		= Part Load Energy Efficiency Ratio efficiency of efficient GSHP unit

= Actual installed

HeatLoad	= Calculated heat load for the building

= EFLHHeat * CapacityHeat

CapacityHeat 	= Heating Output Capacity of Ground Source Heat Pump (Btu/hr)

= Actual installed

EFLHHeat		= Heating Equivalent Full Load Hours of heat pump

Dependent on building type and Existing Buildings or New Construction, provided in section 4.4 HVAC End Use

HSPFBase		= Heating System Performance Factor of baseline electric heating system (kBtu/kWh)

For early replacement, use actual EER rating for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 8 years for GSHP or 15 years for electric resistance). For electric resistance, assume 3.41..

For TOS, NC, and the remaining measure life of early replacement, use minimum standard efficiencies as specified in tables in ‘Definition of Baseline Equipment’ section.

COPGSHP 		= Part Load Coefficient of Performance of efficient GSHP

= Actual installed

3.412 	= Constant to convert the COP of the unit to the Heating Season Performance Factor (HSPF)

ElecDHW 		= 1 if building has electric DHW

= 0 if building has non electric DHW

= 0 if one to one replacement of existing Ground Source Heat Pump

%DHW 	= Percentage of total DHW load that the GSHP will provide

= Actual if known

= If unknown and if desuperheater installed, assume 44%

= 0% if no desuperheater installed

EFelecbase 		= Energy Factor of baseline electric DHW

= Actual. If unknown or for new construction, assume federal standard as defined in applicable table in ‘Definition of Baseline Equipment’ section.

HotWaterUseGallon  = Estimated annual hot water consumption (gallons)

= Actual if possible to provide reasonable custom estimate. If not, two methodologies are provided to develop an estimate:

- Consumption per usable storage tank capacity

= Capacity * Consumption/cap

Where:

Capacity	= Usable capacity of hot water storage tank in gallons

= Actual

Consumption/cap = Estimate of consumption per gallon of usable tank capacity, based on building type:

| Building Type | Consumption/Cap |
| --- | --- |
| Convenience | 528 |
| Education | 568 |
| Grocery | 528 |
| Health | 788 |
| Large Office | 511 |
| Large Retail | 528 |
| Lodging | 715 |
| Other Commercial | 341 |
| Restaurant | 622 |
| Small Office | 511 |
| Small Retail | 528 |
| Warehouse | 341 |
| Nursing | 672 |
| Multi-Family | 894 |

- Consumption per unit area by building type

= (Area/1000) * Consumption/1,000 sq.ft.

Where:

Area  	= Area in sq.ft that is served by DHW boiler

= Actual

Consumption/1,000 sq.ft. = Estimate of DHW consumption per 1,000 sq.ft. based on building type:

| Building Type | Consumption/1,000 sq.ft. |
| --- | --- |
| Convenience | 4,594 |
| Education | 7,285 |
| Grocery | 697 |
| Health | 24,540 |
| Large Office | 1,818 |
| Large Retail | 1,354 |
| Lodging | 29,548 |
| Other Commercial | 3,941 |
| Restaurant | 44,439 |
| Small Office | 1,540 |
| Small Retail | 6,111 |
| Warehouse | 1,239 |
| Nursing | 30,503 |
| Multi-Family | 15,434 |

γWater	 	= Density of water

= 8.33 pounds per gallon

Tout  		= Tank temperature

= 125°F

Tin 		= Incoming water temperature from well or municiplal system

= 50.7°F

1		= Heat Capacity of water (1 Btu/lb*°F)

3.412		= Conversion from Btu to kWh

AFUEbase	= Baseline Annual Fuel Utilization Efficiency Rating.

For early replacement measures, use actual AFUE rating for the remaining useful life of the existing equipment (6 years for furnace, 8 years for boilers).

For TOS, NC, and the remaining measure life of early replacement, use minimum standard efficiencies as specified in tables in ‘Definition of Baseline Equipment’ section.

FurnaceFlag	= 1 if system replaced is a gas furnace, 0 if not.

Fe		= Furnace Fan energy consumption as a percentage of annual fuel consumption

= 7.7%

EFGasBase		= Energy factor of Baseline natural gas DHW heater

= Actual. If unknown or New Construction, assume federal standard as defined in applicable table in ‘Definition of Baseline Equipment’ section.

3412		= Btu per kWh

%IncentiveElectric	= % of total incentive paid by electric utility

= Actual

%IncentiveGas		= % of total incentive paid by gas utility

= Actual

Non Fuel Switch Illustrative Examples

New Construction using ASHP baseline:

For example, a 10 ton closed loop unit with Part Load EER rating of 20 and Part Load COP of 4.4, with desuperheater installed, and with a 100 gallon electric water heater in an Assisted living building in Chicago:

ΔkWh 	= [120,000 * 1,457 * (1/11 – 1/20) / 1000] + [1,646* 120,000 * (1/11 – 1/(4.4*3.412)) / 1000]  + [1 * 0.44 * ((1/0.9568 * (100*672) * 8.33 * (125-50.7) * 1)/3412)]

= 7,153 + 4,800 +5,606  = 17,559 kWh

Early Replacement:

For example, a 10 ton closed loop unit with Part Load EER rating of 20 and Part Load COP of 4.4 and with desuperheater installed in in an Assisted living building in Chicago with a 100 gallon electric water heater, replacing an existing working Air Source Heat Pump with efficiency ratings of 8.2 EER and 7.7 HSPF:

ΔkWH for remaining life of existing unit (1st 8 years):

= [120,000 * 1,457 * (1/8.2 – 1/20) / 1000] + [1,646* 120,000 * (1/7.7 – 1/(4.4*3.412)) / 1000]  + [1 * 0.44 * ((1/0.9568 * (100*672) * 8.33 * (125-50.7) * 1)/3412)]

= 12,580 + 12,495 +5606  = 30,681 kWh

ΔkWH for remaining measure life (next 17 years):

= [120,000 * 1,457 * (1/11 – 1/20) / 1000] + [1,646* 120,000 * (1/11 – 1/(4.4*3.412)) / 1000]  + [1 * 0.44 * ((1/0.9568 * (100*672) * 8.33 * (125-50.7) * 1)/3412)]

= 7,153 + 4,800 +5,606  = 17,559 kWh

Fuel Switch Illustrative Example

[for illustrative purposes a 50:50 Incentive is used for joint programs]

Early Replacement fuel switch:

A 10 ton closed loop unit with Part Load EER rating of 20 and Part Load COP of 4.4 in an Assisted Living building in Chicago with a 100 gallon gas water heater replaces an existing working natural gas boiler with 75% efficiency and central AC of 9.5 EER, and desuperheater installed with natural gas existing DHW heater:

LifetimeSiteEnergySavings (MMBTUs)	=  LifetimeGasHeatReplaced + LifetimeFurnaceFanSavings – LifetimeGSHPSiteHeatConsumed + LifetimeGSHPSiteCoolingImpact + LifetimeGSHPSiteWaterImpact

LifetimeGasHeatReplaced		= ((HeatLoad * 1/AFUEexist) / 1,000,000 * 8 years) + ((HeatLoad * 1/AFUEbase) / 1,000,000 * 17 years)

= ((120,000 * 1,646 * 1/0.75) / 1,000,000 * 8) + ((120,000 * 1,646 * 1/0.8) / 1,000,000 * 17)

= 6304.2 MMBtu

LifetimeFurnaceFanSavings	= ((FurnaceFlag * HeatLoad * 1/AFUEexist * Fe) / 1,000,000 * 8 years) + ((FurnaceFlag * HeatLoad * 1/AFUEbase * Fe_New) / 1,000,000 * 17 years)

= 0 MMBtu

LifetimeGSHPSiteHeatConsumed	= (HeatLoad * 1/COPGSHP) / 1,000,000 * 25 years

= (120,000 * 1,646 * 1/4.4)/1,000,000 * 25

= 1122.3 MMBtu

Fuel Switch Illustrative Example continued

LifetimeGSHPSiteCoolingImpact 	= (((EFLHcool * CapacityCool * (1/EERexist – 1/EERGSHP))/1000 * 3412) / 1,000,000 * 6 years) + (((EFLHcool * CapacityCool * (1/EERbase– 1/EERGSHP))/1000 * 3412) / 1,000,000 * 19 years)

= (((120000 * 1,457 * (1/9.5 – 1/20)) / 1000 * 3412)/1,000,000 * 6) + (((120000 * 1,457 *  (1/11 – 1/20)) / 1000) * 3412)/1,000,000 * 19)

= 661.5 MMBtu

LifetimeGSHPSiteWaterImpactGas =  ((%DHWDisplaced * ((1/EFGas * GPD * Household * 365.25 * γWater * (TOUT – Tin) * 1.0) / 1,000,000) * 25 years

= (0.44 * (1/ 0.8 * (100*672) * 8.33 * (125-50.7) * 1) / 1,000,000) * 25

= 571.9 MMBtu

LifetimeSiteEnergySavings (MMBTUs) = 6304.2 + 0 – 1122.3 + 661.5 + 571.9   = 6,415 MMBtu [Measure is eligible]

First 6 years:

SiteEnergySavings_FirstYear (MMBTUs)	=  GasHeatReplaced + FurnaceFanSavings – GSHPSiteHeatConsumed + GSHPSiteCoolingImpact + GSHPSiteWaterImpact

GasHeatReplaced	= (HeatLoad * 1/AFUEexist) / 1,000,000

= (120,000 * 1,646 * 1/0.75) / 1,000,000

= 263.4 MMBtu

FurnaceFanSavings	= (FurnaceFlag * HeatLoad * 1/AFUEexist * Fe) / 1,000,000

= 0 MMBtu

GSHPSiteHeatConsumed	= (HeatLoad * 1/COPGSHP) / 1,000,000

= (120,000 * 1,646 * 1/4.4)/ 1,000,000

= 44.9 MMBtu

GSHPSiteCoolingImpact 	= ((EFLHcool * CapacityCool * (1/EERexist– 1/EERGSHP))/1000 * 3412)/1,000,000

= ((120000 * 1,457 * (1/9.5 – 1/20)) / 1000 * 3412)/1,000,000

= 33.0 MMBtu

GSHPSiteWaterImpactGas =  (%DHWDisplaced * ((1/EFGas * GPD * Household * 365.25 * γWater * (TOUT – Tin) * 1.0) / 1,000,000

= (0.44 * (1/ 0.8 * (100*672) * 8.33 * (125-50.7) * 1) / 1,000,000

= 22.9 MMBtu

SiteEnergySavings_FirstYear (MMBTUs) = 263.4 + 0 – 44.9 + 33 + 22.9   = 274.4 MMBtu

Fuel Switch Illustrative Example continued

Remaining 10 years:

SourceEnergySavings_PostAdj (MMBTUs)	=  GasHeatReplaced + FurnaceFanSavings – GSHPSourceHeatConsumed + GSHPSourceCoolingImpact + GSHPSourceWaterImpact

GasHeatReplaced	= (HeatLoad * 1/AFUEexist) / 1,000,000

= (120,000 * 1,646 * 1/0.8) / 1,000,000

= 246.9 MMBtu

FurnaceFanSavings	= (FurnaceFlag * HeatLoad * 1/AFUEexist * Fe) / 1,000,000

= 0 MMBtu

GSHPSiteHeatConsumed	= (HeatLoad * 1/COPGSHP) / 1,000,000

= (120,000 * 1,646 * 1/4.4)/ 1,000,000

= 44.9 MMBtu

GSHPSiteCoolingImpact 	= ((EFLHcool * CapacityCool * (1/EERexist– 1/EERGSHP))/1000 * 3412)/1,000,000

= ((120000 * 1,457 * (1/11 – 1/20)) / 1000 * 3412)/1,000,000

= 24.4 MMBtu

GSHPSiteWaterImpactGas =  (%DHWDisplaced * ((1/EFGas * GPD * Household * 365.25 * γWater * (TOUT – Tin) * 1.0) / 1,000,000

= (0.44 * (1/ 0.8 * (100*672) * 8.33 * (125-50.7) * 1) / 1,000,000

= 22.9 MMBtu

SourceEnergySavings_PostAdj (MMBTUs) = 246.9 + 0 – 44.9 + 24.4 + 22.9   = 249.3 MMBtu

Savings would be claimed as follows:

| Measure supported by: | Electric Utility claims: | Gas Utility claims: |
| --- | --- | --- |
| Electric utility only | First 6 years: 274.4 * 1,000,000/3412 = 80,422 kWh Remaining 10 years: 249.3 * 1,000,000/3412 = 73,066 kWh | N/A |
| Electric and gas utility | First 6 years: 0.5 * 274.4 * 1,000,000/3412 = 40,211 kWh Remaining 10 years: 0.5 * 249.3 * 1,000,000/3412 = 36,533 kWh | First 6 years: 0.5 * 274.4 * 10 = 1372 Therms Remaining 10 years: 0.5 * 249.3 * 10 = 1247 Therms |
| Gas utility only | N/A | First 6 years: 274.4 * 10 = 2744 Therms Remaining 10 years: 249.3 * 10 = 2493 Therms |

###### Summer Coincident Peak Demand Savings

ΔkW = (CapacityCool * (1/EERbase - 1/EERGSHP))/1000 * CF

Where:

CFSSP  	= Summer System Peak Coincidence Factor for Central A/C (during system peak hour)

= 91.3%

CFPJM	= PJM Summer Peak Coincidence Factor for Central A/C (average during peak period)

= 47.8%

New Construction or Time of Sale:

For example, a 10 ton closed loop unit with Full Load EER rating of 20:

ΔkWSSP 	= (120,000 * (1/11 – 1/20))/1000 * 0.913

= 4.482kW

ΔkWPJM 	= (36,000 * (1/11 – 1/20))/1000 * 0.478

= 2.347kW

Early Replacement:

For example, a 10 ton closed loop unit with Full Load 20 EER replaces an existing working Air Source Heat Pump with 8.2 EER:

ΔkWSSP for remaining life of existing unit (1st 8 years):

= (120,000 * (1/8.2 – 1/20))/1000 * 0.913

= 7.883 kW

ΔkWSSP for remaining measure life (next 17 years):

= (120,000 * (1/11– 1/20))/1000 * 0.913

= 4.482kW

ΔkWPJM for remaining life of existing unit (1st 8 years):

= (120,000 * (1/8.2 – 1/20))/1000 * 0.478

= 4.127 kW

ΔkWPJM for remaining measure life (next 17 years):

= (120,000 * (1/11 – 1/20))/1000 * 0.478

= 2.347kW

###### Natural Gas Savings

Calculation provided together with Electric Energy Savings above.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Cost Effectiveness Screening and Load Reduction Forecasting when Fuel Switching

This measure can involve fuel switching from gas to electric.

For the purposes of forecasting load reductions due to fuel switch GSHP projects; changes in site energy use at the customer’s meter (using ΔkWh algorithm below) adjusted for utility line losses (at-the-busbar savings), customer switching estimates, NTG, and any other adjustment factors deemed appropriate, should be used.

The inputs to cost effectiveness screening should reflect the actual impacts on the electric and fuel consumption at the customer meter and, for fuel switching measures, this will not match the output of the calculation/allocation methodology presented in the “Electric Energy Savings” and “Natural Gas Savings” sections above. Therefore in addition to the calculation of savings claimed, the following values should be used to assess the cost effectiveness of the measure. For Early Replacement measures, the efficiency terms of the existing unit should be used for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 7 years for furnace, 8 years for boilers or GSHP, 15 years for electric resistance), and the efficiency terms for a new baseline unit should be used for the remaining years of the measure.

ΔTherms	= [Heating Consumption Replaced] + [DHW Savings if existing natural gas DHW]

= [(HeatLoad * 1 AFUEbase)/ 100,000] + [(1 – ElecDHW) * %DHW * (1/ EFGasBase * HotWaterUseGallon * γWater * (TOUT – Tin) * 1.0) / 100,000)]

ΔkWh 	= [FurnaceFanSavings] - [GSHP heating consumption] + [Cooling savings] + [DHW savings if existing electric DHW]

= [FurnaceFlag * HeatLoad * 1/AFUEbase * Fe * 0.000293] - [(HeatLoad * (1/ COPGSHP  * 3.412))/1000] + [(EFLHcool * CapacityCool * (1/EERbase  - 1/EERGSHP))/1000] + [ElecDHW * %DHW * ((1/EFELEC * HotWaterUseGallon * γWater * (TOUT – Tin) * 1.0) / 3412)]

Illustrative Example of Cost Effectiveness Inputs for Fuel Switching:

For example, a 10 ton unit with Part Load EER rating of 20 and Part Load COP of 4.4 in an Assisted living building in Chicago with a 100 gallon gas water heater replaces an existing working natural gas boiler with 75% efficiency and air-cooled chiller of 9.5 EER. [Note the calculation provides the annual savings for the first 8 years of the measure life, an additional calculation (not shown) would be required to calculated the annual savings for the remaining life (years 9-25)]:

ΔTherms	=[HeatLoad * 1 AFUEbase)/ 100,000] + [(1 – ElecDHW) * %DHW * (1/ EFGasBase * HotWaterUseGallon * γWater * (TOUT – Tin) * 1.0) / 100,000)]

= [(120,000 * 1,646 * 1/0.75)/100,000] + [((1 - 0) * 0.44 * (1/0.8 * (100*672) * 8.33 * (125- 50.7) * 1 )/100000)]

= 2,634 + 229

= 2,863 therms

ΔkWh 	= [FurnaceFlag * HeatLoad * 1/AFUEbase * Fe * 0.000293] - [(HeatLoad * (1/ COPGSHP  * 3.412))/1000] + [(EFLHcool * CapacityCool * (1/EERbase  - 1/EERGSHP))/1000] + [ElecDHW * %DHW * ((1/EFELEC * HotWaterUseGallon * γWater * (TOUT – Tin) * 1.0) / 3412)]

= 0 - [(1646 * 120000 * (1/ 4.4  * 3.412))/1000] + [( 1457* 120000 * (1/11  - 1/20))/1000] + [0 * (0.44 * ((1/0.9568) * (100*672) * 8.33 * (125 - 50.7) * 1 /3412))]

= 0 - 153,168 + 7153 + 0

=  -146,015 kWh

###### Measure Code:  CI-HVC-GSHP-V05-220101

###### Review Deadline: 1/1/2025

### Adsorbent Air Cleaning

###### Description

The Adsorbent Air Cleaning (AAC) measure installs modular adsorbent air cleaning devices ("AAC modules") into commercial forced air HVAC systems. These devices pass return air through adsorbent media which remove the gas-phase contaminants carbon dioxide and species of volatile organic compounds (VOCs) from the return air, allowing it to be recirculated rather than removed from the building as exhaust and replaced with ventilation air. This allows HVAC system operators to substantially reduce the amount of outside air brought in for ventilation while still maintaining acceptable indoor air quality, resulting in heating and cooling energy savings. An energy penalty is incurred due to the operation of fans integrated within the AAC modules, as well as from integrated electric heaters used in a regeneration cycle which purges the adsorbent media of contaminants to allow them to be used again. Net energy savings are calculated and are equal to the cooling and heating energy savings due to reduced outdoor air minus the energy required to operate the AAC modules.

This measure serves the market for medium to large commercial and institutional buildings.

This measure is currently applicable to the following program types: NC, RF, DI. If applied to other program types, the measure savings should be verified.

###### Definition Of Efficient Equipment

Efficient equipment is defined as a commercial HVAC system which has AAC modules installed in the return airstream, with the number of modules determined by appropriate sizing calculations. The modules allow for a substantial reduction in the volume of outside air introduced to the building compared to systems without AAC modules.

###### Definition Of Baseline Equipment

Baseline equipment is a variable air volume HVAC system equipped with an integrated economizer and which does not have AAC modules installed. Heating is provided by either electricity, natural gas, or heat pump.

###### Deemed Lifetime Of Efficient Equipment

The expected measure life for HVAC applications is 20 years.

###### Deemed Measure Cost

Actual measure costs should be used if available. If costs are not available, the deemed measure cost below can be used, which is based on a cost per cfm of supply air flow rate.

| Unit | Material Cost / Unit ($/cfm) | Labor Cost / Unit ($/cfm) | Total Cost / Unit ($/cfm) |
| --- | --- | --- | --- |
| Supply Air CFM | $0.90 | $0.48 | $1.38 |

For example, the default deemed measure cost of installing the AAC measure in an HVAC system with a design supply air flow rate of 75,000 cfm is:

Deemed Measure Cost ($) = 75,000 cfm * $1.38/cfm = $103,500

###### Loadshape

For buildings with gas heat:

Loadshape C03 – Commercial Cooling

For buildings with electric heat:

Loadshape C05 – Commercial Electric Heating and Cooling

###### Coincidence Factor

The concidence factor is assumed to be the PJM Summer Peak Coincidence Factor for Commercial Cooling:

CFPJM = 47.8%

Algorithm

###### Calculation of Energy Savings

Savings associated with the Adsorbent Air Cleaning measure were derived from the results of a pilot study conducted in a commercial office building in Chicago during the 2019-2020 cooling and heating seasons. The building had a VAV system with economizer and electric heat. During the study, outdoor air rates were reduced according to the AAC module manufacturer's recommendations. Building cooling and heating loads associated with preconditioning outdoor air were continuously measured both with baseline and reduced outdoor air flow rates over a range of outdoor air temperatures and humidities. Statistical models were developed to predict energy and peak electric load savings as a function of outdoor air flow rate and outdoor air conditions. The models were then used to simulate energy use and peak load savings in other Illinois climate zones using TMY data.

In addition to monitoring cooling and heating energy, the pilot study also measured the electricity used to operate the AAC modules for the duration of the cooling and heating seasons. This energy penalty was subtracted from the cooling and heating load savings to calculate net savings.

###### Electric Energy Savings

Identify the building's heating fuel. Electric energy savings will differ for buildings with natural gas, electric resistance, or electric heat pumps as a heating fuel.

For buildings with natural gas as a heating fuel, electric energy savings are:

ΔkWh = ΔVOA * (NCLS / CoolingCOP – Annual ElectricAAC)

For buildings with electric resistance as a heating fuel, electric energy savings are:

ΔkWh = ΔVOA * (NCLS / CoolingCOP + NHLS – Annual ElectricAAC)

For buildings with electric heat pumps as a heating fuel, electric energy savings are:

ΔkWh = ΔVOA * (NCLS / CoolingCOP + NHLS / HeatingCOP – Annual ElectricAAC)

Where:

ΔVOA	= reduction in minimum outside air flow in scfm due to incorporating an AAC                             module

= if the rate is unknown, calculate using the following equation:

ΔVOA = Vsupply * FOA * FR, where:

Vsupply	= design or operational peak supply air flow rate of air handler in scfm

FOA	= operational minimum fraction of outside air in supply airflow before installing AAC modules

FR		= percentage reduction of outside air due to AAC modules

= custom; if unknown, use 0.7 as a default

NCLS (Normalized Cooling Load Savings)

= ΔkWh/Δscfm savings value for the appropriate climate zone in the table below:

| Normalized Cooling Load Savings (kWh/cfm) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Rockford – Zone 1 | Chicago – Zone 2 | Springfield – Zone 3 | Mt. Vernon/Belleville – Zone 4 | Marion – Zone 5 |
| 17.9 | 18.6 | 24.2 | 26.5 | 23.6 |

NHLS (Normalized Heating Load Savings)

= ΔkWh/Δscfm savings value for the appropriate climate zone and FOA in the table below:

| FOA | Normalized Heating Load Savings (kWh/cfm) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Rockford – Zone 1 | Chicago – Zone 2 | Springfield – Zone 3 | Mt. Vernon/Belleville – Zone 4 | Marion – Zone 5 |
| 0.10 | 2.24 | 1.13 | 1.09 | 0.76 | 0.95 |
| 0.15 | 3.32 | 1.94 | 2.14 | 1.72 | 1.81 |
| 0.20 | 3.90 | 2.44 | 2.76 | 2.28 | 2.37 |
| 0.25 | 4.31 | 2.80 | 3.09 | 2.53 | 2.68 |
| 0.30 | 4.54 | 3.05 | 3.25 | 2.68 | 2.85 |

CoolingCOP	= seasonal average COP of building cooling plant. If unknown, use 4.0 as a default

HeatingCOP	= seasonal average COP of heat pump. If unknown, use 2.5 as a default

Annual ElectricAAC	= annual electricity consumed by AAC modules for the appropriate climate zone

| AAC Electricity Consumption (kWh/cfm) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Rockford – Zone 1 | Chicago – Zone 2 | Springfield – Zone 3 | Mt. Vernon/Belleville – Zone 4 | Marion – Zone 5 |
| 1.07 | 0.91 | 1.06 | 0.98 | 0.89 |

For example, office building in Climate Zone 3 is equipped with a VAV system with electric heat and has a cooling plant COP of 4.0, a design supply air flow rate of 50,000 scfm and an outdoor air ventilation rate of 10,000 scfm. Installing AAC modules will allow reduction of the outdoor air ventilation rate by 70%. In this case:

Vsupply = 50,000 scfm

FOA = 10,000 scfm / 50,000 scfm = 0.2

FR = 0.7

ΔVOA  = Vsupply * FOA * FR = 50,000 scfm * 0.2 * 0.7 = 7,000 scfm

Normalized Cooling Load Savings = 24.2 kWh/scfm (Climate zone 3, FOA = 0.2)

CoolingCOP = 4.0

Normalized Heating Load Savings = 2.76 kWh/scfm (Climate zone 3, FOA = 0.2)

Annual ElectricAAC = 1.06 kWh/scfm (Climate zone 3)

ΔkWh = ΔVOA * (NCLS / CoolingCOP + NHLS – Annual ElectricAAC)

= 7,000 scfm * (24.2 kWh/scfm / 4.0 + 2.76 kWh/scfm – 1.06 kWh/scfm)

= 54,250 kWh

###### Summer Coincident Peak Demand Savings

ΔkW = ΔVOA * (Normalized Peak Cooling Load Savings / CoolingCOP) * CFPJM

Where:

CFPJM	= 0.478

Normalized Peak Cooling Load Savings

= ΔkW/Δscfm savings value for the appropriate combination of building type, climate zone, and measure scenario, as detailed in the table below

| Normalized Peak Cooling Load Savings (kW/cfm) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Rockford – Zone 1 | Chicago – Zone 2 | Springfield – Zone 3 | Mt. Vernon/Belleville – Zone 4 | Marion – Zone 5 |
| 0.0259 | 0.0256 | 0.0296 | 0.0293 | 0.0283 |

###### Natural Gas Savings

Natural gas savings do not apply to buildings where electricity is the heating fuel. For buildings where natural gas is the heating fuel:

Δtherms = ΔVOA * (NHLS / η) * 0.03412

Where:

η	= efficiency of gas heating equipment. If unknown, use 0.78 as default.

0.03412		= therms per kWh. Conversion factor to convert kWh to therms

###### Measure Code: CI-HVC-ADAC-V03-210101

###### Review Deadline: 1/1/2023

### Server Room Temperature Set back

###### Description

This measure involves adjusting existing thermostats or building automation systems for reduced cooling energy consumption and fan energy consumption in server room and/or data center spaces. Existing set points should be documented through an audit or retro-commissioning study. A maximum temperature adjustment of 95°F will limit significant increase in server fan power consumption.

This measure was developed to be applicable to the following program types: RF, DI

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The criteria for this measure is established by optimizing the cooling temperature setpoint with a commercial thermostat or building automation system, up to a maximum of 95°F, which is adjusted to meet or approach ASHRAE recommended standards for data center cooling.

###### Definition of Baseline Equipment

The baseline for this measure is a commercial thermostat or building automation system that is currently controlling to cooling temperature setpoints that do not align with ASHRAE TC 9.9.

###### Deemed Lifetime of Efficient Equipment

The expected measure life of a programmable thermostat is assumed to be 8 years. For the purposes of claiming savings for an adjustment of an existing thermostat, this is reduced to a 50% persistence factor to give a final measure life of 4 years. It is recommended that this assumption be evaluated by future energy measurement and verification activities.

###### Deemed Measure Cost

Actual labor costs should be used if the implementation method allows. If unknown the labor cost for this measure is assumed to be $35.24 per thermostat, as summarized in the following table.

| Measure | Units | Materials | Labor | Total Cost (including O&P) | City Cost Index (Install Only)* | Total | Source |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Adjust Temperature Set Points | 4 | $0.00 | $5.95 | $6.55 | 134.5% | $35.24 | RS Means 2010 (pg 255, Section 23-09-8100) |
| * Chicago, IL - Division 23 |  |  |  |  |  |  |  |

###### Loadshape

Loadshape C03 – Commercial Cooling

###### Coincidence Factor

Since the server room is cooled 8760 hours, the summer peak coincidence factor is assumed to be 100%.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh	= Capacity * (1/EER) * EFLH * LF * %Savings * (Tafter - Tbefore)

Where:

Capacity	= Capacity of the cooling equipment actually installed in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr)

= Actual

EER	= Energy efficiency ratio of the equipment

= Actual

EFLH	= Equivalent full load hours for cooling

= 8,760

LF	= Load Factor,

= 65%

%Savings	= Deemed percent savings

= 4% per degree increase

Tafter	= Space temperature setpoint after adjustment, maximum of 95°F

= Actual

Tbefore	= Space temperature setpoint before adjustment

= Actual

###### Summer Coincident Peak Demand Savings

ΔkW	= Capacity * (1/EER) * LF * %Savings * (Tafter - Tbefore) * CF

Where:

CF		= Summer Peak Coincidence Factor for measure

= 1.0

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-SRSB-V01-200101

###### Review Deadline: 1/1/2024

### Air Deflectors for Unit Ventilators – Provisional Measure

###### Description

Unit ventilators (UVs) are the primary means of space conditioning found in schools, meeting rooms, offices, and other areas where local codes require controlled ventilation based on occupancy density. UVs are capable of heating, cooling, and ventilating a space using steam, hot water, electric heating, chilled water, or remote direct expansion cooling.

UVs have historically been placed next to perimeter exterior windows to serve as a draft stop while also conditioning and ventilating the space. As building envelopes become tighter and windows become better insulated, the draft stop function of UVs has diminished while their positioning under large windows exacerbates unwelcome space heating effects. Air delivered upward from UVs does not mix well with air in the room and creates air stratification. Warmer air stays near ceilings and cooler air stagnates near floors. Longer equipment runtimes are now required to satisfy thermostat setpoints resulting in wasted energy.

Installing supply air deflectors for unit ventilators (ADUVs) improve air mixing and reduce stratification issues for UVs resulting in improved comfort and lower energy consumption. This product is applicable for ChildCare/Pre-school, College/University, Elementary School, High School/Middle School, and Office – Low/Mid Rise with existing UVs.

In addition, deflectors should not be installed on unit on South facing walls as South-facing windows are known to have a higher solar gain, which naturally drives air convection in a room.

This measure was developed to be applicable to the following program types: RF, DI.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment consists of UVs on North, East or West facing walls with supply air deflectors mounted over existing unit ventilators utilizing an angled grille to direct airflow from the unit ventilator into the center of a room.

###### Definition of Baseline Equipment

The baseline equipment is a UV located adjacent to exterior north, east, and west-facing perimeter windows with no existing technology to address air stratification installed. UVs located adjacent to south-facing perimeter windows are not eligible for this measure.

###### Deemed Lifetime of Efficient Equipment

While simple metal deflectors will last indefinitely, it is unknown whether they will remain effectively installed and/or transferred to new unit ventilators when they are replaced.  The expected measure life is estimated at 20 years.

###### Deemed Measure Cost

The measure cost for retrofit or direct installation on an existing unit ventilator is assumed to be the full cost for materials and labor and is estimated at $250 per unit.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

Annual natural gas savings for this measure are deemed at 55 therms/yr per UV unit.

The measured savings are extrapolated to other climate zones of Illinois. The savings are extrapolated based on HDD stipulated in Illinois TRM v7.0.

| Climate Zone | HDD | Formula: Deemed Natural Gas Savings * (HDD/HDDChicago) | Natural Gas Savings (therms/yr) |
| --- | --- | --- | --- |
| 1 (Rockford) | 4,272 | 55 * (4,272/4,029) | 58 |
| 2 (Chicago) | 4,029 | 55 * (4,029/4,029) | 55 |
| 3 (Springfield) | 3,406 | 55 * (3,406/4,029) | 46 |
| 4 (Belleville) | 2,515 | 55 * (2,515/4,029) | 34 |
| 5 (Marion) | 2,546 | 55 * (2,546/4,029) | 35 |

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-ADUV-V01-200101

###### Review Deadline: 1/1/2023

### Small Commercial Thermostats

###### Description

This measure characterizes the energy savings from the installation of either a Programmable or an advanced Thermostat to reduce heating and cooling consumption in a small commercial building.

The thermostat must be installed to control a single-zone HVAC system. This measure is limited to packaged HVAC units 10 tons or less. This measure should not be used when HVAC systems are being replaced, in new construction and whenever code compliance is required.

The savings associated with small commercial installations of thermostats had not been well evaluated at the time this measure was created for TRM Version 8.0. In the absence of assumptions specific to small commercial customers, the percent savings derived from Illinois Residential evaluations were used. In version 9.0 the cooling savings percentage was updated based on research conducted on small commercial programmable thermostat applications. In CY2020, additional research was performed to support a potential update to the heating savings percentage. The results did not provide a sufficient statistically significant basis for changing the current assumption.

Note that while these devices and service could potentially be used as part of a demand response program, the costs, delivery, impacts, and other aspects of DR-specific program delivery are not included in this characterization at this time, though they could be added in the future.

This measure was developed to be applicable to the following program types: TOS, RF, DI.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The criteria for this measure are established by replacement of a manual-only thermostat, with one that has the capability to establish a schedule of time and/or temperature setpoints, or replacement of a programmable thermostat with an Advanced Thermostat.

###### Definition of Baseline Equipment

The baseline is assumed to be a manual or programmable thermostat.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 11 years.

###### Deemed Measure Cost

For DI and other programs for which installation services are provided, the actual material, labor, and other costs should be used. If unknown then the average incremental cost for the new installation measure is assumed to be $175.

###### Loadshape

Loadshape C05 - Commercial Electric Heating and Cooling, or

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

In the absence of conclusive results from empirical studies on peak savings, the TAC agreed to a temporary assumption of 50% of the cooling coincidence factor, acknowledging that while the savings from the Thermostat will track with the cooling load, the impact during peak periods may be lower. This is an assumption that could use future evaluation to improve these estimates.

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 45.7

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 23.9%

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Heating savings are provided based upon the percentage savings from the Residential version of this measure. Cooling savings are based on research on small commercial programmable thermostat installations. Future research on heating savings percentages for small commercial applications, and heating and cooling savings percentages for Advanced Thermostat applications, should be used to improve this assumption.

ΔkWh 	= ΔkWhheating + ΔkWhcooling

ΔkWhheating 	= (%ElecHeat * kBtu/hrheat * 1/HSPF * EFLHheat * Heating_Reduction * BAF) + ((1 - %ElecHeat) * ∆Therms * Fe * 29.3)

ΔkWhcool 	= kBtu/hrcool * 1/SEER * EFLHcool * Cooling_Reduction * BAF

Where:

%ElecHeat 	= Percentage of heating savings assumed to be electric

= 1 if electric heat, 0 if gas heat. If unknown assumu 0.08.

kBtu/hrheat	= capacity of the heating equipment in kBtu per hour.

= Actual. If unknown assume 114.5

HSPFbase	= Heating Seasonal Performance Factor of the baseline equipment

= Actual, if unknown assume Code base

EFLHheat	= Heating mode equivalent full load hours in Existing Buildings are provided in section 4.4 HVAC End Use.

Heating_Reduction 	= Assumed percentage reduction in total building heating energy consumption due to thermostat

= 8.8%

∆Therms 	= Therm savings if Natural Gas heating system

= See calculation in Natural Gas section below

Fe	= Furnace Fan energy consumption as a percentage of annual fuel consumption

= 7.7%

29.3		= kWh per therm

kBtu/hrcool 	= capacity of the cooling equipment actually installed in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr)

= Actual. If unknown assume 61.0

SEER		= Seasonal Energy Efficiency Ratio of the cooling equipment

= Actual, is unknown assume Code base

EFLHcool	= Equivalent Full Load Hours for cooling in Existing Buildings are provided in section 4.4 HVAC End Use.

Cooling_Reduction 	= Average percentage reduction in total building cooling energy consumption due to installation of thermostat:

= 17.7%

BAF	= Baseline adjustment factor.

= 1.0, if the baseline thermostat was manual type

= 0.6, if the baseline thermostat was programmable type

= 0.8, if the baseline is unknown

###### Summer Coincident Peak Demand Savings

ΔkW 	= kBtu/hrcool * 1/EER  * Cooling_Reduction * BAF  * CF

Where:

EER	= Energy Efficiency Ratio of the equipment

= Actual, if unknown assume current Code. For air-cooled units < 65 kBtu/hr, assume the following conversion from SEER to EER for calculation of peak savings:

EER = (-0.02 * SEER2) + (1.12 * SEER)

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 45.7

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 23.9%

Other variables as provided above.

###### Natural Gas Savings

∆Therms  = ((1 - %ElectricHeat) * EFLHheat * Capacity * 1/AFUE * Heating_Reduction * BAF)/ 100,000Btu/Therm

Where:

Capacity 	= Nominal Heating Input Capacity (Btu/hr) of heating system

= Actual

AFUE		= Annual Fuel Utilization Efficiency Rating

= Actual, if unknown assume code baseline.

Other variables as provided above.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-THST-V03-220101

###### Review Deadline: 1/1/2025

### Boiler Chemical Descaling

###### Description

The measure is for a non-residential hot water or steam boiler serving process loads or one that provides space heating. Even with careful and precise water treatment in a boiler system, mineral scales are formed over time due to the high pressure and heat. Boiler scale is typically calcium, carbon, iron and silica particle deposits that form on the boiler tubes. Scale creates a problem because it typically possesses a thermal conductivity, an order of magnitude less than the corresponding value for bare steel. Even thin layers of scale serve as an effective insulator and inhibit heat transfer. The result is overheating of boiler tube metal, tube failures, and loss of energy efficiency.

De-scaling a boiler system will improve boiler efficiency by removing mineral scale build up on boiler tubes. De-scaling is done either through mechanical or chemical cleaning techniques. There are several limitations to mechanical cleaning, namely firetube boilers cannot be mechanically cleaned. Depending on the size of the boiler, it can take up to a week to mechanically clean the tubes. This measure applies to chemical de-scaling, which is an efficient alternative, since it is not plagued by these limitations. The procedure typically involves the boiler being emptied and taken off-line, following which, the correct chemical solution ratio is pumped through the boiler system for four to eight hours.

This measure was developed to be applicable to the following program types: RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure, the facility must, as applicable, complete the chemical de-scaling by an approved technician and be NSF/ANSI/CAN 60 compliant.

The efficient equipment is a boiler system which has been de-scaled using a chemical solution. After the cleaning is complete, the personnel have to ensure that all safety checks are completed including checks for leaks. Lastly, any remains of the descaling chemical solution have to be eliminated from the tubes by flushing the system with water and a blowdown.

###### Definition of Baseline Equipment

The baseline condition is a boiler system that is compromised by scale build up.

###### Deemed Lifetime of Efficient Equipment

The lifetime of this measure varies based on the location of the site in Illinois. It has been established that the rate of scale buildup in hydronic systems is directly dependent on the hardness of the supply water (the amount of dissolved Calcium, Magnesium and Iron). Based on an analysis of water supply composition in Illinois, the estimated  life of measure(in years) before requiring de-scaling is listed below:

| Climate Zone | Measure Life of De-scaling |
| --- | --- |
| Rockford | 2 |
| Chicago | 6 |
| Springfield | 2 |
| Belleville | 3 |
| Marion | 3 |

###### Deemed Measure Cost

The cost of this measure is estimated to be $378/MMBtu/hr per boiler.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

∆Therms = (Capacity * EFLH * %Ei) / 100,000

Where:

Capacity 	= Nominal Heating Input Capacity Boiler Size (Btu/hr) for boiler unit

= Actual

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings are provided in section 4.4 HVAC End Use. For process loads, use custom hours.

%Ei	= Percent efficiency improvement from chemical descaling

= Dependent on system pressure and estimate of scale thickness. If unknown assume normal.

|  | Efficiency Improvement (%Ei) |  |
| --- | --- | --- |
| Scale Thickness (inches) | Low Pressure (15psig and below) Applications | High Pressure (above 15psig) Applications |
| Low (≤1/64 ) | 1% | 1.6% |
| Normal (≥1/32 & ≤ 3/64) | 2.5% | 3.9% |
| High (≥1/16) | 3.9% | 6.2% |

100,000	= Converts Btu to Therms

For example, a 10,000 MBH firetube steam boiler in a Manufacturing facility in Rockford. The scaling on the tubes was estimated to be of ‘normal’ thickness and the steam supply was ‘low pressure’ at 15 psig.

∆Therms 	= (Capacity * EFLH * %Ei) / 100,000

= (10,000,000 * 1,048 * 0.025) / 100,000

= 2,620 Therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-BCHD-V01-210101

###### Review Deadline: 1/1/2024

### Electric Chillers with Integrated Variable Speed Drives

###### Description

This measure relates to the installation of a new electric chiller(s) equipped with variable speed drives (VSDs) and meeting the efficiency standards presented below. This measure could relate to new construction, or the installation of a new system in an existing building (i.e. time of sale). Multiple-chiller applications as specified by building type can be assessed with this methodology. The characterization is specifically designed for centrifugal chillers with magnetic bearings/ceramic bearing (oilless) and VSDs, centrifugal chiller with VSDs, and screw chillers with VSDs. All the chillers in this characterization are water cooled. Oilless bearing VSD and centrifugal VSD chillers included in this characterization are up to 1,250 tons in nominal capacity, per chiller.  Screw VSD  chillers included in this characterization are up to 550 tons in nominal capacity, per chiller.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to exceed either Path A or Path B efficiency requirements defined in the table below:

| Type | Tons | Full Load kW/ton |  | Source |
| --- | --- | --- | --- | --- |
|  |  | Path A | Path B |  |
| Screw | <75 tons | 0.750 | 0.780 | IECC 2018 |
| Screw | 75-150 tons | 0.720 | 0.750 | IECC 2018 |
| Screw | 150-300 tons | 0.660 | 0.680 | IECC 2018 |
| Screw | 300-600 tons | 0.610 | 0.625 | IECC 2018 |
| Screw | >600 tons | 0.560 | 0.585 | IECC 2018 |
| Scroll | <75 tons | 0.750 | 0.780 | IECC 2018 |
| Scroll | 75-150 tons | 0.720 | 0.750 | IECC 2018 |
| Scroll | 150-300 tons | 0.660 | 0.680 | IECC 2018 |
| Scroll | 300-600 tons | 0.610 | 0.625 | IECC 2018 |
| Scroll | >600 tons | 0.560 | 0.585 | IECC 2018 |
| Centrifugal | 0-150 tons | 0.610 | 0.695 | IECC 2018 |
| Centrifugal | 150-300 tons | 0.610 | 0.635 | IECC 2018 |
| Centrifugal | 300-400 tons | 0.560 | 0.595 | IECC 2018 |
| Centrifugal | 400-600 tons | 0.560 | 0.585 | IECC 2018 |
| Centrifugal | >600 tons | 0.560 | 0.585 | IECC 2018 |

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit (if unknown assume IECC 2018 provided above).

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 23 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is provided below.

| Water-Cooled Centrifugal Chiller Incremental Costs ($/Ton) |  |  |  |
| --- | --- | --- | --- |
| Capacity (Tons) | Efficiency kW/ton (Full Load) |  |  |
|  | 0.6 | 0.58 | 0.54 |
| 100 | $62 | $99 | $172 |
| 150 | $42 | $66 | $115 |
| 200 | $31 | $49 | $86 |
| 300 | N/a | N/a | $55 |
| 600 | N/a | N/a | $22 |

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

CFSSP 	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM = PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

The measure uses run hours, chiller(s) size, baseline and proposed system efficiencies to calculate annual cooling savings in kWh and demand in kW. The tables with these values are included in the reference section of this measure. Run hours by building type and climate zone were calculated using EnergyPlus/OpenStudio models and the corresponding cooling loads were extracted. The cooling loads were extracted from the EnergyPlus/OpenStudio models based upon the DOE Prototype Buildings described in NREL’s “U.S. Department of Energy Commercial Reference Building Models of the National Building Stock” and a calibration log file that documents all of the variations made to each model to get them calibrated is provided in “ILCalibration-Log_2019-08-27.xlsx”. These documents and all the models are available on the SharePoint site.

Run hours were calculated based on the sum of the cooling coil loads from the EnergyPlus/OpenStudio models and were reduced based on airside-economizer setpoints for the commercial buildings. These setpoints are referenced in Table 1. Run hours by climate zone and building type are found in Table 2.

System efficiencies were developed for each applicable building type. First, the baseline chiller efficiency was developed. Baseline chiller selection was based on chiller size for the associated DOE prototype building and was defined by the peak load and modeling guidelines. Table 3 summarizes these modeling guidelines. The chillers were designed with 1.15 capacity factor. Baseline chiller types are identified for all five climate zones according to building type and can be found in Table 4.

Chilled water control strategies were also established for the energy models including condenser water reset and chilled water reset. The parameters for the reset strategies are found in Table 5 and Table 6. Chillers were staged on with the above referenced air-side economizer settings or were staged off if found to meet minimum thresholds for the baseline chiller technology. These minimum thresholds are found in Table 7. The model performance on the baseline curves did not match those of actual performance data at low loads and lower entering condenser water temperatures. The best available curves for baseline chiller performance are from the 2016 Nonresidential Alternative Calculation Method (ACM) Reference Manual. Upon research, these coefficients were made using chillers that met the ASHRAE 90.1 2010 minimum requirements for baseline chiller performance. Understanding this, as a conservative approach, the better performing coefficients of the two were used for the lower loads and lower condenser water temperatures offset by the differential in the peak operating kW of the modeled chillers. Condenser water temperature was determined using a 10°F cooling tower approach, with a maximum temperature of 85°F.

For modeling purposes, the chillers were modeled meeting energy efficiency requirements of the IECC 2018. The oilless bearing VSD and other VSD chiller efficiencies and part load data were provided by multiple chiller manufacturers. This data was used to develop the part load curves for the high efficiency oilless bearing VSD and integrated centrifugal VSD chillers. DOE2.2 performance curves were used to model the baseline chiller part load performance.

Chiller performance was calculated for all hours of cooling for each applicable building type. An average performance for the entire year was calculated for the baseline systems as well as high efficiency chiller systems. High efficiency chillers were replaced individually to develop savings performance characteristics for buildings with mixed chillers of varying efficiency. The intent for the chiller performance curves is to indicate system performance for each modeled scenario. Each modeled scenario was combined into an annualized performance based on chiller size and type. As the proposed chiller models were developed for above and below 500 tons for oilless bearing and VSD chillers and under 550 tons for the VSD screw, these thresholds were used to define the performance break points for averaging.  Chillers over 1,250 tons would not be applicable to this characterization and measure savings would need to be verified.

###### Electric Energy Savings

Energy efficiency savings:

ΔkWH = Tons * ((Baseline Chiller Efficiency) – (Proposed Chiller Efficiency)) * Run Hours

Where:

Tons 	= total chiller nominal cooling capacity being replaced in tons (note: 1 ton is 12,000 Btu/hr)

= Actual installed

Baseline Chiller Efficiency 	= annualized efficiency of baseline chiller as found the following table

| Baseline kW/ton | MBC | VSD | VSD Screw |
| --- | --- | --- | --- |
| Baseline < 500 tons | 0.52887 | 0.52887 | --- |
| Baseline 500-1000 tons | 0.55293 | 0.55293 | --- |
| Baseline < 550 tons | --- | --- | 0.51316 |

Proposed Chiller Efficiency 	= annualized efficiency of proposed chiller as found in the following table10

| Proposed kW/ton | MBC | VSD | VSD Screw |
| --- | --- | --- | --- |
| Proposed < 500 Tons | 0.40088 | 0.44254 | --- |
| Proposed 500-1250 tons | 0.38642 | 0.47237 | --- |
| Proposed < 550 Tons | --- | --- | 0.45705 |

Run Hours	= run hours for cooling as defined in Table 2 in Reference Tables section

= Actual, if known

###### Summer Coincident Peak Demand Savings

ΔkW = Tons * ((PEbase) – (PEee)) * CFSSP

ΔkW = Tons * ((PEbase) – (PEee)) * CFPJM

Where:

PEbase 		= Peak efficiency of baseline equipment expressed as Full Load (kW/ton) from  Table 2

PEee 		= Peak efficiency of high efficiency equipment expressed as Full Load (kW/ton)

= Actual installed

CFSSP 	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Reference Tables

Table 3 – Air-Side Economizer Setpoints by Building Type

| Building Type | Air-Side Economizer Temperature (F)* |
| --- | --- |
| College | 55 |
| Elementary School | 55 |
| Healthcare Clinic | 55 |
| High School | 55 |
| Hospital CV | - |
| Hospital CV econ | 55 |
| Hospital FCU | - |
| Hospital VAV | 55 |
| Hotel | 55 |
| Office High Rise CAV | - |
| Office High Rise CAV econ | 55 |
| Office High Rise FCU | - |
| Office High Rise VAV | 55 |
| Office Mid Rise | 55 |

Table 4 – Run Hours by Building Type

| Run Hours by Building Type | Z-1 (Rockford) | Z-2 (Chicago) | Z-3 (Springfield) | Z-4 (Belleville) | Z-5 (Marion) |
| --- | --- | --- | --- | --- | --- |
| College | 2,581 | 2,749 | 3,135 | 3,106 | 3,263 |
| Elementary School | 2,354 | 2,465 | 2,822 | 2,811 | 2,918 |
| Healthcare Clinic | 3,650 | 3,932 | 4,506 | 4,390 | 4,667 |
| High School | 2,614 | 2,800 | 3,164 | 3,208 | 3,345 |
| Hospital CV | 8,710 | 8,760 | 8,760 | 8,760 | 8,760 |
| Hospital CV econ | 3,514 | 3,748 | 4,425 | 4,211 | 4,412 |
| Hospital FCU | 8,760 | 8,760 | 8,760 | 8,760 | 8,760 |
| Hospital VAV | 3,650 | 3,932 | 4,506 | 4,390 | 4,667 |
| Hotel | 3,652 | 3,935 | 4,502 | 4,389 | 4,663 |
| Office High Rise CAV | 7,773 | 7,847 | 7,855 | 7,861 | 7,761 |
| Office High Rise CAV econ | 3,640 | 3,914 | 4,473 | 4,354 | 4,667 |
| Office High Rise FCU | 5,283 | 5,342 | 5,652 | 5,671 | 5,737 |
| Office High Rise VAV | 2,391 | 2,543 | 2,840 | 2,840 | 2,967 |
| Office Mid Rise | 2,568 | 2,722 | 3,061 | 3,057 | 3,224 |
| Unknown | 4,367 | 4,532 | 4,890 | 4,843 | 4,987 |

Table 5 – Chiller Sizing Guidelines

| Building Peak Cooling Load | Number and Type of Baseline Chillers for Screw VSD Models* | Number and Type of Baseline Chillers for Oilless and VSD Models** |
| --- | --- | --- |
| <=300 tons | 1 water-cooled screw chiller | 1 water-cooled screw chiller |
| >300 tons, <550 tons | 1 water-cooled screw chiller | 2 water-cooled screw chillers sized equally |
| >550 tons, <600 tons | 2 water-cooled screw chillers added so that no chiller is larger than 550 tons, all sized equally | 2 water-cooled screw chillers sized equally |
| >600 tons | 2 water-cooled centrifugal chillers minimum with chillers added so that no chiller is larger than 550 tons, all sized equally | 2 water-cooled centrifugal chillers minimum with chillers added so that no chiller is larger than 1,000 tons, all sized equally |

Table 6 – Baseline Chiller Selection by Building Type and Climate Zone

| Baseline Chiller | Z-1 (Rockford) | Z-2 (Chicago) | Z-3 (Springfield) | Z-4 (Belleville) | Z-5 (Marion) |
| --- | --- | --- | --- | --- | --- |
| College | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |
| Elementary School | Screw | Screw | Screw | Screw | Screw |
| Healthcare Clinic | Screw | Screw | Screw | Screw | Screw |
| High School | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |
| Hospital CV | Screw | Screw | Screw | Screw | Screw |
| Hospital CV econ | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |
| Hospital FCU | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |
| Hospital VAV | Screw | Centrifugal | Screw | Screw | Centrifugal |
| Hotel | Screw | Screw | Screw | Screw | Screw |
| Office High Rise CAV | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |
| Office High Rise CAV econ | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |
| Office High Rise FCU | Screw | Screw | Screw | Screw | Screw |
| Office High Rise VAV | Screw | Screw | Screw | Screw | Screw |
| Office Mid Rise | Screw | Screw | Screw | Screw | Screw |

Table 7 – Entering Condenser Water Minimum Temperatures

| Zone | City | Entering Condenser Water Minimum Temp (°F)* |
| --- | --- | --- |
| Z1 | Rockford | 70 |
| Z2 | Chicago | 70 |
| Z3 | Springfield | 70 |
| Z4 | Belleville | 75 |
| Z5 | Marion | 75 |

Table 8 – Chilled Water Reset Schedule

| Chilled Water Reset Schedule (F) |  |
| --- | --- |
| Outside Air Temp (F) | Leaving Chilled Water Temp (F) |
| >=80 | 44 minimum |
| <=60 | 54 maximum |

Table 9 – Chiller Minimum Thresholds

| Chiller Type | Minimum Compressor Load* |
| --- | --- |
| Screw | 15% |
| Centrifugal <300 | 10% |
| Centrifugal 300-600 | 10% |
| Centrifugal >600 | 10% |

Table 10  – Chiller System Performance Factors (Magnetic Bearing Chillers)

###### Measure Code: CI-HVC-CFVD-V02-220101

###### Review Deadline: 1/1/2024

### Advanced Rooftop Controls with High Rotor Pole Switch Reluctance Motors

###### Description

A High Rotor Pole Switch Reluctance Motor (HRSRM) is a type of brushless DC electric motor that runs by reluctance torque. Unlike other DC motor types, power is delivered to windings in the stator rather than the rotor. This simplifies the mechanical design; power does not need to be delivered to a moving part, but a switching system needs through software control and delivering power to the different windings. Electronic devices can precisely time switch, facilitating HRSRM configurations.

In application on RTUs, the HRSRM motor is comparable or more efficient than an RTU equipped with a variable speed drive supply fan. It results in fan energy savings and can also include cooling savings if coupled with compressor or ventilation control, compared to a baseline scenario of constant-volume, constant-ventilation operation that is typical of single-zone, packaged HVAC units.

Fan energy savings come from the new integrated motor controls that allow for higher efficiency at varying loads, and is achieved in all applications. Cooling savings can also be added from the effective use of variable speed or multi-stage cooling.

The markets that can be served by HRSRM motors are those which utilize RTUs, including but not limited to:

- Fast-Service Restaurant

- Full-Service Restaurant

- Small Office

- Stand-Alone Retail

- Strip Mall

- Warehouse

This measure was developed to be applicable to the following program types: NC, RF, EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is a single-zone, packaged HVAC unit with an existing functional integrated economizer that has been fitted with a HRSRM supply-fan and integrated speed control. This applies to both retrofit and new construction, and early replacement applications.

###### Definition of Baseline Equipment

The baseline equipment is a single-zone, packaged HVAC unit (with an existing functional integrated economizer)

that lacks demand-controlled ventilation controls and lacks supply-fan speed control via a variable-frequency drive.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 12 years based on the HRSRM life.

###### Deemed Measure Cost

Actual measure costs should be used if available. If costs are not available, the deemed measure cost below can be used. Material cost is based on the horsepower (hp) of the supply fan used in the RTU. Retrofit represents the full cost of the installation. New construction and early replacement represent the incremental cost of the motor itself on a new unit.

Deemed Measure Cost Details

| Type | HP | Material Cost | Labor Hours | Labor Rate | Deemed Cost |
| --- | --- | --- | --- | --- | --- |
| Retrofit | 1 | $1,554.75 | 3 | $96.67 | $1,844.76 |
| Retrofit | 1.5 | $1,580.75 | 3 | $96.67 | $1,870.76 |
| Retrofit | 2 | $1,644.75 | 3 | $96.67 | $1,934.76 |
| Retrofit | 5 | $1,758.75 | 3 | $96.67 | $2,048.76 |
| Retrofit | 7.5 | $2,417.75 | 3 | $96.67 | $2,707.76 |
| Retrofit | 10 | $2,587.75 | 3 | $96.67 | $2,877.76 |
| New Construction/Early Replacement | 1 | $932.85 | - | - | $932.85 |
| New Construction/Early Replacement | 1.5 | $948.45 | - | - | $948.45 |
| New Construction/Early Replacement | 2 | $986.85 | - | - | $986.85 |
| New Construction/Early Replacement | 5 | $1,055.25 | - | - | $1,055.25 |
| New Construction/Early Replacement | 7.5 | $1,450.65 | - | - | $1,450.65 |
| New Construction/Early Replacement | 10 | $1,552.65 | - | - | $1,552.65 |

###### Loadshape

Commercial ventilation C23

###### Coincidence Factor

CFSSP 	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM = PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

Six different building types were selected for study. OpenStudio measures were used to generate ASHRAE 90.1-2013 code-compliant DOE prototype baseline models for each building type. The total conditioned area, the number of conditioned zones, and the peak cooling demand for each building are summarized in the following table.

Selected DOE Prototype Buildings

| Building Type | Small Office | Stand-Alone Retail | Warehouse | Strip Mall | Fast-Service Restaurant | Full-Service Restaurant |
| --- | --- | --- | --- | --- | --- | --- |
| Conditioned Area (ft2) | 5,502 | 24,692 | 52,045 | 22,500 | 2,501 | 5,502 |
| Number of Conditioned Zones | 5 | 4 | 3 | 10 | 2 | 2 |
| Total Fan Break Horsepower (BHP) | 3.5 | 25 | 5 | 23 | 7 | 11 |
| Design Cooling Load (Ton) | 8.5 | 65 | 13 | 69 | 20 | 33 |

In order to achieve savings, the RTU control options consist of following modes:

- Ventilation Mode:

  - Outdoor air is at a minimum for building type

  - Fan speed set to 40%

  - Heating and cooling coils are off

- Economizer Mode

  - Outdoor air rate was set from 40% and increased as needed to satisfy indoor air temperature

  - When outdoor air could no longer satisfy cooling, cooling mode was staged on

- Mechanical Cooling Mode

  - Outdoor air is at a minimum for building type

  - Compressors (if multiple or variable) were staged/modulated to meet setpoint temperature of the space

  - Supply fan set to 100%

- Heating mode

  - Outdoor air is at a minimum for building type

  - Heating coil staged as necessary

  - Supply fan set to 100%

The models produced a percentage energy savings based on using a HRSRM fan and varying compressor types. Retrofit savings include fan only. For new construction and early replacement, savings are based on compressor type and energy efficiency of the unit. These RTU control options are reflected in the table below. As a correction to these entries, a second set of single two-stage compressor RTU fan options are also reflected in the Energy Savings Type: ESF_Fan entry in the table below:

- Ventilation

  - Supply fan set to 40%

- Heating/Cooling 1

  - Supply fan set to 75%

- Heating/Cooling 2

  - Supply fan set to 90%

###### Electric Energy Savings

For units with cooling capacities less than 65 kBtu/hr:

ΔkWH = (kBtu/hr) * (1/ SEERexist) * EFLH * ESF_Cooling + 0.746 * FanHP * RunHours * ESF_Fan

For units with cooling capacities equal to or greater than 65 kBtu/hr:

ΔkWH = (kBtu/hr) * (1/IEERexist) * EFLH * ESF_Cooling + 0.746 * FanHP * RunHours * ESF_Fan

Where:

kBtu/hr 	= capacity of the cooling equipment in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr)

SEERexist 	= Seasonal Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation. IECC 2018 provided below for referenced.

IEERexist 	= Integrated Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation. IECC 2018 provided below for reference.

EFLH 	= Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in Illinois TRM version 8.0 section 4.4 HVAC End Use

ESF_Cooling	= Energy savings factor for cooling as found in table below.

ESF_Fan	= Energy savings factor for cooling as found in table below

Energy Savings Factors

| Energy Savings Type | Retrofit Type | HRSM on Single Stage Compressor | HRSM on Single Two Stage Compressor | HRSM on Variable Speed Compressor |
| --- | --- | --- | --- | --- |
| ESF_Cooling | New Construction/Early Replacement | 0% | 0% | 0% |
| ESF_Cooling | Supply Fan Retrofit Only | 9.6% | 8.1% | 9.1% |
| ESF_Fan | New Construction/Early Replacement | 45.8% | 60.0% | 63.7% |
| ESF_Fan | Supply Fan Retrofit Only | 45.8% | 60.0% | 63.7% |

FanHP	= Horsepower of fan in RTU

= Actual

RunHours	= Annual operating hours for fan motor based on building type

= Default hours are provided for HVAC applications which vary by HVAC application and building type. When available, actual hours should be used.

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly | 7,235 | eQuest |
| Assisted Living | 8,760 | eQuest |
| Auto Dealership | 7,451 | OpenStudio |
| College | 4,836 | OpenStudio |
| Convenience Store | 7,004 | eQuest |
| Drug Store | 7,156 | OpenStudio |
| Elementary School | 3,765 | OpenStudio |
| Emergency Services | 8,760 | OpenStudio |
| Garage | 7,357 | eQuest |
| Grocery | 8,543 | OpenStudio |
| Healthcare Clinic | 4,314 | OpenStudio |
| High School | 3,460 | OpenStudio |
| Manufacturing Facility | 8,706 | eQuest |
| MF - High Rise | 8,760 | OpenStudio |
| MF - Mid Rise | 8,760 | OpenStudio |
| Hotel/Motel - Guest | 2,409 | OpenStudio |
| Hotel/Motel - Common | 8,683 | OpenStudio |
| Movie Theater | 7,505 | eQuest |
| Office - Low Rise | 6,345 | OpenStudio |
| Office - Mid Rise | 3,440 | OpenStudio |
| Religious Building | 7,380 | eQuest |
| Restaurant | 7,302 | OpenStudio |
| Retail - Department Store | 7,155 | OpenStudio |
| Retail - Strip Mall | 6,921 | OpenStudio |
| Warehouse | 6,832 | OpenStudio |
| Unknown | 6,241 | n/a |

2018 IECC Minimum Efficiency Requirements

###### Summer Coincident Peak Demand Savings

ΔkW = [(kBtu/hr) * (1/EERexist) * ESF_Cooling + 0.746 * FanHP * ESF_Fan] * CF

Where:

EERexist 	= Energy Efficiency Ratio of the existing equipment (assume the following conversion from SEER to EER for calculation of peak savings: EER = (-0.02 * SEER2) + (1.12 * SEER))

= Actual, or assume Code base in place at the original time of existing unit installation

CFSSP 	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-HSRM-V02-220101

###### Review Deadline: 1/1/2024

### Hydronic Heating Radiator Replacement

###### Description

A hydronic heating radiator’s capacity to evenly and consistently distribute heat throughout a space, utilizing piped hot-water or steam is often stymied by the buildup of mineral deposits and contaminates. Past research has shown that eliminating these deposits regularizes flow rate and boiler behavior, in effect restoring a radiator to a like-new condition. A space is heated more effectively in this improved state and this condition furthermore reduces the need for continual (additionally wasteful) thermostat readjustment. A straightforward process to achieve this is to simply replace the fouled hydronic radiator pipe system with a new system equivalent to the replaced system’s pre-fouled performance levels. This avoids any possible inconsistencies associated with a radiator-flushing procedure (e.g., less-than-expected savings, failure to return the pipe system to like-new condition, inability to treat a system due to its interlinking with separate domestic hot water systems, etc.) and furthermore ensures that expected savings are realized. This measure offers benefits during heating seasons for natural gas, is applicable to both residential and commercial applications, and considers hot water or steam as the source of thermal energy (seeing as both heat transfer mediums can theoretically act as the intermediary from which contaminates precipitate).

The calculations of savings presented in this section are furthermore normalized to apply to both commercial and multi-family residential applications and additionally consider the differences between the physical characteristics of hot water or steam (e.g., thermal resistance, temperature, convective heat transfer) when computing the savings tabulated in the ‘Annual Normalized Gas Savings per Surface Area’ table shown below.

This measure was developed to be applicable to the following program types:  RF

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is a new replacement hydronic radiator free of mineral deposit scaling and/or sludge which must reflect the capacity of the replaced system’s pre-fouled performance levels (i.e., a “like-for-like” replacement).

###### Definition of Baseline Equipment

The baseline condition is the hydronic radiator being replaced, which has shown decreased performance due to a high degree of mineral deposit scaling and sludge buildup. The built-up scale inside the radiators is predominantly assumed to be Iron Oxide (Fe3O4) and to have a thermal conductivity of 3.01 Btu/hr.ft.°F.

A “standard scaled” radiator is assumed to be 10% clogged and a “heavily scaled” radiator is assumed to be 30% clogged. An implementation contractor will need to verify the baseline condition of the radiator, to classify it as either standard or heavily scaled. Measuring the surface temperature spread using an infrared temperature thermometer can be used to determine this; surface temperature spot readings below 180°F for a steam system and below 100°F for a hot water system can be labeled as ‘standard scaling’. A “heavily scaled” radiator is assumed to one with surface temperature spots below 150°F for a steam system and below 90°F for a hot water system. This should be verified by the implementation contractor by measuring the radiator surface temperature at multiple points when operating the boiler system at full load and when outdoor air temperatures are below 20°F. Implementer should strive to perform spot readings on at least 10% of total radiators. Based on the collected spot temperature readings, qualify the facility as either standard scaled or heavily scaled.

The baseline for this measure are aging scaled radiators. Most facilities tend not to replace their old radiators and often tend to add a means of secondary heating. This measure is aimed at these facilities to incentivize the replacement of these old radiators.

###### Deemed Lifetime of Efficient Equipment

Hydronic radiator systems are extremely diverse, in size, scope or application, and in the materials utilized for the heat transfer surface. Cast iron, steel, and copper piping are common in radiators, as are polymer materials such as polyethylene (often seen in newer radiator systems). As such, an estimated useful life will naturally vary based on these circumstances and the quality of previous radiator maintenance. The estimated useful life of a typical hydronic radiator has been approximated to be 25 years.

###### Deemed Measure Cost

The measure cost is the full cost of removing the existing unit and installing a new one. The actual program cost should be used. If unknown, assume $61.35 per vertical column. For more details on the definition of section of a radiator, the cited reference can be used.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

The annual natural gas savings per area for radiator replacement is calculated by determining the difference between the heat transfer from the replacement radiator and the radiator being replaced.

ΔTherms=QNew-QBase*EFLH(100,000* η)

QBase=(A* ΔT)RBase

RBase=Rconv1+Rcond+Rrad*Rconv2Rrad+Rconv2

QNew=(A* ΔT)RNew

The thermal resistance components remain the same as the above (RBase), with the exception of the contaminate oxide layer which is no longer present in the post-case:

RNew=Rconv1+Rrad*Rconv2Rrad+Rconv2

Where:

QNew (Btu/hr)		= The heat emission from the replacement hydronic heating system

QBase (Btu/hr)		= The heat emission from the hydronic heating system being replaced

EFLH			= Effective full load hours based on the climate zone

Heating Season Recirculation Hours

| Climate Zone | Hours |
| --- | --- |
| 1 - Rockford | 5,039 |
| 2 - Chicago | 4,963 |
| 3 - Springfield | 4,495 |
| 4 - Belleville | 4,021 |
| 5 - Marion | 4,150 |

η	= Actual Thermal Efficiency of the Heating Equipment (if unknown, use 81.9% for water boilers and 80.7% for steam boilers)

100,000 	= conversion factor (1 Therm = 100,000 Btu)

A (ft2) 			= the effective area of heat transfer of the radiator

ΔT (°F) 	= the temperature difference between the supply fluid temperature and the conditioned room design temperature

RBase (ft2 °F hr/ BTU) 	= the overall thermal resistance of the system before replacement

RNew (ft2 °F hr/ BTU)	= the overall thermal resistance of the system after replacement

Rconv1(ft2 °F hr/ BTU) 	= the thermal resistance of convection between the hot water/steam and the radiator

Rcond(ft2 °F hr/ BTU)	= the thermal resistance of conduction in the oxide layer buildup

Rrad(ft2 °F hr/ BTU) 	= the thermal resistance of radiation between the radiator and the conditioned space

Rconv2(ft2 °F hr/ BTU) 	= the thermal resistance of convection between radiator and the conditioned space

Annual Normalized Gas Savings per Surface Area (therms/ft2)

| HVAC System Type |  | 1 - Rockford | 2 - Chicago | 3 - Springfield | 4 - Belleville | 5 - Marion |
| --- | --- | --- | --- | --- | --- | --- |
| Hot Water Radiator | Standard Scaling | 0.115 | 0.113 | 0.102 | 0.091 | 0.094 |
|  | Heavy Scaling | 0.337 | 0.332 | 0.301 | 0.269 | 0.278 |
| Steam Radiator | Standard Scaling | 0.170 | 0.168 | 0.152 | 0.136 | 0.140 |
|  | Heavy Scaling | 0.501 | 0.493 | 0.447 | 0.400 | 0.413 |

∆Therms= HScz*Arearadiator

Where:

HScz	= Annual heating savings per area of radiator by climate zone, values from ‘Annual Normalized Gas Savings per Surface Area’ table above.

Arearadiator	= Total surface area of radiator (ft2)

For example, a building in Climate Zone 1 is equipped with a heavily scaled steam radiator system. The surface area of the replacement and radiator being replaced was calculated to be 85 ft2.

ΔTherms	= Annual Normalized Gas Savings (therms/sq.ft.) * Surface Area (sq.ft.)

= 0.501  * 85

= 42.59 therms annually

Example:

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-HHRR-V01-210101

###### Review Deadline: 1/1/2024

### HVAC Supply, Return and Exhaust Fans - Fan Energy Index

###### Description

The Fan Energy Index (FEI) is a new fan efficiency metric that allows for the comparison of different fans at application specific operating conditions. This is a significant improvement over the current Fan Efficiency Grade metric, which is defined at a rated condition. FEI is incorporated in ASHRAE 90.1-2019 and IECC-2021. These codes set the baseline FEI as 1.0 for constant speed fan operation and 0.95 for variable speed fan operation. More efficient fans will have FEI greater than these values. It is only applicable to stand-alone fans, and not for fans embedded in packaged equipment. This measure results in fan energy savings compared to a baseline scenario of an existing fan’s FEI or code minimum FEI for a new fan.

Note this measure should be used for evaluating more efficient over baseline fans with the same control system. Measure 4.4.26 should be utilized to evaluate control system modifications. When combining the two measures, the FEPnew value should be used to replace the 0.746×HP×LFηmotor term in Measure 4.4.26.

This measure serves the market for commercial and industrial buildings.

This measure was developed to be applicable to the following program types: TOS, NC, and EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to exceed the efficiency requirements defined by the program.

###### Definition of Baseline Equipment

For Time of Sale (TOS):  The baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit or sale (if unknown assume IECC 2018).

For New Construction (NC): The baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit (if unknown assume IECC 2018).

For Early Replacement (EREP): The baseline equipment is assumed to be the existing fan.

###### Deemed Lifetime of Efficient Equipment

For variable speed fans, the expected measure life is 15 years.

For constant speed fans, the expected measure life is 18 years for centrifugal housed and unhoused fans. The expected measure life is 25 years for all other fan types.

###### Deemed Measure Cost

Actual measure costs should be used if available. Default measure costs are noted below for fans with FEI greater than 1.0. These costs are established at an FEI of 1.2. To calculate the cost for a fan with different FEI, prorate the default cost with the actual FEI (see example).

TOS and NC

| Fan Type | Cost ($/hp) |  |
| --- | --- | --- |
|  | Small (< 10 hp) | Large (>= 10 hp) |
| Axial Cylindrical Housed | $264 | $87 |
| Panel | $29 | $10 |
| Centrifugal Housed | $199 | $55 |
| Centrifugal Unhoused | $76 | $18 |
| Inline and Mixed Flow | $297 | $97 |
| Radial | $119 | $33 |
| Power Roof Ventilator | $140 | $42 |
| Axial Cylindrical Housed | $264 | $87 |

EREP

| Fan Type | Cost ($/hp) |  |
| --- | --- | --- |
|  | Small (< 10 hp) | Large (>= 10 hp) |
| Axial Cylindrical Housed | $3,218 | $1,068 |
| Panel | $319 | $104 |
| Centrifugal Housed | $1,381 | $382 |
| Centrifugal Unhoused | $827 | $195 |
| Inline and Mixed Flow | $2,301 | $751 |
| Radial | $1,570 | $434 |
| Power Roof Ventilator | $1,536 | $460 |
| Axial Cylindrical Housed | $3,218 | $1,068 |

For example, the default deemed measure cost of installing of a new construction, centrifugal housed, 5 hp fan with FEI = 1.3 is:   Deemed Measure Cost ($) = $199/hp * 5 hp * (1.3 / 1.2) = $1,078

###### Loadshape

Loadshape C39 - VFD - Supply fans <10 HP

Loadshape C40 - VFD - Return fans <10 HP

Loadshape C41 - VFD - Exhaust fans <10 HP

###### Coincidence Factor

The demand savings factor (DSF) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Note this measure should be used for evaluating more efficient over baseline fans with the same control system. Measure 4.4.26 should be utilized to evaluate control system modifications. When combining the two measures, the FEPnew value should be used to replace the 0.746×HP×LFηmotor term in Measure 4.4.26.

| ∆kWhfan = | FEPNew*(FEINewFEIBase-1)*RHRS*0%100%%FF*PLR |
| --- | --- |
| ∆kWhtotal = | ∆kWhfan*(1+IEenergy) |

Where:

∆kWhfan	= Fan-only annual energy savings (kWh)

FEPNew		= Fan Electrical Power of new fan at 100% flow fraction (kW)

FEINew		= Fan Energy Index of new fan at 100% flow fraction (-)

FEIBase 		= Fan Energy Index of baseline fan at 100% flow fraction (-)

TOS and NC: 	FEIbase is defined per IECC.

= 0.95 for Variable Speed Fan

= 1.0 for Constant Speed Fan

EREP: 		FEIbase is defined as existing fan efficiency. If unknown, use:

| Fan Type | Drive Type |  |  |
| --- | --- | --- | --- |
|  | Variable Speed - Belt | Constant Speed - Belt | Constant Speed - Direct |
| Axial Cylindrical Housed | 0.88 | 0.88 | 0.97 |
| Panel | 0.95 | 0.95 | 0.88 |
| Centrifugal Housed | 0.92 | 0.92 | 0.92 |
| Centrifugal Unhoused | 0.94 | 0.94 | 1.03 |
| Inline and Mixed Flow | 0.79 | 0.79 | 0.77 |
| Radial | 0.81 | 0.81 | 0.94 |
| Power Roof Ventilator | 0.82 | 0.82 | 0.76 |

RHRS		= Annual operating hours for fan based on building type

Default hours are provided for HVAC applications which vary by HVAC application and building type. When available (provided via Energy Management Software or metered),  actual hours should be used.

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly | 7235 | eQuest |
| Assisted Living | 8760 | eQuest |
| Auto Dealership | 7451 | OpenStudio |
| College | 4836 | OpenStudio |
| Convenience Store | 7004 | eQuest |
| Drug Store | 7156 | OpenStudio |
| Elementary School | 3765 | OpenStudio |
| Emergency Services | 8760 | OpenStudio |
| Garage | 7357 | eQuest |
| Grocery | 8543 | OpenStudio |
| Healthcare Clinic | 4314 | OpenStudio |
| High School | 3460 | OpenStudio |
| Hospital - VAV econ | 4666 | OpenStudio |
| Hospital - CAV econ | 8021 | OpenStudio |
| Hospital - CAV no econ | 7924 | OpenStudio |
| Hospital - FCU | 4055 | OpenStudio |
| Manufacturing Facility | 8706 | eQuest |
| MF - High Rise | 8760 | OpenStudio |
| MF - Mid Rise | 8760 | OpenStudio |
| Hotel/Motel - Guest | 2409 | OpenStudio |
| Hotel/Motel - Common | 8683 | OpenStudio |
| Movie Theater | 7505 | eQuest |
| Office - High Rise - VAV econ | 2369 | OpenStudio |
| Office - High Rise - CAV econ | 2279 | OpenStudio |
| Office - High Rise - CAV no econ | 5303 | OpenStudio |
| Office - High Rise - FCU | 1648 | OpenStudio |
| Office - Low Rise | 6345 | OpenStudio |
| Office - Mid Rise | 3440 | OpenStudio |
| Religious Building | 7380 | eQuest |
| Restaurant | 7302 | OpenStudio |
| Retail - Department Store | 7155 | OpenStudio |
| Retail - Strip Mall | 6921 | OpenStudio |
| Warehouse | 6832 | OpenStudio |
| Unknown | 6241 | n/a |

%FF 		= Percentage of run-time spent within a given flow fraction range

Default Fan Duty Cycle Based on 2012 ASHRAE Handbook; HVAC Systems and Equipment, page 45.11, Figure 12.

| Flow Fraction (% of design cfm) | Percent of Time at Flow Fraction |
| --- | --- |
| 0% to 10% | 0.0% |
| 10% to 20% | 1.0% |
| 20% to 30% | 5.5% |
| 30% to 40% | 15.5% |
| 40% to 50% | 22.0% |
| 50% to 60% | 25.0% |
| 60% to 70% | 19.0% |
| 70% to 80% | 8.5% |
| 80% to 90% | 3.0% |
| 90% to 100% | 0.5% |

PLR		= Part load ratio for a given flow fraction range

| Control Type | Flow Fraction |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% |
| No Control or Bypass Damper | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Discharge Dampers | 0.46 | 0.55 | 0.63 | 0.70 | 0.77 | 0.83 | 0.88 | 0.93 | 0.97 | 1.00 |
| Outlet Damper, BI & Airfoil Fans | 0.53 | 0.53 | 0.57 | 0.64 | 0.72 | 0.80 | 0.89 | 0.96 | 1.02 | 1.05 |
| Inlet Damper Box | 0.56 | 0.60 | 0.62 | 0.64 | 0.66 | 0.69 | 0.74 | 0.81 | 0.92 | 1.07 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.53 | 0.56 | 0.57 | 0.59 | 0.60 | 0.62 | 0.67 | 0.74 | 0.85 | 1.00 |
| Inlet Vane Dampers | 0.38 | 0.40 | 0.42 | 0.44 | 0.48 | 0.53 | 0.60 | 0.70 | 0.83 | 0.99 |
| Outlet Damper, FC Fans | 0.22 | 0.26 | 0.30 | 0.37 | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06 |
| Eddy Current Drives | 0.17 | 0.20 | 0.25 | 0.32 | 0.41 | 0.51 | 0.63 | 0.76 | 0.90 | 1.04 |
| Inlet Guide Vane, FC Fans | 0.21 | 0.22 | 0.23 | 0.26 | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04 |
| VFD with duct static pressure controls | 0.09 | 0.10 | 0.11 | 0.15 | 0.20 | 0.29 | 0.41 | 0.57 | 0.76 | 1.01 |
| VFD with low/no duct static pressure | 0.05 | 0.06 | 0.09 | 0.12 | 0.18 | 0.27 | 0.39 | 0.55 | 0.75 | 1.00 |

Provided below is the resultant values based upon the defaults provided above:

| Control Type | 0%100%%FF×PLR |
| --- | --- |
| No Control or Bypass Damper | 1.00 |
| Discharge Dampers | 0.80 |
| Outlet Damper, BI & Airfoil Fans | 0.78 |
| Inlet Damper Box | 0.69 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.63 |
| Inlet Vane Dampers | 0.53 |
| Outlet Damper, FC Fans | 0.53 |
| Eddy Current Drives | 0.49 |
| Inlet Guide Vane, FC Fans | 0.39 |
| VFD with duct static pressure controls | 0.30 |
| VFD with low/no duct static pressure | 0.27 |

∆kWhtotal	= Total project annual energy savings (kWh)

IEenergy		= HVAC interactive effects factor for energy (default = 15.7%)

###### Summer Coincident Peak Demand Savings

| ∆kWfan = | FEPretrofit*FEIretrofitFEIbase-1*PLRFFpeak |
| --- | --- |
| ∆kWtotal = | ∆kWfan*(1+IEdemand) |

Where:

∆kWfan		= Fan-only summer coincident peak demand impact (kW)

PLRFFpeak	= The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the baseline flow control type (default average flow fraction during peak period = 90%)

∆kWtotal		= Total project summer coincident peak demand impact (kW)

IEdemand		= HVAC interactive effects factor summer coincident peak demand (default = 15.7%)

###### Natural Gas Savings

There are no expected fossil fuel impacts for this measure.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-FFEI-V01-220101

###### Review Deadline: 1/1/2023

### Process Heating Boiler

###### Description

A process boiler is a pressure vessel that transfers heat to water for industrial process applications. Process boilers can be configured as an integrated packaged boiler or as modular instantaneous boiler arrays. This measure is applicable to boilers which serve process loads in a facility.

Modular instantaneous boilers are a recent addition to the industrial/commercial market aimed at addressing some of the drawbacks of conventional large boiler systems. They achieve high efficiencies by using multiple smaller sized modules to meet the minimum demand. They allow each boiler to operate at or close to full rated load most of the time, with reduced standby losses. The boiler design is a low water mass pressure vessel that produces steam at operating pressure rapidly then shuts off the combustion system once the demand requirement is met, thereby saving fuel.

Traditional packaged boiler systems are designed to provide the entire steam load of the facility using one or two boilers. Typically, the boiler horsepower is sized for the maximum steam load required at any facility. However, the average steam load of any facility is only 30 to 40 percent of this, and the average load on the boiler system is low. Therefore, they are not able to achieve these high efficiencies.

This measure was developed to be applicable to the following program types: NC, EREP, TOS.

###### Definition of Efficient Equipment

The efficient case is the replacement of a non-residential standard efficiency process boiler for process loads with a high-efficiency process boiler exceeding the energy conservation standards outlined below. The efficient unit may either be a conventional packaged boiler or a modular boiler array system. Non-residential commercial boilers are defined as having an input rating greater than 300,000 Btu/h.

###### Definition of Baseline Equipment

For Time of Sale and New Construction:

Gas-fired boilers greater than or equal to 300,000 Btu/hr termed as commercial packaged boilers, manufactured on or after March 2, 2012 and prior to January 10, 2023 must comply with the standards defined in the Code of Federal Regulations, 10 CFR 431.87.

Boiler baseline efficiency standards (on or after March 2, 2012 until January 10, 2023)

| Boiler Type | Efficiency |
| --- | --- |
| Hot Water Boiler > 300,000 Btu/h and < 2,500,000 Btu/h | 80% ET |
| Hot Water Boiler > 2,500,000 Btu/h | 82% EC |
| Steam Boiler – all except natural draft > 300,000 Btu/h and < 2,500,000 Btu/h | 79% ET |
| Steam Boiler – all except natural draft > 2,500,000 Btu/h | 79% ET |
| Steam Boiler – natural draft > 300,000 & < 2,500,000 Btu/h | 77% ET |
| Steam Boiler – natural draft > 2,500,000 Btu/h | 77% ET |

where ET means “thermal efficiency” and EC means “combustion efficiency” as defined in 10 CFR 431.82.

A NEW FEDERAL STANDARD WILL BECOME EFFECTIVE JANUARY 10, 2023. TRM VERSION 11 UPDATES SHOULD INCLUDE A DISCUSSION ABOUT EFFECTIVE DATE FOR THIS NEW BASELINE. IT IS INCLUDED BELOW FOR INFORMATIONAL/PLANNING PURPOSES.

Each gas-fired commercial packaged boiler listed in Table 3 to §431.87 and manufactured on or after January 10, 2023, must meet the applicable energy conservation standard levels as below. This baseline will be applicable to NC from January 10, 2023.

Boiler baseline efficiency standards (on or after January 10, 2023)

| Boiler Type | Efficiency |
| --- | --- |
| Hot Water Boiler > 300,000 Btu/h and < 2,500,000 Btu/h | 84% ET |
| Hot Water Boiler > 2,500,000 Btu/h and <10,000,000 Btu/h | 85% EC |
| Hot Water Boiler >10,000,000 Btu/h | 82% EC |
| Steam Boiler > 300,000 Btu/h and < 2,500,000 Btu/h | 81% ET |
| Steam Boiler > 2,500,000 Btu/h and <10,000,000 Btu/h | 82% ET |
| Steam Boiler > 10,000,000 Btu/h | 79% ET |

where ET means “thermal efficiency” and EC means “combustion efficiency” as defined in 10 CFR 431.82.

For early replacement: The efficiency of the existing equipment should be used for the assumed remaining useful life of the equipment and a new baseline equipment as described above (post 2023) for the remainder of the measure life.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 25 years.

For EREP, the remaining useful life of the existing equipment is assumed to be 1/3rd of EUL (25/3) or 8 years.

###### Deemed Measure Cost

The measure cost for this technology is tiered based on the boiler type and combustion efficiencies. As installation costs for the base case and the measure case units are assumed to be the same, labor costs are not specified for this measure.

Incremental and Gross Measure costs for Process Boilers

| Boiler Type | Incremental Measure Cost ($/KBtu) | Full Measure Cost ($/KBtu) |
| --- | --- | --- |
| Hot Water Boiler >85% EC and <90% EC | $2.17 | $12.94 |
| Hot Water Boiler >90% EC | $12.17 | $22.95 |
| Steam Boiler >83% EC and <85% EC | $4.35 | $19.24 |
| Modular Steam Boiler Arrays (>85% EC) | Custom |  |

A deferred baseline replacement cost, consistent with the delta between the full measure cost and incremental cost above should be assumed after the remaining useful life of the existing equipment.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

For first 8 years:

∆Therms=8,766*×Capacity× * Utilization FactorUF*×EfficiencyEEEfficiencyExist-1EfficiencyEE-EfficiencyBaseEfficiencyBase*×1100,000

For remaining 17 years:

∆Therms=8,766*Capacity* UF*EfficiencyEEEfficiencyBase-1*1100,000

Where:

8,766	=	  Annual Operating hours for Process Boilers

The assumed hours of operation are based on continual plant operation. Variation in plant operating hours is accounted for in the utilization factor. While the boiler may operate during the entire year, it may not be operating at its full rated load.

Capacity	= 	Nominal heating input capacity boiler size for high-efficiency unit (Btu/hr)

UF	 = Utilization Factor

= Custom or if unknown 41.9%

EfficiencyExist	= Existing boiler efficiency rating,

= Actual

EfficiencyBase	= 	Baseline boiler efficiency rating, dependent on year and boiler type or use actual operating efficiencies for early replacements. See table in “Definition of Baseline Equipment.”

EfficiencyEE	= 	Efficient boiler efficiency rating for packaged or modular boiler system

= 	Actual value, specified to one significant digit (i.e., 95.7%)

100,000	= 	Constant to convert from Btu to therm

For example, a 800,000 Btu/hr gas-fired process steam boiler with a thermal efficiency rating of 87% is installed replacing a similar sized natural draft steam boiler with baseline efficiency of 77%.

ΔTherms	= 8,766 * 800,000 * 0.419 * (0.870 – 0.770)/0.770 / 100,000

=  3,816 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-PHBO-V01-220101

###### Review Deadline: 1/1/2025

### Commercial Gas Heat Pump

###### Description

Heat pumps are a class of HVAC equipment that moves heat from cold source to warm sink, moving heat “uphill”. Often heat pumps can operate in reverse, using a reversing valve or other means to provide air conditioning (A/C) and space heating with the same product. If heat recovery is employed, the heat pump can also provide service hot water (SHW).  Heat pumps generally involve the use of a refrigerant and so are based on refrigeration cycles. Gas-fired heat pumps are a subset of heat pumps whose primary input drive energy is a gaseous fuel, instead of an electrically-driven compressor. Gas-fired heat pumps can be separated into two categories, work-activated technologies where a delivered fuel drives a prime mover (e.g. internal combustion engine) which supplies work to a refrigerant compressor and heat-activated where the primary energy input to the heat pump cycle is thermal energy, often from fuel combustion, driving a sorption-type or other thermally-driven heat pump cycle.

This measure characterizes the installation of a commercial gas-fired heat pump for the following scenarios: NC, TS, EREP, and RF.

- New Construction:

- The installation of a new commercial heat-activated (e.g. sorption-type) or work-activated (e.g. engine-driven) gas heat pump, certified to ANSI Z21.40.1 or ANSI Z21.40.2 respectively, that meets the criteria laid out in ANSI Z21.40.4 Performance Testing and Rating of Gas-Fired, Air Conditioning and Heat Pump Appliances.

- Note the baseline in this case should be determined via EM&V and the algorithms are provided to allow savings to be calculated from any baseline condition defined in the Efficient Equipment section.

- Time of Sale:

- The planned installation of a new gas heat pump meeting the efficiency standards laid out below that does not meet the criteria for early replacement as described in section C below.

- Note the baseline in this case is the purchase of new equipment that is similar technology to existing equipment. Where unknown, the baseline should be determined via EM&V and the algorithms are provided to allow savings to be calculated from any baseline condition. The calculation of savings is dependent on whether an incentive for the installation has been provided by both a gas and electric utility, only an electric utility, or only a gas utility. SHW savings are calculated based on the fuel and efficiency of the existing unit.

- Early Replacement/Retrofit:

- The early removal of functioning electric or gas space heating and/or cooling systems from service, prior to the natural end of life, and replacement with a new high efficiency commercial gas heat pump system.

- Note the baseline in this case is the existing equipment being replaced. The calculation of savings is dependent on whether an incentive for the installation has been provided by both a gas and electric utility, only an electric utility, or only a gas utility. SHW savings are calculated based on the fuel and efficiency of the existing unit.

- Early Replacement determination will be based on meeting the following conditions:

  - The existing unit is operational when replaced, or

  - The existing unit requires minor repairs to be operational, defined as costing less than 20% of the new baseline replacement cost (as defined in the Measured Cost section of the relevant equipment).

  - All other conditions will be considered Time of Sale.

For the Baseline efficiency of the existing unit being replaced:

  - Use actual existing efficiency whenever possible.

  - If the efficiency of the existing unit is unknown, use assumptions based on the Federal minimum standards provided in tables below.

  - If the operational status or repair cost of the existing unit is unknown use time of sale assumptions.

###### Definition of Efficient Equipment

Gaseous fuel heat pumps for space heating/cooling and domestic/service hot water heating. The table below shows the current gas heat pump products in two broad commercial categories – water heating and space heating/cooling. The table additionally lists applicable industry test methods and the primary efficiency metric.

###### Definition of Baseline Equipment

The baseline equipment includes Service Hot Water, Space Heating, and Air-Conditioning.

New Construction:

The 2018 edition of the IECC went into effect on 7/1/19 for commercial facilities and is applicable here.

To calculate savings with an electric baseline, the baseline equipment is assumed to be an Air Source Heat Pump meeting the Federal Standard efficiency level as outlined in Table 2 below.

To calculate savings with a chiller/unitary cooling system (Table 3) and boiler/furnace baseline (Table 4 for boilers and Table 5 for warm air furnaces), the baseline equipment is assumed to meet the minimum standard efficiencies as outlined in their respective tables.

To calculate savings with water heater applications, the baseline equipment is assumed to meet the minimum standard efficiencies outlined in Table 6.

Table 2: IECC 2018 Air-Source Heat Pumps Minimum Efficiency Requirements (effective 7/1/2019)

(Table 2: Continued)

Table 3: IECC 2018 Electric Chillers, Air-Cooled and Water-Cooled Minimum Efficiency Requirements (effective 7/1/2019)

Note Code of Federal Regulations for gas-fired hot water boilers manufactured after January 15, 2021 require <300,000 Btu/hr hot water boilers to be 84% AFUE and <300,000 Btu/hr steam boilers to be 82% AFUE (10 CFR 432(e)(3)). This should be assumed baseline from 1/1/2022.

Table 4: IECC 2018 Boiler Minimum Efficiency Requirements (effective 7/1/2019)

Table 5: IECC 2018 Warm-Air Furnace Minimum Efficiency Requirements (effective 7/1/2019)

Table 6: IECC 2018 Water Heater Minimum Efficiency Requirements (effective 7/1/2019)

Time of Sale: The baseline for this measure is a new replacement unit of the same system type as the existing unit, meeting the minimum efficiencies provided above.

Early Replacement / Retrofit: The baseline for this measure is the efficiency of the existing heating, cooling, and hot water equipment for the assumed remaining useful life of the existing unit, and a new baseline heating and cooling system for the remainder of the measure life (as provided in tables above).

###### Deemed Lifetime of Efficient Equipment

The expected measure life of the gas heat pump is assumed to be 15 years for a natural gas heat pump.

For early replacement, the remaining life of existing equipment is assumed to be 6 years for an air-source heat pump and Central A/C, 6 years for a furnace, and 8 years for boilers and ground source heat pumps.

###### Deemed Measure Cost

New Construction and Time of Sale: Incremental costs of the gas heat pump should be used. This would be the actual installed cost of the heat pump equipment as well as system commissioning costs, minus the assumed installation cost of the baseline equipment.

Early Replacement: The actual installed cost of the gas heat pump should be used. The assumed deferred cost of replacing existing equipment with a new baseline is 1/3 of the incremental cost. This future cost should be discounted to present value using the nominal societal discount rate.

The incremental cost of gas heat pump over various replacement equipment is shown in Table 7.

Table 7: Incremental Cost of Commercial Gas Heat Pump

Guide to read incremental cost:

Example 1: for a gas boiler and air cooled electric chiller being replaced with a gas heat pump, the incremental cost will be Cost of GHP – (Cost of Natural Gas Boiler + Air-Cooled Electric Chiller) = $3,800 - ($594 + $988) = $2,218.

Example 2: for a gas boiler and gas-fired water heater being replaced with a gas heat pump, the incremental cost will be Cost of GHP – (Cost of Natural Gas Boiler + Gas Fired Water Heater) = $3,800 – ($594+$384) = $2,822.

###### Loadshape

Depending on the baseline conditions, the appropriate loadshapes will be a combination of some, but not all, of the below. Note for the purpose of cost-effectiveness screening for a fuel switching scenario, the cooling therm increase and heating therm decrease should be calculated separately such as the appropriate loadshape (i.e. Loadshape Co4 – Commercial Electric Heating and Loadshape C03 – Commercial Cooling, respectively) can be applied.

Loadshape C02 – Commercial Electric SHW

Loadshape C03 – Commercial Cooling

Loadshape C04 – Commercial Electric Heating (if replacing building with no existing cooling)

Loadshape C05 – Commercial Electric Heating and Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits. The second represents the average savings over the defined summer peak period and is presented so that savings can be bid into PJM’s capacity market. Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP 	= Summer System Peak Coincidence Factor for Commercial Cooling (during system peak hour)

= 91.3%

CFPJM	= PJM Summer Peak Coincidence Factor for Commercial Cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings and natural gas savings

Non Fuel Switch Measures:

Δtherms 	= ΔthermsSPACE + ΔthermsSHW

Space Heating Savings

ΔthermsSPACE	= EFLH * Capacity * ((EfficiencyEE - EfficiencyBase) / EfficiencyBase) / 100,000

Where:

EFLH 	= Equivalent Full Load Hours for heating in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

Capacity 	= Nominal Heating Input Capacity Size (Btu/hr) for efficient unit not existing unit

= custom gas-fired heat pump input capacity in Btu/hr

EfficiencyBase	= Baseline Efficiency Rating, dependant on year and boiler type. See Table 4 above.

EfficiencyEE	= Rated Commerical Gas Heat Pump space heating efficiency, expressed as a fuel-input only COPGas, for the nominal capacity rating condition

Hot water boiler baseline:

| Year | Efficiency |
| --- | --- |
| Hot Water <300,000 Btu/hr < January 1, 2022 | 82% AFUE |
| Hot Water <300,000 Btu/hr ≥ January 1, 2022 | 84% AFUE |
| Hot Water ≥300,000 & ≤2,500,000 Btu/hr | 80% ET |
| Hot Water >2,500,000 Btu/hr | 82% EC |

For example, a 150,000 BTU/hr water boiler meeting COPGas 1.4 is installed in Rockford at a high rise office building , in the year 2022

ΔTherms	= 2,089* 150,000  * (1.4-0.840)/0.840) / 100,000 Btu/Therm

= 2,089.0 therms

Service Hot Water Savings:

∆ThermsSHW=Tout-Tin * HotWaterUseGallon*γWater*1.0*1TEgasbase- 1COPEff100,000

Where:

Tout		= Tank temperature

= 140°F

Tin		= Incoming water temperature from well or municipal system

= 54°F

HotWaterUseGallon	= Estimated annual hot water consumption (gallons)

= Actual, if possible to provide reasonable custom estimate. If not, two methodologies are provided to develop an estimate:

- Consumption per usable storage tank capacity = Capacity * Consumption/cap

Where:	Capacity		= Usable capacity of hot water storage tank in gallons

= Actual

Consumption/cap = Estimate of consumption per gallon of usable tank    capacity, based on building type:

| Building Type | Consumption/Cap |
| --- | --- |
| Convenience | 528 |
| Education | 568 |
| Grocery | 528 |
| Health | 788 |
| Large Office | 511 |
| Large Retail | 528 |
| Lodging | 715 |
| Other Commercial | 341 |
| Restaurant | 622 |
| Small Office | 511 |
| Small Retail | 528 |
| Warehouse | 341 |
| Nursing | 672 |
| Multi-Family | 894 |

- Consumption per unit area by building type = (Area/1000) * Consumption/1,000 sq.ft.

Where:	Area  	= Area in sq.ft that is served by SHW boiler

= Actual

Consumption/1,000 sq.ft. = Estimate of SHW consumption per 1,000 sq.ft. based on building type:

| Building Type | Consumption/1,000 sq.ft. |
| --- | --- |
| Convenience | 4,594 |
| Education | 7,285 |
| Grocery | 697 |
| Health | 24,540 |
| Large Office | 1,818 |
| Large Retail | 1,354 |
| Lodging | 29,548 |
| Other Commercial | 3,941 |
| Restaurant | 44,439 |
| Small Office | 1,540 |
| Small Retail | 6,111 |
| Warehouse | 1,239 |
| Nursing | 30,503 |
| Multi-Family | 15,434 |

γWater		= Specific weight capacity of water (lb/gal) = 8.33 lbs/gal

1	= Specific heat of water (Btu/lb.°F)

100,000		= Converts Btu to Therms

TEgasbase  	= Rated efficiency of baseline water heater (expressed as Uniform Energy Factor (UEF) or Thermal Efficiency as provided below).

COPEff	= Rated efficiency of the commercial gas heat pump as certified expressed as Uniform Energy Factor (UEF) or Coefficient of Performance as provided below.

Note the same draw pattern (very small, low, medium, and high draw) should be used for both baseline and efficient units.

| Equipment Type | Sub Category | Draw Pattern | Federal Standard – Uniform Energy Factor or Thermal Efficiency |
| --- | --- | --- | --- |
| Residential-duty Commercial High Capacity Storage Gas-Fired Storage Water Heaters > 75,000 Btu/h | ≤120 gallon tanks | Very small | UEF = 0.2674 – (0.0009 * Rated Storage Volume in Gallons) |
|  |  | Low | UEF = 0.5362 – (0.0012 * Rated Storage Volume in Gallons) |
|  |  | Medium | UEF = 0.6002 – (0.0011 * Rated Storage Volume in Gallons) |
|  |  | High | UEF = 0.6597 – (0.0009 * Rated Storage Volume in Gallons) |
| Commercial Gas Storage Water Heaters >75,000 Btu/h | >120 gallon tanks | All | 80% Ethermal, Standby Losses = (Q /800 + 110√Rated Storage Volume in Gallons) |
| Commercial Gas Storage Water Heaters >155,000 Btu/h |  |  |  |
| Commercial Gas Instantaneous Water Heaters > 200,000 Btu/h | <10 gal | All | 80% Ethermal |
|  | ≥10 gal | All | 78% Ethermal |

Draw patterns are based on first hour rating (gallons) for storage tanks and maximum flow (GPM) for instantaneous as shown below:

| Storage Water Heater Draw Pattern |  |
| --- | --- |
| Draw Pattern | First Hour Rating (gallons) |
| Very Small | ≥ 0 and < 18 |
| Low | ≥ 18 and < 51 |
| Medium | ≥ 51 and < 75 |
| High | ≥ 75 |

| Instantaneous Water Heater Draw Pattern |  |
| --- | --- |
| Draw Pattern | Max GPM |
| Very Small | ≥ 0 and < 1.7 |
| Low | ≥ 1.7 and < 2.8 |
| Medium | ≥ 2.8 and < 4 |

For example, for a 200,000 Btu/h, 150 gallon, GHP with a COP = 1.4 installed in a 1500 ft2 restaurant:

ΔTherms		= ((140 – 54) * ((1,500/1,000) * 44,439) * 8.33 * 0.975 * (1/0.8 - 1/1.4))/100,000

= 249.4 Therms

Fuel Switch Measures:

Fuel switching measures must produce positive total annual source fuel savings (i.e., reduction in source Btus) in order to qualify. This is determined as follows (note for early replacement measures the lifetime savings should be calculated by calculating savings for the remaining useful life of the existing equipment and for the remaining measure life):

SourceEnergySavings (MMBTUs)	= (ElectricHeatReplaced - GHPEnergyConsumedHeat) + (ElectricCoolingReplaced - GHPEnergyConsumedCool ) + (ElectricWaterHeatReplaced -  GHPEnergyConsumedSHW)

If SourceEnergySavings calculated above is positive, the measure is eligible.

Electric Space Heating Replaced with Natural Gas Heat Pump

ElectricHeatReplaced [MMBTUsource]	= (kBtu/hrheat * EFLHheat * (1/COPbase)) * 1000/3412 * (LifetimeHgrid * (1 + ElectricT&D))/ 1,000,000

GHPEnergyConsumedHeat [MMBTUsource]	= ((kBtu/hrheat * EFLHheat * (1/COPGHP)) / 1000) * (1 + GasSystemDistributionLoss)

kBtu/hrheat 	= capacity of the heating equipment in kBtu per hour (1 ton of heating capacity equals 12 kBtu/hr).

COPbase	= Coefficient of performance of the baseline equipment, or thermal efficiency if applicable, at nominal condition

= based on the applicable Code on the date of equipment purchase (if unknown assume current Code). If rating is HSPF, COP = HSPF / 3.413

EFLHHeat		= Heating Equivalent Full Load Hours

Dependent on building type and Existing Buildings or New Construction, provided in section 4.4 HVAC End Use

COPGHP		= Coefficient of performance of the GHP equipment at nominal condition

= Actual installed

LifetimeHgrid	= Average Heat rate of the grid in BTU/kWh over the lifetime of the measure. Used to  calculate eligibility

= 7,700 BTU/kWh.

FirstYearHgrid	= Heat rate of the grid in BTU/kWh for first year of the measure. Used to calculate savings for first 6 years of measure life.

= 8,600 BTU / kWh

PostAdjHgrid	= Heat rate of the grid in BTU/kWh for remaining years of the measure life. Used to calculated savings for remaining years of measure life resulting in approximately equal lifetime savings.

= 7,200 BTU/kWh

ElectricT&D	= Electric marginal Transmission and Distribution Loss Factor

ComEd: 		10.7%

Ameren: 	11.3%

GasSystemDistributionLoss	= Gas System and Distribution Loss Factor

= 0%

Electric Cooling Replaced with Natural Gas Heat Pump

ElectricCoolingReplaced  [MMBTUsource]	= (kBtu/hrcool * EFLHcool * (1/EERbase)) * (LifetimeHgrid * (1 + ElectricT&D))/ 1,000,000

GHPEnergy Consumedcool [MMBTUsource]	= ((kBtu/hrcool* EFLHcool * (1/COPGHP)) / 1000) * (1 + GasSystemDistributionLoss)

kBtu/hrcool 	= capacity of the cooling equipment in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr).

EERbase		= Energy Efficiency Ratio of the baseline equipment at nominal condition

EFLHcool	= Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

COPGHP		= Coefficient of performance of the GHP equipment at nominal condition

= Actual installed

Electric Water Heating Replaced with Natural Gas Heat Pump

ElectricWaterHeatReplaced [MMBTUsource]	= ((Tout-Tin)  * HotWaterUsegallon* γWater * 1.0 * (1/TEelecbase)) / 3412 *  (LifetimeHgrid * (1 + ElectricT&D))/ 1,000,000

GHPEnergyConsumedSHW [MMBTUsource]	= (Tout-Tin)  * HotWaterUsegallon*γWater * 1.0 * (1/COPGHP) / 1,000,000) * (1 + GasSystemDistributionLoss)

**See previous nonfuel switch section for most descriptions

TEelecbase  	= Rated efficiency of baseline water heater expressed as Uniform Energy Factor (UEF) or Thermal Efficiency (TE) or Coefficient of Performance (COP), if not provided for resistance-type electric water heating assume TEelec,base = 0.98

COPGHP		= Coefficient of performance of the GHP equipment

= Actual installed

Total Therm Savings 		= SourceEnergySavings * 10/(1 + GasSystemDistributionLoss)

Example:

[for illustrative purposes an ElectricT&D of 10.7%, GasSystemDistibutionLoss of 1.4% is used]

A 3,000-squarefoot building with a 120 kBtu/hr output gas heat pump system replacing existing baseline equipment with COP of 1.3 in heating, cooling, and water heating in a Chicagoland public elementary school. The baseline equipment being replaced are all electric heating, cooling, and service hot water heater.

Baseline equipment efficiency: electric air source heating – 2.25 COP; electric air source cooling – 10.8 EER. Electric service hot water heater – 0.98 TE.

Heating Source MMBTU Savings = ElectricHeatReplaced - GHPEnergyConsumedHeat

ElectricHeatReplaced [MMBTUsource]	= (kBtu/hrheat * EFLHheat * (1/COPbase)) * 1000/3412 * (LifetimeHgrid * (1 + ElectricT&D))/ 1,000,000

= (120 * 1603 * (1/2.25)) * 1000/3412 * (7,700 * (1 + 0.107))/1,000,000

= 213.6

GHPEnergyConsumedHeat [MMBTUsource]	= ((kBtu/hrheat * EFLHheat * (1/COPGHP)) / 1000) * (1 + GasSystemDistributionLoss)

= (120 * 1603 * 1/1.3)/1000 * (1 + 0.014)

= 150.0

Cooling Source MMBTU Savings = ElectricCoolingReplaced- GHPEnergy Consumedcool

ElectricCoolingReplaced  [MMBTUsource]	= (kBtu/hrcool * EFLHcool * (1/EERbase)) * (LifetimeHgrid * (1 + ElectricT&D))/ 1,000,000

= (120 * 837 * 1/10.8) * (7,700 * (1 + 0.107))/1,000,000

=  79.3

GHPEnergy Consumedcool [MMBTUsource]	= ((kBtu/hrcool* EFLHcool * (1/COPGHP)) / 1000) * (1 + GasSystemDistributionLoss)

= (120 * 837 * 1/1.3) /1000 * (1 + 0.014)

=

78.3

Service Hot Water Heater Source MMBTU Savings = ElectricWaterHeatReplaced - GHPEnergyConsumedSHW

ElectricWaterHeatReplaced [MMBTUsource]	= ((Tout-Tin)  * HotWaterUsegallon* γWater * 1.0 * (1/TEelecbase)) / 3412 *  (LifetimeHgrid * (1 + ElectricT&D))/ 1,000,000

= ((140 - 54) * (7285*3) * 8.33 * 1 *(1/0.98)) / 3412 * (7,700 * (1 + 					0.107))/1,000,000

= 39.9

GHPEnergyConsumedSHW [MMBTUsource]	= ((Tout-Tin)  * HotWaterUsegallon*γWater * 1.0 * (1/COPGHP) / 1,000,000) * (1 + GasSystemDistributionLoss)

= (((140 - 54) * (7285*3) * 8.33 * 1.0 * (1/1.3))/1,000,000) * (1 + 0.014)

=  12.2

Example continued:

Total Source MMBTU Savings		= (213.6 – 150.0 ) + (79.3 – 78.3) + (39.9 – 12.2)

=  92.3

Total Therm Savings 		= 92.3 * 10/(1 + 0.014)

= 910.3 Therms

Summer Coincident Peak Demand Savings

New Construction / Time of Sale:

ΔkW 	= (kBtu/hr * (1/EERbase)) * CF

Early Replacement / Retrofit:

ΔkW	= (kBtu/hr) * [(1/EERexist)] * CF

Where:

EERbase 	= Energy Efficiency Ratio of the baseline equipment

EERexist 		= Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

For example, a 120 kBtu/hr electric air source cooling with a 10.8 EER replaced with a gas heat pump in Chicago would save:

ΔkWSSP 	= (120) * [(1/10.8)] * .913

= 10.14 kW

###### Natural Gas Savings

Calculation provided together with Electric Energy Savings above.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A. The installed cost of gas heat pump includes O&M agreement.

###### Cost Effectiveness Screening and Load Reduction Forecasting when Fuel Switching

This measure can involve fuel switching from electric to gas.

For the purposes of forecasting load reductions due to fuel switch HP projects; changes in site energy use at the customer’s meter (using ΔkWh algorithm below) adjusted for utility line losses (at-the-busbar savings), customer switching estimates, NTG, and any other adjustment factors deemed appropriate, should be used.

The inputs to cost effectiveness screening should reflect the actual impacts on the electric and fuel consumption at the customer meter and, for fuel switching measures, this will not match the output of the calculation/allocation methodology presented in the “Electric Energy Savings” and “Natural Gas Savings” sections above. Therefore in addition to the calculation of savings claimed, the following values should be used to assess the cost effectiveness of the measure. For Early Replacement measures, the efficiency terms of the existing unit should be used for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 6 years for furnace, 8 years for boilers or GSHP, 15 years for electric resistance), and the efficiency terms for a new baseline unit should be used for the remaining years of the measure.

ΔTherms	= [Increased Consumption]

ΔTherms 	= - (ThermsSPACE + ThermsSHW + ThermsCool)

ThermsSPACE	= ((kBtu/hrheat) * 1/COPGHP * EFLHheat)* 1000/ 100,000

ThermsSHW 	= ((Tout-Tin)  * HotWaterUsegallon*γWater *1 * (1/COPGHP))/100,000

ThermsCool 	= ((kBtu/hrcool) * 1/COPGHP * EFLHcool) * 1,000/100,000

ΔkWh 		= [Replaced Consumption]

ΔkWh 		= (kWhSPACE + kWhSHW + kWhCool)

kWhSPACE 	= (kBtu/hrheat)/3.412 * 1/COPbase * EFLHheat

kWhSHW		= ((Tout-Tin)  * HotWaterUsegallon*γWater *0.975 * (1/TEelecbase))/3413

kWhCool 		= (kBtu/hrcool) * (1/EERbase) * EFLHcool

###### Measure Code:  CI-HVC-GFHP-V01-220101

###### Review Deadline: 1/1/2023

## Lighting End Use

The commercial lighting measures use a standard set of variables for hours of use, waste heat factors, coincident factors and HVAC interaction effects.  This table has been developed based on information provided by the various stakeholders.  For ease of review, the table is included here and referenced in each measure.

The building characteristics of the eQuest models can be found in the reference table named “EFLH Building Descriptions Updated 2014-11-21.xlsx”. The OpenStudio models are based upon the DOE Prototypes described in NREL’s “U.S. Department of Energy Commercial Reference Building Models of the National Building Stock” and a calibration log file that documents all of the variations made to each model to get them calibrated is provided in “IL-Calibration-Log_2019-08-27.xlsx”.  Documents and all models are  all available on the SharePoint site.

Note where a measure installation is within a building or application that does not fit with any of the defined building types below, the user should apply custom assumptions where it is reasonable to estimate them, else the building of best fit should be utilized.

| Building/Space Type | Fixture Annual Operating Hours | Screw based bulb Annual Operating hours | Waste Heat Cooling Energy WHFe | Waste Heat Cooling DemandWHFd | Coinci-dence Factor CF | Waste Heat Gas Heating IFTherms | Waste Heat Electric Resistance Heating IFkWh | Waste Heat Electric Heat Pump Heating IFkWh | Model Source |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Agriculture – Chicken Broilers | 3,251 | 3,251 | 1.00 | 1.00 | 0.76 | 0.000 | 0.000 | 0.000 | n/a |
| Agriculture – Chicken Breeders | 4,606 | 4,606 | 1.00 | 1.00 | 0.95 | 0.000 | 0.000 | 0.000 | n/a |
| Agriculture – Chicken Layers | 4,914 | 4,914 | 1.00 | 1.00 | 0.95 | 0.000 | 0.000 | 0.000 | n/a |
| Agriculture – Turkey Hens | 2,231 | 2,231 | 1.00 | 1.00 | 0.76 | 0.000 | 0.000 | 0.000 | n/a |
| Agriculture – Turkey Toms | 5,351 | 5,351 | 1.00 | 1.00 | 0.95 | 0.000 | 0.000 | 0.000 | na |
| Agriculture – Turkey Breeder Hens | 4,396 | 4,396 | 1.00 | 1.00 | 0.95 | 0.000 | 0.000 | 0.000 | n/a |
| Agriculture – Turkey Breeder Toms | 5,446 | 5,446 | 1.00 | 1.00 | 0.95 | 0.000 | 0.000 | 0.000 | n/a |
| Agriculture – Dairy Long Day Lighting | 6,205 | 6,205 | 1.00 | 1.00 | 0.95 | 0.000 | 0.000 | 0.000 | n/a |
| Assisted Living | 7,862 | 5,950 | 1.14 | 1.30 | 0.66 | 0.035 | 0.823 | 0.358 | eQuest |
| Auto Dealership | 4,099 | 2,935 | 1.16 | 1.24 | 0.97 | 0.013 | 0.315 | 0.137 | OpenStudio |
| Childcare/Pre-School | 2,860 | 2,860 | 1.17 | 1.29 | 0.72 | 0.018 | 0.420 | 0.183 | eQuest |
| College | 3,395 | 2,588 | 1.02 | 1.54 | 0.63 | 0.023 | 0.548 | 0.238 | OpenStudio |
| Convenience Store | 4,672 | 3,650 | 1.09 | 1.26 | 0.76 | 0.035 | 0.828 | 0.360 | eQuest |
| Drug Store | 4,093 | 2,935 | 1.05 | 1.34 | 1.00 | 0.017 | 0.394 | 0.171 | OpenStudio |
| Elementary School | 3,038 | 2,118 | 1.04 | 1.51 | 0.65 | 0.019 | 0.455 | 0.198 | OpenStudio |
| Emergency Services | 2,698 | 3,088 | 1.06 | 1.09 | 0.65 | 0.001 | 0.014 | 0.006 | OpenStudio |
| Garage | 3,401 | 3,540 | 1.00 | 1.00 | 0.92 | 0.000 | 0.000 | 0.000 | eQuest |
| Garage, 24/7 lighting | 8,766 | 8,766 | 1.00 | 1.00 | 1.00 | 0.000 | 0.000 | 0.000 | eQuest |
| Grocery | 5,468 | 3,650 | 1.05 | 1.22 | 0.82 | 0.010 | 0.230 | 0.100 | OpenStudio |
| Healthcare Clinic | 3,890 | 4,207 | 1.14 | 1.04 | 0.67 | 0.020 | 0.463 | 0.201 | OpenStudio |
| High School | 3,038 | 2,327 | 1.15 | 1.40 | 0.65 | 0.011 | 0.249 | 0.108 | OpenStudio |
| Hospital - CAV no econ | 7,616 | 4,207 | 1.17 | 1.32 | 0.56 | 0.009 | 0.211 | 0.092 | OpenStudio |
| Hospital - CAV econ | 7,616 | 4,207 | 1.14 | 1.27 | 0.56 | 0.009 | 0.205 | 0.089 | OpenStudio |
| Hospital - VAV econ | 7,616 | 4,207 | 1.13 | 1.35 | 0.56 | 0.006 | 0.148 | 0.064 | OpenStudio |
| Hospital - FCU | 7,616 | 4,207 | 1.16 | 1.42 | 0.56 | 0.000 | 0.000 | 0.000 | OpenStudio |
| Manufacturing Facility | 4,618 | 2,629 | 1.02 | 1.04 | 0.81 | 0.012 | 0.270 | 0.117 | eQuest |
| MF - High Rise - Common | 6,138 | 5,950 | 1.20 | 1.24 | 0.90 | 0.005 | 0.109 | 0.047 | OpenStudio |
| MF - Mid Rise - Common | 5,216 | 5,950 | 1.11 | 1.16 | 0.62 | 0.021 | 0.484 | 0.211 | OpenStudio |
| Hotel/Motel - Guest | 2,390 | 777 | 1.17 | 1.21 | 0.46 | 0.020 | 0.468 | 0.204 | OpenStudio |
| Hotel/Motel - Common | 6,138 | 4,542 | 1.09 | 1.26 | 0.85 | 0.017 | 0.406 | 0.176 | OpenStudio |
| Movie Theater | 3,506 | 5,475 | 1.11 | 1.38 | 0.53 | 0.029 | 0.673 | 0.293 | eQuest |
| Office - High Rise - CAV no econ | 2,886 | 3,088 | 1.22 | 1.30 | 0.60 | 0.006 | 0.149 | 0.065 | OpenStudio |
| Office - High Rise - CAV econ | 2,886 | 3,088 | 1.00 | 1.07 | 0.57 | 0.039 | 0.905 | 0.394 | eQuest |
| Office - High Rise - VAV econ | 2,886 | 3,088 | 1.06 | 1.65 | 0.60 | 0.015 | 0.345 | 0.150 | OpenStudio |
| Office - High Rise - FCU | 2,886 | 3,088 | 1.21 | 1.17 | 0.60 | 0.007 | 0.153 | 0.067 | OpenStudio |
| Office - Low Rise | 2,698 | 3,088 | 1.10 | 1.26 | 0.52 | 0.010 | 0.231 | 0.100 | OpenStudio |
| Office - Mid Rise | 3,266 | 3,088 | 1.10 | 1.36 | 0.60 | 0.016 | 0.378 | 0.164 | OpenStudio |
| Religious Building | 2,085 | 1,664 | 1.12 | 1.37 | 0.48 | 0.015 | 0.356 | 0.155 | eQuest |
| Restaurant | 5,571 | 4,784 | 1.08 | 1.10 | 1.00 | 0.009 | 0.208 | 0.090 | OpenStudio |
| Retail - Department Store | 4,099 | 2,935 | 1.06 | 1.06 | 0.94 | 0.015 | 0.346 | 0.150 | OpenStudio |
| Retail - Strip Mall | 4,093 | 2,935 | 1.12 | 1.29 | 0.71 | 0.019 | 0.450 | 0.196 | eQuest |
| Warehouse | 3,135 | 4,293 | 1.02 | 1.17 | 0.85 | 0.016 | 0.378 | 0.164 | OpenStudio |
| Unknown | 3,379 | 3,612 | 1.08 | 1.30 | 0.67 | 0.015 | 0.354 | 0.154 | n/a |
| Exterior – dusk to dawn | 4,303 | 4,303 | 1.00 | 1.00 | 0.00 | 0.000 | 0.000 | 0.000 | n/a |
| Exterior – dusk to business close | See calculation below |  | 1.00 | 1.00 | 0.00 | 0.000 | 0.000 | 0.000 | n/a |
| Low-Use Small Business | 2,954 | 2,954 | 1.31 | 1.53 | 0.66 | 0.023 | 0.524 | 0.262 | n/a |
| Uncooled Building | Varies | varies | 1.00 | 1.00 | 0.66 | 0.014 | 0.320 | 0.160 | n/a |
| Refrigerated Cases | 5,802 | n/a | 1.29 | 1.29 | 1.00 | 0.000 | 0.000 | 0.000 | n/a |
| Freezer Cases | 5,802 | n/a | 1.50 | 1.5 | 1.00 | 0.000 | 0.000 | 0.000 | n/a |

Annual Operating Hours – Spaces with Lighting Controls

For spaces where occupancy or daylight sensors are known to be already installed, the user should adjust the Annual Operating Hours using the formula below. For v9.0, the TAC agreed that if current state is unknown by the implementer, then subsequent evaluation should assume the space does not have lighting controls. Over 2021 program year, this should be evaluated and the TAC will determine if a different unknown assumption should be used from V10 on.

Sensor Controlled Hours = Annual Operating Hours * (1- ESF)

Where:

Annual Operating Hours	= Average hours of use per year for specific space type, provided in the Reference Table above.

ESF 	= Energy Savings factor (represents the percentage reduction to the operating Hours from the non-controlled baseline lighting system),

Table from Measure 4.5.10 Lighting Controls:

| Lighting Control Type | Energy Savings Factor |
| --- | --- |
| Fixture Measurement of Control savings through Networked Trending | Custom |
| Interior Occupancy Sensor (Switch, Wall, Fixture or Remote Mounted or Integrated in Fixture) | 24% 34% with High End Trim |
| Interior Occupancy Sensor configured as “Vacancy Sensor” (Switch, Wall, Fixture or Remote Mounted or Integrated in Fixture) | 31% 41% with High End Trim |
| Interior Daylight Sensor (Wall, Fixture or Remote Mounted) | 28% 38% with High End Trim |
| Interior Dual Occupancy & Daylight Sensor (Integrated of Fixture Mounted) | 38% 48% with High End Trim |
| Interior Luminaire-Level Lighting Controls | 50% |
| Refrigerated Case Occupancy Sensor – Freezer and Cooler | 27% |
| Exterior Occupancy Sensor | 41% |
| No Lighting Control | 0% |

Note, if a program is installing lighting fixtures and controls, the interactive effect should be accounted for by either assuming:

- Fixture watt savings for full annual operating hours, control savings on efficient fixture

Or

- Control savings on baseline fixture, fixture watt savings for “sensor controlled hours”.

Exterior Lighting Hours – dusk to business close

Hours	= (6.19 * Days) + (%Adj * Days)

Where:

6.19        	= Average hours per day between dusk and midnight

Days      	= Days of business operation

= Actual

%Adj     	= Percent adjustment dependent on hour closing

| Business closes at | 4pm | 5pm | 6pm | 7pm | 8pm | 9pm | 10pm | 11pm | 12pm | 1am | 2am | 3am |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| %Adj | -619% | -604% | -564% | -500% | -400% | -300% | -200% | -100% | 0% | 100% | 200% | 300% |

For example a business open until 8pm, 260 days per year, would assume:

Hours 	= (6.19 * 260) + (-400% * 260) = 569.4 hours

### Commercial ENERGY STAR Compact Fluorescent Lamp (CFL) – Retired 12/31/2018, Removed in v8

### Fluorescent Delamping

###### Description

This measure addresses the permanent removal of existing 8’, 4’, 3’, and 2’ fluorescent lamps. Unused lamps, lamp holders, and ballasts must be permanently removed from the fixture. This measure is applicable when retrofitting from T12 lamps to T8 lamps or simply removing lamps from a T8 fixture. Removing lamps from a T12 fixture that is not being retrofitted with T8 lamps are not eligible for this incentive.

Customers are responsible for determining whether or not to use reflectors in combination with lamp removal in order to maintain adequate lighting levels. Lighting levels are expected to meet the Illuminating Engineering Society of North America (IESNA) recommended light levels. Unused lamps, lamp holders, and ballasts must be permanently removed from the fixture and disposed of in accordance with local regulations. A pre-approval application is required for lamp removal projects.

This measure was developed to be applicable to the following program types: RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Savings are defined on a per removed lamp basis. The retrofit wattage (efficient conditioned) is therefore assumed to be zero. The savings numbers provided below are for the straight lamp removal measures, as well as the lamp removal and install reflector measures.  The lamp installed/retrofit is captured in another measure.

###### Definition of Baseline Equipment

The baseline condition is either a T12 or a T8 lamp with default wattages provided below. Note, if the program does not allow for the lamp type to be known, then a T12:T8 weighting of 40%:60% can be applied.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 11 years per DEER 2005.

###### Deemed Measure Cost

The incremental capital cost is provided in the table below:

| Measure Category | Value | Source |
| --- | --- | --- |
| 8-Foot Lamp Removal | $16.00 | ComEd/KEMA regression |
| 4-Foot Lamp Removal | $12.00 | ICF Portfolio Plan |
| 8-Foot Lamp Removal with reflector | $30.00 | KEMA Assumption |
| 4-Foot Lamp Removal with reflector | $25.00 | KEMA Assumption |
| 2-Foot or 3-Foot Removal | $12.35 | KEMA Assumption |
| 2-Foot or 3-Foot Removal with reflector | $25.70 | KEMA Assumption |

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the location type. Values are provided for each building type in the reference section below.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh	=((WattsBase-WattsEE)/1000) * ISR * Hours * WHFe

Where:

WattsBase	= Assume wattage reduction of lamp removed

|  | Wattage of lamp removed |  | Weighted average |
| --- | --- | --- | --- |
|  | T8 | T12 | 40% T12, 60% T8 |
| 8-ft T8 | 38.6 | 60.3 | 47.3 |
| 4-ft T8 | 19.4 | 33.7 | 25.1 |
| 3-ft T8 | 14.6 | 40.0 | 24.8 |
| 2-ft T8 | 9.8 | 28.0 | 17.1 |

WattsEE	= 0

ISR	 	= In Service Rate or the percentage of units rebated that get installed.

=100% if application form completed with sign off that equipment permanently removed and disposed of.

Hours 	= Average hours of use per year are provided in Reference Table in Section 4.5. If unknown use the Miscellaneous value.

WHFe	= Waste heat factor for energy to account for cooling energy savings from efficient lighting are provided below for each building type in Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

For example, delamping a 4 ft T8 fixture in an office building:

ΔkWh	=((19.4 - 0)/1000) * 1.0 * 4439 * 1.25

= 107.6 kWh

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = (((WattsBase-WattsEE)/1000) * ISR * Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

For example, delamping a 4 ft T8 fixture in a heat pump heated office building:

ΔkWhheatpenalty	=((19.4 - 0)/1000) * 1.0 * 4439 * -0.151

=-13.0 kWh

###### Summer Coincident Peak Demand Savings

ΔkW	= ((WattsBase-WattsEE)/1000) * ISR * WHFd * CF

Where:

WHFd	= Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings is provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value..

CF 	= Summer Peak Coincidence Factor for measure is provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value..

Other factors as defined above

For example, delamping a 4 ft T8 fixture in an office building:

ΔkW	=((19.4 - 0)/1000) * 1.0 * 1.3 * 0.66

= 0.017 kW

###### Natural Gas Energy Savings

Heating Penalty if fossil fuel heated building (or if heating fuel is unknown):

ΔTherms  = (((WattsBase-WattsEE)/1000) * ISR * Hours *- IFTherms

Where:

IFTherms	= Lighting-HVAC Interation Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

Other factors as defined above

For example, delamping a 4 ft T8 fixture in an office building:

ΔTherms	=((19.4 - 0)/1000) * 1.0 * 4439 * -0.016

=-1.4 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-LTG-DLMP-V03-210101

###### Review Deadline: 1/1/2026

### High Performance and Reduced Wattage T8 Fixtures and Lamps

###### Description

This measure applies to “High Performance T8” (HPT8) lamp/ballast systems that have higher lumens per watt than standard T8 systems.  This measure applies to the installation of new equipment with efficiencies that exceed that of the equipment that would have been installed following standard market practices and is applicable to time of sale as well as retrofit measures.  Retrofit measures may include new fixtures or relamp/reballast measures. In addition, options have been provided to allow for the “Reduced Wattage T8 lamps” or RWT8 lamps that result in re-lamping opportunities that produce equal or greater light levels than standard T8 lamps while using fewer watts.

If the implementation strategy does not allow for the installation location to be known, a deemed split of 100% Commercial and 0% Residential should be used.

This measure was developed to be applicable to the following program types: TOS, EREP, DI.

If applied to other program types, the measure savings should be verified.

The measure applies to all commercial HPT8 installations excluding new construction and major renovation or change of use measures (see lighting power density measure).  Lookup tables have been provided to account for the different types of installations. Whenever possible, actual costs and hours of use should be utilized for savings calculations. Default new and baseline assumptions have been provided in the reference tables.  Default component costs and lifetimes have been provided for Operating and Maintenance Calculations. Please see the Definition Table to determine applicability for each program. HPT8 configurations not included in the TRM may be included in custom program design using the provided algorithms as long as energy savings is achieved. The following table defines the applicability for different programs:

| Time of Sale (TOS) | Early Replacement (EREP) and Direct Install (DI) |
| --- | --- |
| This measure relates to the installation of new equipment with efficiency that exceeds that of equipment that would have been installed following standard market practices. In general, the measure will include qualifying high efficiency low ballast factor ballasts paired with high efficiency long life lamps as detailed in the attached tables. High-bay applications use this system paired with qualifying high ballast factor ballasts and high performance 32 w lamps. Custom lighting designs can use qualifying low, normal or high ballast factor ballasts and qualifying lamps in lumen equivalent applications where total system wattage is reduced when calculated using the Calculation of Savings Algorithms. | This measure relates to the replacement of existing equipment with new equipment with efficiency that exceeds that of the existing equipment. In general, the retrofit will include qualifying high efficiency low ballast factor ballasts paired with high efficiency long life lamps as detailed in the attached tables. Custom lighting designs can use qualifying low, normal or high ballast factor ballasts and qualifying lamps in lumen equivalent applications where total system wattage is reduced when calculated using the Calculation of Savings Algorithms. High efficiency troffers (new/or retrofit) utilizing HPT8 technology can provide even greater savings. When used in a high-bay application, high-performance T8 fixtures can provide equal light to HID high-bay fixtures, while using fewer watts; these systems typically utilize high ballast factor ballasts, but qualifying low and normal ballast factor ballasts may be used when appropriate light levels are provided and overall wattage is reduced. |

###### Definition of Efficient Equipment

The efficient conditions for all applications are a qualifying HP or RWT8 fixture and lamp/ballast combinations listed on the CEE website under qualifying HP T8 products and qualifying RWT8 products.

The definition of efficient equipment varies based on the program and is defined below:

| Time of Sale (TOS) | Early Replacement (EREP) and Direct Install (DI) |
| --- | --- |
| High efficiency troffers combined with high efficiency lamps and ballasts allow for fewer lamps to be used to provide a given lumen output. High efficiency troffers must have a fixture efficiency of 80% or greater to qualify. Default values are given for a 2 lamp HPT8 fixture replacing a 3 lamp standard efficiency T8 fixture, but other configurations may qualify and the Calculation of savings algorithm used to account for base watts being replaced with EE watts. High bay fixtures must have fixture efficiencies of 85% or greater. RWT8 lamps: 2', 3' and 8' lamps must meet the wattage requirements specified in the RWT8 new and baseline assumptions table. This measure assumes a lamp only purchase. | High efficiency troffers (new or retrofit kits) combined with high efficiency lamps and ballasts allow for fewer lamps to be used to provide a given lumen output. High efficiency troffers must have a fixture efficiency of 80% or greater to qualify. Default values are given for a 2 lamp HPT8 fixture replacing a 3 lamp standard efficiency T8 fixture, but other configurations may qualify and the Calculation of savings algorithm used to account for base watts being replaced with EE watts. High bay fixtures will have fixture efficiencies of 85% or greater. RWT8: 2', 3' and 8' lamps must meet the wattage requirements specified in the RWT8 new and baseline assumptions table. |

###### Definition of Baseline Equipment

The definition of baseline equipment varies based on the program and is defined below:

| Time of Sale (TOS) | Early Replacement (EREP) and Direct Install (DI) |
| --- | --- |
| The baseline is standard efficiency T8 systems that would have been installed. The baseline for high-bay fixtures is pulse start metal halide fixtures, the baseline for a 2 lamp high efficiency troffer is a 3 lamp standard efficiency troffer. | The baseline is the existing system. In July 14, 2012, Federal Standards were enacted that were expected to eliminate T-12s as an option for linear fluorescent fixtures. Through v3.0 of the TRM, it was assumed that the T-12 would no longer be baseline for retrofits from 1/1/2016. However, due to significant loopholes in the legislation, T-12 compliant product is still freely available and in Illinois T-12s continue to hold a significant share of the existing and replacement lamp market. Therefore the timing of the sunsetting of T-12s as a viable baseline has been pushed back and will be revisited in future update sessions. There will be a baseline shift applied to all early replacement measures with a T12 baseline. See table C-1. |

###### Deemed Lifetime of Efficient Equipment

The deemed lifetime of efficient equipment varies based on the program and is defined below:

| Time of Sale (TOS) | Early Replacement (EREP) and Direct Install (DI) |
| --- | --- |
| Fixture lifetime is rated lifetime of fixture/hours of use. If unknown default is 12 years. Fixture retrofits which utilize RWT8 lamps have a lifetime equivalent to the life of the lamp, capped at 15 years. There is no guarantee that a reduced wattage lamp will be installed at time of burnout, but if one is, savings will be captured in the RWT8 measure below. RWT8 lifetime is the life of the product, at the reported operating hours (lamp life in hours divided by operating hours per year – see reference table "RWT8 Component Costs and Lifetime"), capped at 12 years. | Fixture lifetime is rated lifetime of fixture/hours of use. If unknown default is 15 years. As per explanation above, for existing T12 fixtures, a mid life baseline shift should be applied as described in table C-1. Note, since the fixture lifetime is deemed at 12 years, the replacement cost of both the lamp and ballast should be incorporated in to the O&M calculation. |

###### Deemed Measure Cost

The deemed measure cost is found in the reference table at the end of this characterization.

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh  = ((Wattsbase-WattsEE)/1000)  * Hours * WHFe * ISR

Where:

Wattsbase 	= Input wattage of the existing system which  depends on the baseline fixture configuration (number and  type of lamp) and number of fixtures.  Value can be selected from the appropriate reference table as shown below, or a custom value can be entered if the configurations in the tables is not representative of the exisitng system.

| Program | Reference Table |
| --- | --- |
| Time of Sale | A-1: HPT8 New and Baseline Assumptions |
| Early Replacement | A-2: HPT8 New and Baseline Assumptions |
| Reduced Wattage T8, time of sale or Early Replacement | A-3: RWT8 New and Baseline Assumptions |

WattsEE	= New Input wattage of EE fixture which depends on new fixture configuration (number of lamps) and ballast factor and number of fixtures.  Value can be selected from the appropriate reference table as shown below, of a custom value can be entered if the configurations in the tables is not representative of the exisitng system.

| Program | Reference Table |
| --- | --- |
| Time of Sale | A-1: HPT8 New and Baseline Assumptions |
| Early Replacement | A-2: HPT8 New and Baseline Assumptions |
| Reduced Wattage T8, time of sale or Early Replacement | A-3: RWT8 New and Baseline Assumptions |

Hours	= Average hours of use per year as provided by the customer or selected from the Reference Table in Section 4.5, Fixture annual operating hours.  If hours or building type are unknown, use the Miscellaneous value.

WHFe 	= Waste heat factor for energy to account for cooling energy savings from efficient lighting is selected from the Reference Table in Section 4.5 for each building type. If building is un-cooled, the value is 1.0.

ISR 	= In Service Rate or the percentage of units rebated that get installed.

=100% if application form completed with sign off that equipment is not placed into storage

If sign off form not completed assume the following 3 year ISR assumptions:

| Weighted Average 1st year In Service Rate (ISR) | 2nd year Installations | 3rd year Installations | Final Lifetime In Service Rate |
| --- | --- | --- | --- |
| 93.4% | 2.5% | 2.1% | 98.0% |

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = (((WattsBase-WattsEE)/1000) * ISR * Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

###### Summer Coincident Demand Savings

ΔkW  =( (Wattsbase-WattsEE)/1000)  * WHFd*CF*ISR

Where:

WHFd 	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is selected from the Reference Table in Section 4.5 for each building type.   If the building is not cooled WHFd is 1.

CF	= Summer Peak Coincidence Factor for measure is selected from the Reference Table in Section 4.5 for each building type. If the building type is unknown, use the Miscellaneous value of 0.66.

Other factors as defined above

###### Natural Gas Savings

ΔTherms  =  (((WattsBase-WattsEE)/1000) * ISR * Hours *- IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting.  Please select from the Reference Table in Section 4.5 for each building type.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

Actual operation and maintenance costs will vary by specific equipment installed/replaced. See Reference tables for Operating and Maintenance Values;

| Program | Reference Table |
| --- | --- |
| Time of Sale | B-1: HPT8 Component Costs and Lifetime |
| Early Replacement | B-2: HPT8 Component Costs and Lifetime |
| Reduced Wattage T8, time of sale or Early Replacement | B-3: HPT8 Component Costs and Lifetime |

###### Reference Tables

See following page

A-1:  Time of Sale:  HPT8 New and Baseline Assumptions

| EE Measure Description | Nominal Watts | WattsEE | Baseline Description | Nominal Watt | WattsBASE | Incremental Cost | WattsSAVE |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4-Lamp HPT8 w/ High-BF Ballast High-Bay | 128 | 147.2 | 200 Watt Pulse Start Metal-Halide | 200 | 232 | $75 | 84.80 |
| 4-Lamp HPT8 w/ High-BF Ballast High-Bay | 128 | 147.2 | 250 Watt Metal Halide | 250 | 295 | $75 | 147.80 |
| 6-Lamp HPT8 w/ High-BF Ballast High-Bay | 192 | 220.8 | 320 Watt Pulse Start Metal-Halide | 320 | 348.8 | $75 | 128.00 |
| 6-Lamp HPT8 w/ High-BF Ballast High-Bay | 192 | 220.8 | 400 Watt Pulse Start Metal Halide | 400 | 455 | $75 | 234.20 |
| 8-Lamp HPT8 w/ High-BF Ballast High-Bay | 256 | 294.4 | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 320 PSMH | 320 | 476 | $75 | 181.60 |
| 8-Lamp HPT8 w/ High-BF Ballast High-Bay | 256 | 292.4 | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 400 W Metal Halide | 400 | 618 | 75 | 323.60 |
| 1-Lamp HPT8-high performance 32 w lamp | 32 | 24.64 | 1-Lamp Standard F32T8 w/ Elec. Ballast | 32 | 28.16 | $15 | 3.52 |
| 1-Lamp HPT8-high performance 28 w lamp | 28 | 21.56 | 1-Lamp Standard F32T8 w/ Elec. Ballast | 32 | 28.16 | $15 | 6.60 |
| 1-Lamp HPT8-high performance 25 w lamp | 25 | 19.25 | 1-Lamp Standard F32T8 w/ Elec. Ballast | 32 | 28.16 | $15 | 8.91 |
| 2-Lamp HPT8 -high performance 32 w lamp | 64 | 49.28 | 2-Lamp Standard F32T8 w/ Elec. Ballast | 64 | 56.32 | $18 | 7.04 |
| 2-Lamp HPT8-high performance 28 w lamp | 56 | 43.12 | 2-Lamp Standard F32T8 w/ Elec. Ballast | 64 | 56.32 | $18 | 13.20 |
| 2-Lamp HPT8-high performance 25 w lamp | 50 | 38.5 | 2-Lamp Standard F32T8 w/ Elec. Ballast | 64 | 56.32 | $18 | 17.82 |
| 3-Lamp HPT8-high performance 32 w lamp | 96 | 73.92 | 3-Lamp Standard F32T8 w/ Elec. Ballast | 96 | 84.48 | $20 | 10.56 |
| 3-Lamp HPT8-high performance 28 w lamp | 84 | 64.68 | 3-Lamp Standard F32T8 w/ Elec. Ballast | 96 | 84.48 | $20 | 19.80 |
| 3-Lamp HPT8-high performance 25 w lamp | 75 | 57.75 | 3-Lamp Standard F32T8 w/ Elec. Ballast | 96 | 84.48 | $20 | 26.73 |
| 4-Lamp HPT8 -high performance 32 w lamp | 128 | 98.56 | 4-Lamp Standard F32T8 w/ Elec. Ballast | 128 | 112.64 | $23 | 14.08 |
| 4-Lamp HPT8-high performance 28 w lamp | 112 | 86.24 | 4-Lamp Standard F32T8 w/ Elec. Ballast | 128 | 112.64 | $23 | 26.40 |
| 4-Lamp HPT8-high performance 25 w lamp | 100 | 77 | 4-Lamp Standard F32T8 w/ Elec. Ballast | 128 | 112.64 | $23 | 35.64 |
| 2-lamp High-Performance HPT8 Troffer | 64 | 49.28 | 3-Lamp F32T8 w/ Elec. Ballast | 96 | 84.48 | $100 | 35.20 |

Table developed using a constant ballast factor of .77 for troffers/linear HPT8 and 1.15 for HPT8 highbay, 1.0 for all MH/MHPS, and 0.95 for T12 and 0.88 for standard T8.  Input wattages are an average of manufacturer inputs that account for ballast efficacy

A-2:  Early ReplacementHPT8 New and Baseline Assumptions

| EE Measure Description | Nominal Watts | Ballast Factor | WattsEE | Baseline Description | Nominal Watts | WattsBASE | WattsSAVE | Full Measure Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4-Lamp HPT8 w/ High-BF Ballast High-Bay | 128 | 1.15 | 147.2 | 200 Watt Pulse Start Metal-Halide | 200 | 232 | 84.80 | $200 |
| 4-Lamp HPT8 w/ High-BF Ballast High-Bay | 128 | 1.15 | 147.2 | 250 Watt Metal Halide | 250 | 295 | 147.80 | $200 |
| 6-Lamp HPT8 w/ High-BF Ballast High-Bay | 192 | 1.15 | 220.8 | 320 Watt Pulse Start Metal-Halide | 320 | 348.8 | 128.00 | $225 |
| 6-Lamp HPT8 w/ High-BF Ballast High-Bay | 192 | 1.15 | 220.8 | 400 Watt Pulse Start Metal Halide | 400 | 455 | 234.20 | $225 |
| 8-Lamp HPT8 w/ High-BF Ballast High-Bay | 256 | 1.15 | 294.4 | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 320 PSMH | 320 | 476 | 181.60 | $250 |
| 8-Lamp HPT8 w/ High-BF Ballast High-Bay | 256 | 1.15 | 294.4 | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 400 W Metal Halide | 400 | 618 | 323.60 | $250 |
| 1-Lamp Relamp/Reballast T12 to HPT8 | 32 | 0.77 | 24.64 | 1-Lamp F34T12 w/ EEMag Ballast | 34 | 42 | 17.36 | $50 |
| 2-Lamp Relamp/Reballast T12 to HPT8 | 64 | 0.77 | 49.28 | 2-Lamp F34T12 w/ EEMag Ballast | 68 | 67 | 17.72 | $55 |
| 3-Lamp Relamp/Reballast T12 to HPT8 | 96 | 0.77 | 73.92 | 3-Lamp F34T12 w/ EEMag Ballast | 102 | 104 | 30.08 | $60 |
| 4-Lamp Relamp/Reballast T12 to HPT8 | 128 | 0.77 | 98.56 | 4-Lamp F34T12 w/ EEMag Ballast | 136 | 144 | 45.44 | $65 |
| 1-Lamp Relamp/Reballast T12 to HPT8 | 32 | 0.77 | 24.64 | 1-Lamp F40T12 w/ EEMag Ballast | 40 | 41 | 16.36 | $50 |
| 2-Lamp Relamp/Reballast T12 to HPT8 | 64 | 0.77 | 49.28 | 2-Lamp F40T12 w/ EEMag Ballast | 80 | 87 | 37.72 | $55 |
| 3-Lamp Relamp/Reballast T12 to HPT8 | 96 | 0.77 | 73.92 | 3-Lamp F40T12 w/ EEMag Ballast | 120 | 141 | 67.08 | $60 |
| 4-Lamp Relamp/Reballast T12 to HPT8 | 128 | 0.77 | 98.56 | 4-Lamp F40T12 w/ EEMag Ballast | 160 | 172 | 73.44 | $65 |
| 1-Lamp Relamp/Reballast T12 to HPT8 | 32 | 0.77 | 24.64 | 1-Lamp F40T12 w/ Mag Ballast | 40 | 51 | 26.36 | $50 |
| 2-Lamp Relamp/Reballast T12 to HPT8 | 64 | 0.77 | 49.28 | 2-Lamp F40T12 w/ Mag Ballast | 80 | 97 | 47.72 | $55 |
| 3-Lamp Relamp/Reballast T12 to HPT8 | 96 | 0.77 | 73.92 | 3-Lamp F40T12 w/ Mag Ballast | 120 | 135 | 61.08 | $60 |
| 4-Lamp Relamp/Reballast T12 to HPT8 | 128 | 0.77 | 98.56 | 4-Lamp F40T12 w/ Mag Ballast | 160 | 175 | 76.44 | $65 |
| 1-Lamp Relamp/Reballast T8 to HPT8 | 32 | 0.77 | 24.64 | 1-Lamp F32T8 w/ Elec. Ballast | 32 | 28.16 | 3.52 | $50 |
| 2-Lamp Relamp/Reballast T8 to HPT8 | 64 | 0.77 | 49.28 | 2-Lamp F32T8 w/ Elec. Ballast | 64 | 56.32 | 7.04 | $55 |
| 3-Lamp Relamp/Reballast T8 to HPT8 | 96 | 0.77 | 73.92 | 3-Lamp F32T8 w/ Elec. Ballast | 96 | 84.48 | 10.56 | $60 |
| 4-Lamp Relamp/Reballast T8 to HPT8 | 128 | 0.77 | 98.56 | 4-Lamp F32T8 w/ Elec. Ballast | 128 | 112.64 | 14.08 | $65 |
| 2-lamp High-Performance HPT8 Troffer or high efficiency retrofit troffer | 64 | 0.77 | 49.28 | 3-Lamp F32T8 w/ Elec. Ballast | 96 | 84.48 | 35.20 | $100 |

Table developed using a constant ballast factor of 0.77 for troffers/linear HPT8 and 1.15 for HPT8 highbay, 1.0 for all MH/MHPS, and 0.95 for T12 and 0.88 for standard T8.  Input wattages are an average of manufacturer inputs that account for ballast efficacy.

| EE Measure Description | Nominal Watts | WattsEE | EE Lamp Cost | Baseline Description | Base Lamp Cost | Nominal Watts | WattsBASE | WattsSAVE | Measure Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RW T8 - F28T8 Lamp | 28 | 24.64 | $4.50 | F32 T8 Standard Lamp | $2.50 | 32 | 28.16 | 3.52 | $2.00 |
| RWT8 F2T8 Extra Life Lamp | 28 | 24.64 | $4.50 | F32 T8 Standard Lamp | $2.50 | 32 | 28.16 | 3.52 | $2.00 |
| RWT8 - F32/25W T8 Lamp | 25 | 22.00 | $4.50 | F32 T8 Standard Lamp | $2.50 | 32 | 28.16 | 6.16 | $2.00 |
| RWT8 - F32/25W T8 Lamp Extra Life | 25 | 22.00 | $4.50 | F32 T8 Standard Lamp | $2.50 | 32 | 28.16 | 6.16 | $2.00 |
| RWT8 F17T8 Lamp - 2 ft | 16 | 14.08 | $4.80 | F17 T8 Standard Lamp - 2ft | $2.80 | 17 | 14.96 | 0.88 | $2.00 |
| RWT8 F25T8 Lamp - 3 ft | 23 | 20.24 | $5.10 | F25 T8 Standard Lamp - 3ft | $3.10 | 25 | 22.00 | 1.76 | $2.00 |
| RWT8 F30T8 Lamp - 6' Utube | 30 | 26.40 | $11.31 | F32 T8 Standard Utube | $9.31 | 32 | 28.16 | 1.76 | $2.00 |
| RWT8 F29T8 Lamp - Utube | 29 | 25.52 | $11.31 | F32 T8 Standard Utube | $9.31 | 32 | 28.16 | 2.64 | $2.00 |
| RWT8 F96T8 Lamp - 8 ft | 65 | 57.20 | $9.00 | F96 T8 Standard Lamp - 8 ft | $7.00 | 70 | 61.60 | 4.40 | $2.00 |

A– 3:  RWT8 New and Baseline Assumptions

Table developed using a constant ballast factor of 0.88 for RWT8 and Standard T8.

B-1:  Time of Sale T8 Component Costs and Lifetime

| EE Measure Description | EE Lamp Cost | EE Lamp Life (hrs) | EE Lamp Rep. Labor Cost per lamp | EE Ballast Cost | EE Ballast Life (hrs) | EE Ballast Rep. Labor Cost | Baseline Description | Base Lamp Cost | Base Lamp Life (hrs) | Base Lamp Rep. Labor Cost | Base Ballast Cost | Base Ballast Life (hrs) | Base Ballast Rep. Labor Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4-Lamp HPT8 w/ High-BF Ballast High-Bay | $5.00 | 24000 | $6.67 | $32.50 | 70000 | $15.00 | 200 Watt Pulse Start Metal-Halide | $21.00 | 10000 | $6.67 | $87.75 | 40000 | $22.50 |
| 6-Lamp HPT8 w/ High-BF Ballast High-Bay | $5.00 | 24000 | $6.67 | $32.50 | 70000 | $15.00 | 320 Watt Pulse Start Metal-Halide | $21.00 | 20000 | $6.67 | $109.35 | 40000 | $22.50 |
| 8-Lamp HPT8 w/ High-BF Ballast High-Bay | $5.00 | 24000 | $6.67 | $32.50 | 70000 | $15.00 | Lamp HPT8 Equivalent to 320 PSMH | $21.00 | 20000 | $6.67 | $109.35 | 40000 | $22.50 |
| 1-Lamp HPT8 – all qualifying lamps | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 1-Lamp Standard F32T12 w/ Elec Ballast | $2.50 | 20000 | $2.67 | $15.00 | 70000 | $15.00 |
| 2-Lamp HPT8 – all qualifying lamps | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 2-Lamp Standard F32T12 w/ Elec Ballast | $2.50 | 20000 | $2.67 | $15.00 | 70000 | $15.00 |
| 3-Lamp HPT8 – all qualifying lamps | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 3-Lamp Standard F32T8 w/ Elec. Ballast | $2.50 | 20000 | $2.67 | $15.00 | 70000 | $15.00 |
| 4-Lamp HPT8 – all qualifying lamps | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 4-Lamp Standard F32T8 w/ Elec. Ballast | $2.50 | 20000 | $2.67 | $15.00 | 70000 | $15.00 |
|  |  |  |  | $32.50 |  |  |  |  |  |  |  |  |  |
| 2-lamp High-Performance HPT8 Troffer | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 3-Lamp F32T8 w/ Elec. Ballast | $2.50 | 20000 | $2.67 | $15.00 | 70000 | $15.00 |

B-2:  T8 Early Replacement Component Costs and Lifetime

| EE Measure Description | EE Lamp Cost | EE Lamp Life (hrs) | EE Lamp Rep. Labor Cost per lamp | EE Ballast Cost | EE Ballast Life (hrs) | EE Ballast Rep. Labor Cost | Baseline Description | Base Lamp Cost | Base Lamp Life (hrs) | Base Lamp Rep. Labor Cost | Base Ballast Cost | Base Ballast Life (hrs) | Base Ballast Rep. Labor Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4-Lamp HPT8 w/ High-BF Ballast High-Bay | $5.00 | 24000 | $6.67 | $32.50 | 70000 | $15.00 | 200 Watt Pulse Start Metal-Halide | $29.00 | 12000 | $6.67 | $87.75 | 40000 | $22.50 |
| 6-Lamp HPT8 w/ High-BF Ballast High-Bay | $5.00 | 24000 | $6.67 | $32.50 | 70000 | $15.00 | 320 Watt Pulse Start Metal-Halide | $72.00 | 20000 | $6.67 | $109.35 | 40000 | $22.50 |
| 8-Lamp HPT8 w/ High-BF Ballast High-Bay | $5.00 | 24000 | $6.67 | $32.50 | 70000 | $15.00 | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 320 PSMH | $17.00 | 20000 | $6.67 | $109.35 | 40000 | $22.50 |
| 1-Lamp Relamp/Reballast T12 to HPT8 | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 1-Lamp F34T12 w/ EEMag Ballast | $2.70 | 20000 | $2.67 | $20.00 | 40000 | $15.00 |
| 2-Lamp Relamp/Reballast T12 to HPT8 | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 2-Lamp F34T12 w/ EEMag Ballast | $2.70 | 20000 | $2.67 | $20.00 | 40000 | $15.00 |
| 3-Lamp Relamp/Reballast T12 to HPT8 | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 3-Lamp F34T12 w/ EEMag Ballast | $2.70 | 20000 | $2.67 | $20.00 | 40000 | $15.00 |
| 4-Lamp Relamp/Reballast T12 to HPT8 | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 4-Lamp F34T12 w/ EEMag Ballast | $2.70 | 20000 | $2.67 | $20.00 | 40000 | $15.00 |
| 1-Lamp Relamp/Reballast T8 to HPT8 | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 1-Lamp F32T8 w/ Elec. Ballast | $2.70 | 20000 | $2.67 | $20.00 | 70000 | $15.00 |
| 2-Lamp Relamp/Reballast T8 to HPT8 | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 2-Lamp F32T8 w/ Elec. Ballast | $2.70 | 20000 | $2.67 | $20.00 | 70000 | $15.00 |
| 3-Lamp Relamp/Reballast T8 to HPT8 | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 3-Lamp F32T8 w/ Elec. Ballast | $2.70 | 20000 | $2.67 | $20.00 | 70000 | $15.00 |
| 4-Lamp Relamp/Reballast T8 to HPT8 | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 4-Lamp F32T8 w/ Elec. Ballast | $2.70 | 20000 | $2.67 | $20.00 | 70000 | $15.00 |
| 2-lamp High-Performance HPT8 Troffer | $5.00 | 24000 | $2.67 | $32.50 | 70000 | $15.00 | 3-Lamp F32T8 w/ Elec. Ballast | $2.50 | 20000 | $2.67 | $15.00 | 70000 | $15.00 |

B-3:  Reduced Wattage T8 Component Costs and Lifetime

| EE measure description | EE Lamp Cost | EE Lamp Life (hrs) | Baseline Description | Base Lamp Cost | Base Lamp Life (hrs) | Base Lamp Rep. Labor Cost |
| --- | --- | --- | --- | --- | --- | --- |
| RW T8 - F28T8 Lamp | $4.50 | 30000 | F32 T8 Standard Lamp | $2.50 | 15000 | $2.67 |
| RWT8 F2T8 Extra Life Lamp | $4.50 | 36000 | F32 T8 Standard Lamp | $2.50 | 15000 | $2.67 |
| RWT8 - F32/25W T8 Lamp | $4.50 | 30000 | F32 T8 Standard Lamp | $2.50 | 15000 | $2.67 |
| RWT8 - F32/25W T8 Lamp Extra Life | $4.50 | 36000 | F32 T8 Standard Lamp | $2.50 | 15000 | $2.67 |
| RWT8 F17T8 Lamp - 2 ft | $4.80 | 18000 | F17 T8 Standard Lamp - 2ft | $2.80 | 15000 | $2.67 |
| RWT8 F25T8 Lamp - 3 ft | $5.10 | 18000 | F25 T8 Standard Lamp - 3ft | $3.10 | 15000 | $2.67 |
| RWT8 F30T8 Lamp - 6' Utube | $11.31 | 24000 | F32 T8 Standard Utube | $9.31 | 15000 | $2.67 |
| RWT8 F29T8 Lamp - Utube | $11.31 | 24000 | F32 T8 Standard Utube | $9.31 | 15000 | $2.67 |
| RWT8 F96T8 Lamp - 8 ft | $9.00 | 24000 | F96 T8 Standard Lamp - 8 ft | $7.00 | 15000 | $2.67 |

C-1:  T12 Baseline Adjustment:

For early replacement measures replacing existing T12 fixtures the full savings (as calculated above in the Algorithm section) will be claimed for the remaining useful life of the T12 fixture. This should be calculated as follows:

RUL of existing T12 fixture = (1/3 * 40,000)/Hours

A savings adjustment should then be applied to the annual savings for the remainder of the measure life. The adjustment to be applied for each measure should be calculated as:

% Adjustment = (TOS Base Watts – Efficient Watts)/(Existing T12 Watts – Efficient Watts)

For example, an existing 2 lamp T12 fixture (87W) in a college is replaced by a 2 lamp HPT8 (49.3W).

Mid life adjustment of (56.4 – 49.3)/(87 – 49.3) = 19%

Applied after (1/3 * 40000)/3395 = 3.9 years

The adjustment to be applied for each default measure described above is listed in the reference table below:

| Savings Adjustment Factors |  |  |  |
| --- | --- | --- | --- |
| EE Measure Description | Savings Adjustment T12 EEmag ballast and 34 w lamps to HPT8 | Savings Adjustment T12 EEmag ballast and 40 w lamps to HPT8 | Savings Adjustment T12 mag ballast and 40 w lamps to HPT8 |
| 1-Lamp Relamp/Reballast T12 to HPT8 | 20% | 22% | 13% |
| 2-Lamp Relamp/Reballast T12 to HPT8 | 40% | 19% | 15% |
| 3-Lamp Relamp/Reballast T12 to HPT8 | 35% | 16% | 17% |
| 4-Lamp Relamp/Reballast T12 to HPT8 | 31% | 19% | 18% |

###### Measure Code: CI-LTG-T8FX-V09-200101

###### Review Deadline: 1/1/2025

### LED Bulbs and Fixtures

###### Description

This characterization provides savings assumptions for a variety of LED lamps including Omnidirectional (e.g., A-Type lamps), Decorative (e.g., Globes and Torpedoes) and Directional (PAR Lamps, Reflectors, MR16), TLEDs and fixtures including refrigerated case, recessed and outdoor/garage fixtures.

If the implementation strategy does not allow for the installation location to be known, for Residential targeted programs (e.g., an upstream retail program), a deemed split of 97% Residential and 3% Commercial assumptions should be used, and for Commercial targeted programs a deemed split of 97% Commercial and 3% Residential for non-linear LED Bulbs and 100% Commercial and 0% Residential for LED Fixtures and TLEDs should be used.

This measure was developed to be applicable to the following program types:  TOS, NC, EREP, DI, KITS.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, new lamps must be ENERGY STAR in accordance with  ENERGY STAR specification v2.1 (effective 1/2/2017) or be listed on the Design Lights Consortium Qualifying Product List.

###### Definition of Baseline Equipment

The Standard Rx Program will assume a Time of Sale baseline for all one to one replacements, and early replacement for lighting redesign and early retirement for delamping.

For early replacement, the baseline is the existing fixture being replaced.

If the existing fixture is a T12: In July 14, 2012, Federal Standards were enacted that were expected to eliminate T-12s as an option for linear fluorescent fixtures. Through v3.0 of the TRM, it was assumed that the T-12 would no longer be baseline for retrofits from 1/1/2016. However, due to significant loopholes in the legislation, T-12 compliant product is still freely available and in Illinois T-12s continue to hold a significant share of the existing and replacement lamp market. From v8.0 on, a midlife adjustment is applied after the remaining useful life of the T12 fixture (calculated as 1/3 of the 40,000 hour ballast life/ hours). This assumes that T12 replacement lamps will continue to be available until then. See ‘Early Replacement Measures with T12 baseline’ section.

For Time of Sale, refer to the baseline tables at the end of this measure.

In 2012, Federal legislation stemming from the Energy Independence and Security Act of 2007 (EIAS) required all general-purpose light bulbs (defined as omni-directional or standard A-lamps) between 40 watts and 100 watts to have ~30% increased efficiency, essentially phasing out standard incandescent technology.  In 2012, the 100 w lamp standards went in to effect followed by the 75 w lamp standards in 2013 and 60 w and 40 w lamps in 2014.

Additionally, an EISA backstop provision was included that would require replacement baseline lamps to meet an efficacy requirement of 45 lumens/watt or higher beginning on 1/1/2020.

However, in December 2019, DOE issued a final determination for General Service Incandescent Lamps (GSILs), finding that this more stringent standard was not economically justified.

The natural growth of LED market share however, has and will continue to grow over the lifetime of the LED measures installed. The TAC convened a Lamp Forecast Working Group to develop a forecast of the baseline growth of LED, based upon historical growth rates provided via CREED LightTracker data, comparisons with no-program states and review of projections provided by the Department of Energy. The TAC determined that using the Residential-derived forecast is appropriate for the small commercial participants likely to be purchasing lamps through the efficiency programs.

This baseline forecast was then used to estimate how replacement lamps would change over the lifetime of an LED. A single mid-life adjustment is calculated that results in an equivalent net present value of lifetime savings as the forecast decline in annual savings.

Specialty and Directional lamps were not included in the original definition of General Service Lamps in the Energy Independence and Security Act of 2007 (EISA). Therefore, the initial baseline is an incandescent / halogen lamp described in the tables below.

A DOE Final Rule released on 1/19/2017 updated the EISA regulations to remove the exemption for these lamp types such that they become subject to the backstop provision defined within the original legislation.  However, in September 2019 this decision was revoked in a new DOE Final Rule. The natural growth of LED market share of specialty and directional lamps was also estimated by the Working Group and applied to those lamp types.

###### Deemed Lifetime of Efficient Equipment

For fixtures, the lifetime is the life of the product, at the reported operating hours (lamp life in hours divided by operating hours per year – see reference table "LED component Costs and Lifetime."  The analysis period is the same as the lifetime, capped at 15 years.  (15 years from GDS Measure Life Report, June 2007).

For lamps lifetime is calculated as the rated lifetime of the product (actual if available, otherwise assume 20,000 hours for Omnidirectional, 17,000 hours for decorative and 25,000 for directional lamps based on average rated life of lamps on the ENERGY STAR Qualified Products list (accessed 6/16/2020)) divided by the reported operating hours, capped at 10 years.

###### Deemed Measure Cost

Wherever possible, actual incremental costs should be used. Refer to reference table “LED component Cost & Lifetime” for defaults.

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting Loadshape C60 – Non-Residential Agriculture Lighting – 6 Hours Loadshape C61 – Non-Residential Agriculture Lighting – 8 Hours Loadshape C62 – Non-Residential Agriculture Lighting – 12 Hours Loadshape C63 – Non-Residential Dairy Long Day Lighting – 17 Hours Loadshape C64 – Non-Residential Agriculture Lighting – 24 Hours

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the location type. Values are provided for each building type in the reference section below.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh  = ((Wattsbase-WattsEE)/1000)  * Hours *WHFe*ISR

Where:

Wattsbase 	= Input wattage of the existing (for early replacement) or baseline system. Reference  the “LED New and Baseline Assumptions” table for default values.

WattsEE	= Actual wattage of LED purchased / installed. If unknown, use default provided below:

For ENERGY STAR rated lamps the following lumen equivalence tables should be used:

Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps.

| Minimum Lumens | Maximum Lumens | LED Wattage (WattsEE) | Baseline (WattsBase) | Delta Watts (WattsEE) |
| --- | --- | --- | --- | --- |
| 120 |  | 399 |  | 4.0 |  | 25 |  | 21.0 |  |
| 400 |  | 749 |  | 6.6 |  | 29 |  | 22.4 |  |
| 750 |  | 899 |  | 9.6 |  | 43 |  | 33.4 |  |
| 900 |  | 1,399 |  | 13.1 |  | 53 |  | 39.9 |  |
| 1,400 |  | 1,999 |  | 16.0 |  | 72 |  | 56.0 |  |
| 2,000 |  | 2,999 |  | 21.8 |  | 150 |  | 128.2 |  |
| 3,000 |  | 3,999 |  | 28.9 |  | 200 |  | 171.1 |  |
| 4,000 |  | 5,000 |  | 35.7 |  | 300 |  | 264.3 |  |

Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps

| Bulb Type |  | Minimum Lumens |  | Maximum Lumens |  | LED Wattage (WattsEE) | Baseline (WattsBase) |  | Delta Watts (WattsEE) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Omni-Directional 3-Way |  | 1,100 |  | 1,999 |  | 14.7 | 100 |  | 85.3 |
|  |  | 2,000 |  | 2,700 |  | 22.6 | 150 |  | 127.4 |
| Globe (medium and intermediate bases less than 750 lumens) |  | 150 |  | 349 |  | 3.0 | 25 |  | 22 |
|  |  | 350 |  | 499 |  | 4.7 | 40 |  | 35.3 |
|  |  | 500 |  | 574 |  | 5.7 | 60 |  | 54.3 |
|  |  | 575 |  | 649 |  | 6.5 | 75 |  | 68.5 |
|  |  | 650 |  | 1,000 |  | 8.2 | 100 |  | 91.8 |
| Globe (candelabra bases less than 1050 lumens) |  | 150 |  | 349 |  | 3.5 | 25 |  | 21.5 |
|  |  | 350 |  | 499 |  | 4.4 | 40 |  | 35.6 |
|  |  | 500 |  | 574 |  | 5.5 | 60 |  | 54.5 |
| Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) |  | 160 |  | 299 |  | 2.6 | 25 |  | 22.4 |
|  |  | 300 |  | 499 |  | 4.3 | 40 |  | 35.7 |
|  |  | 500 |  | 800 |  | 5.8 | 60 |  | 54.2 |
| Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra bases less than 1050 lumens) |  | 120 |  | 159 |  | 1.5 | 15 |  | 13.5 |
|  |  | 160 |  | 299 |  | 2.7 | 25 |  | 22.3 |
|  |  | 300 |  | 499 |  | 4.2 | 40 |  | 35.8 |
|  |  | 500 |  | 650 |  | 5.5 | 60 |  | 54.5 |

Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps.

For Directional R, BR, and ER lamp types:

| Bulb Type | Minimum Lumens | Maximum Lumens | LED Wattage (WattsEE) | Baseline (WattsBase) | Delta Watts (WattsEE) |
| --- | --- | --- | --- | --- | --- |
| Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 400 | 649 | 7.0 | 50 | 43 |
|  | 650 | 899 | 10.7 | 75 | 64.3 |
|  | 900 | 1,049 | 13.9 | 90 | 76.1 |
|  | 1,050 | 1,199 | 13.8 | 100 | 86.2 |
|  | 1,200 | 1,499 | 15.9 | 120 | 104.1 |
|  | 1,500 | 1,999 | 18.9 | 150 | 131.1 |
|  | 2,000 | 4,200 | 27.3 | 250 | 222.7 |
| Reflector lamp types with medium screw bases (PAR16, R14, R16, etc.) w/ diameter <2.25" (*see exceptions below) | 280 | 374 | 4.6 | 35 | 30.4 |
|  | 375 | 600 | 6.4 | 50 | 43.6 |
| *BR30, BR40, or ER40 | 650 | 949 | 9.3 | 65 | 55.7 |
|  | 950 | 1,099 | 12.7 | 75 | 62.3 |
|  | 1,100 | 1,399 | 14.4 | 85 | 70.6 |
|  | 1,400 | 1,600 | 16.6 | 100 | 83.4 |
|  | 1,601 | 1,800 | 22.2 | 120 | 97.8 |
| *R20 | 450 | 524 | 6.0 | 40 | 34.0 |
|  | 525 | 750 | 7.1 | 45 | 37.9 |
| *MR16 | 250 | 324 | 3.8 | 20.0 | 16.2 |
|  | 325 | 369 | 4.8 | 25.0 | 20.2 |
|  | 370 | 400 | 4.9 | 25.0 | 20.1 |

For PAR, MR, and MRX Lamps Types:

For these highly focused directional lamp types, it is necessary to have Center Beam Candle Power (CBCP) and beam angle measurements to accurately estimate the equivalent baseline wattage.  The formula below is based on the Energy Star Center Beam Candle Power tool. If CBCP and beam angle information are not available or if the equation below returns a negative value (or undefined), use the manufacturer’s recommended baseline wattage equivalent.

Wattsbase=

375.1-4.355D- 227,800-937.9D-0.9903D2-1479BA-12.02D*BA+14.69BA2-16,720*ln⁡(CBCP)

Where:

D 		= Bulb diameter (e.g.  for PAR20 D = 20)

BA		= Beam angle

CBCP		= Center beam candle power

The result of the equation above should be rounded DOWN to the nearest wattage established by Energy Star:

| Diameter | Permitted Wattages |
| --- | --- |
| 16 | 20, 35, 40, 45, 50, 60, 75 |
| 20 | 50 |
| 30S | 40, 45, 50, 60, 75 |
| 30L | 50, 75 |
| 38 | 40, 45, 50, 55, 60, 65, 75, 85, 90, 100, 120, 150, 250 |

Additional EISA non-exempt bulb types:

| Bulb Type | Minimum Lumens | Maximum Lumens | LED Wattage (WattsEE) | Baseline (WattsBase) | Delta Watts (WattsEE) |
| --- | --- | --- | --- | --- | --- |
| Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | 120 | 399 | 4.0 | 25 | 21.0 |
|  | 400 | 749 | 6.6 | 29 | 22.4 |
|  | 750 | 899 | 9.6 | 43 | 33.4 |
|  | 900 | 1,399 | 13.1 | 53 | 39.9 |
|  | 1,400 | 1,999 | 16.0 | 72 | 56.0 |

Hours	= Average hours of use per year are provided in the Reference Table in Section 4.5 for each building type.  If unknown, use the Miscellaneous value.

WHFe	= Waste heat factor for energy to account for cooling energy savings from efficient lighting are provided below for each building type in the Referecne Table in Section 4.5.  If unknown, use the Miscellaneous value.

ISR		= In Service Rate -the percentage of units rebated that actually get installed.

=100% if application form completed with sign off that equipment is not placed into storage. If sign off form not completed, assume the following 3 year ISR assumptions, if program survey  data is not available:

| Type | Weighted Average 1st year In Service Rate (ISR) | 2nd year Installations | 3rd year Installations | Final Lifetime In Service Rate |
| --- | --- | --- | --- | --- |
| LED Bulbs | 82.5% | 8.4% | 7.1% | 98.0% |
| LED Fixtures (Energy Star Fixtures) | 92.9% | 2.8% | 2.3% | 98.0% |
| TLEDs | 83.1% | 8.1% | 6.8% | 98.0% |
| Efficiency Kits | 70.9% | 11.9% | 10.2% | 93.0% |

Mid Life Baseline Adjustment

Omnidirectional, Decorative and Directional Lamps

During the lifetime of an LED, the baseline incandescent/halogen bulb would need to be replaced multiple times. Natural growth of LED market share has, and will continue to grow over the lifetime of the measure, and so a single mid-life adjustment is calculated that results in an equivalent net present value of lifetime savings as the forecast decline in annual savings.   See ‘Lamp Forecast Workbook_2021.xls’ for details.

The calculated mid-life adjustments for 2021 are provided below for each population:

| Lamp Type | Year from which adjustment is applied | Adjustment Factor applied to Annual kWh Savings |
| --- | --- | --- |
| Omnidirectional | 2026 | 34% |
| Decorative | 2026 | 70% |
| Directional | 2026 | 61% |

For example, a 1000 lumen omnidirectional lamp installed in a high school in 2021.

ΔkWh (2021 – 2024) 	= ((53-11.4)/1000) * 2327 * 1.15 * 1

= 111.3 kWh

ΔkWh (2025 on)		= 111.3 * 0.34

= 37.8k kWh

Early Replacement Measures with T12 Baseline

For early replacement measures replacing existing T12 fixtures the full savings (as calculated above in the Algorithm section) will be claimed for the remaining useful life of the T12 fixture. This should be calculated as follows:

RUL of existing T12 fixture = (1/3 * 40,000)/Hours

A savings adjustment should then be applied to the annual savings for the remainder of the measure life.  The adjustment factor to be applied for each T12 installation is 57%.

For example, for an existing 68W T12 fixture in a college is replaced by a 3000 lumen LED 2x2 Recessed Light Fixture (25.4W), a mid life adjustment of 57% should be applied after (1/3 * 40000)/3395 = 3.9 years.

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = (((WattsBase-WattsEE)/1000) * ISR * Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

For example, a 9W LED omnidirectional lamp, 450 lumens, is installed in a heat pump heated office in 2014 and sign off form provided:

ΔkWhheatpenalty	= ((29-6.7)/1000)*1.0*3088* -0.151

= - 10.4 kWh

###### Deferred Installs

As presented above, if a sign off form is not completed the characterization assumes that a percentage of bulbs purchased are not installed until Year 2 and Year 3 (see ISR assumption above). The Illinois Technical Advisory Committee has determined the following methodology for calculating the savings of these future installs.

Year 1 (Purchase Year) installs:	Characterized using assumptions provided above or evaluated assumptions if available.

Year 2 and 3 installs: 	Characterized using delta watts assumption and hours of use from the Install Year, i.e., the actual deemed (or evaluated if available) assumptions active in Year 2 and 3 should be applied.

The NTG factor for the Purchase Year should be applied.

###### Summer Coincident Peak Demand Savings

ΔkW  = ((Wattsbase-WattsEE)/1000) * ISR * WHFd * CF

Where:

WHFd	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is provided in Referecne Table in Section 4.5.  If unknown, use the Miscellaneous value.

CF 	= Summer Peak Coincidence Factor for measure is provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

For example, a 9W LED omnidirectional lamp, 450 lumens, is installed in an office in 2014 and sign off form provided:

ΔkW  	= ((29-6.7)/1000)* 1.0*1.3*0.66

= 0.019 kW

###### Natural Gas Energy Savings

Heating Penalty if fossil fuel heated building (or if heating fuel is unknown):

ΔTherms = ((WattsBase-WattsEE)/1000) * ISR * Hours * - IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting.  Values are provided in the Referecne Table in Section 4.5.  If unknown, use the Miscellaneous value.

For example, a 9W LED omnidirectional lamp, 450 lumens, is installed in an office in 2014 and sign off form provided:

ΔTherms  	= ((29-6.7)/1000)*1.0*3088* -0.016

= - 1.10 therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

For fixture measures, the individual component lifetimes and costs are provided in the reference table section below.

For lamps in order to account for the natural growth of LED over the lifetime of the measure, an equivalent annual levelized baseline replacement cost is calculated and applied over the life of the measure as described above.

The NPV for replacement lamps and annual levelized replacement costs using the societal real discount rate of 0.42% are presented below. It is important to note that for cost-effectiveness screening purposes, the O&M cost adjustments should only be applied in cases where the light bulbs area actually in service and so should be multiplied by the appropriate ISR:

| Lamp Type | Location | NPV of replacement costs for period | Levelized annual replacement cost savings |  |
| --- | --- | --- | --- | --- |
|  |  | 2021 | 2021 |
| Omnidirectional | Commercial | $11.88 | $2.18 |
|  | Multifamily common areas | $19.57 | $5.88 |
| Decorative | Commercial | $15.91 | $3.43 |
|  | Multifamily common areas | $22.77 | $8.04 |
| Directional | Commercial | $41.54 | $6.11 |
|  | Multifamily common areas | $73.43 | $17.69 |

For halogen bulbs, we assume the same replacement cycle as incandescent bulbs. The replacement cycle is based on the miscellaneous hours of use. Both incandescent and halogen lamps are assumed to last for 1,000 hours before needing replacement and CFLs after 10,000 hours.

###### Reference Tables

LED Bulb Assumptions

Wherever possible, actual incremental costs should be used. If unavailable assume the following incremental costs:

| Bulb Type | Year | LED | Incandescent | Incremental Cost |
| --- | --- | --- | --- | --- |
| Omnidirectional | 2017 | $3.21 | $1.25 | $1.96 |
|  | 2018 | $3.21 |  | $1.96 |
|  | 2019 | $3.11 |  | $1.86 |
|  | 2020 | $2.70 |  | $1.45 |
| Directional | 2017 | $6.24 | $3.53 | $2.71 |
|  | 2018+ | $5.18 |  | $1.65 |
| Decorative and Globe | 2017 | $3.50 | $1.60 | $1.90 |
|  | 2018+ | $3.40 | $1.74 | $1.66 |

LED Fixture Wattage, TOS Baseline and Incremental Cost Assumptions

| LED Category | EE Measure Description | WattsEE | Baseline Description | WattsBASE | Incremental Cost |
| --- | --- | --- | --- | --- | --- |
| LED Downlight Fixtures | LED Recessed, Surface, Pendant Downlights | 17.6 | Baseline Recessed, Surface, Pendant Downlights | 54.3 | $27 |
| LED Interior Directional | LED Track Lighting | 12.2 | Baseline Track Lighting | 60.4 | $59 |
|  | LED Wall-Wash Fixtures | 8.3 | Baseline Wall-Wash Fixtures | 17.7 | $59 |
| LED Display Case | LED Display Case Light Fixture | 4 per ft | Baseline Display Case Light Fixture | 36.2 per ft | $11/ft |
|  | LED Undercabinet Shelf-Mounted Task Light Fixtures | 4 per ft | Baseline Undercabinet Shelf-Mounted Task Light Fixtures | 36.2 per ft | $11/ft |
|  | LED Refrigerated Case Light, Horizontal or Vertical | 4 per ft | Baseline Refrigerated Case Light, Horizontal or Vertical (per foot) | 15.2 per ft | $11/ft |
|  | LED Freezer Case Light, Horizontal or Vertical | 4 per ft | Baseline Freezer Case Light, Horizontal or Vertical (per foot) | 18.7 per ft | $11/ft |
| LED Linear Replacement Lamps | T8 LED Replacement Lamp (TLED), < 1200 lumens | 8.9 | F17T8 Standard Lamp - 2 foot | 15.0 | $13 |
|  | T8 LED Replacement Lamp (TLED), 1200-2400 lumens | 15.8 | F32T8 Standard Lamp - 4 foot | 28.2 | $15 |
|  | T8 LED Replacement Lamp (TLED), > 2400 lumens | 22.9 | F32T8/HO Standard Lamp - 4 foot | 41.8 | $13 |
| LED Troffers | LED 2x2 Recessed Light Fixture, 2000-3500 lumens | 25.4 | 2-Lamp 32w T8 (BF < 0.89) | 57.0 | $53 |
|  | LED 2x2 Recessed Light Fixture, 3501-5000 lumens | 36.7 | 3-Lamp 32w T8 (BF < 0.88) | 84.5 | $69 |
|  | LED 2x4 Recessed Light Fixture, 3000-4500 lumens | 33.3 | 2-Lamp 32w T8 (BF < 0.89) | 57.0 | $55 |
|  | LED 2x4 Recessed Light Fixture, 4501-6000 lumens | 44.8 | 3-Lamp 32w T8 (BF < 0.88) | 84.5 | $76 |
|  | LED 2x4 Recessed Light Fixture, 6001-7500 lumens | 57.2 | 4-Lamp 32w T8 (BF < 0.88) | 112.6 | $104 |
|  | LED 1x4 Recessed Light Fixture, 1500-3000 lumens | 21.8 | 1-Lamp 32w T8 (BF <0.91) | 29.1 | $22 |
|  | LED 1x4 Recessed Light Fixture, 3001-4500 lumens | 33.7 | 2-Lamp 32w T8 (BF < 0.89) | 57.0 | $75 |
|  | LED 1x4 Recessed Light Fixture, 4501-6000 lumens | 43.3 | 3-Lamp 32w T8 (BF < 0.88) | 84.5 | $83 |
| LED Linear Ambient Fixtures | LED Surface & Suspended Linear Fixture, <= 3000 lumens | 19.5 | 1-Lamp 32w T8 (BF <0.91) | 29.1 | $10 |
|  | LED Surface & Suspended Linear Fixture, 3001-4500 lumens | 32.1 | 2-Lamp 32w T8 (BF < 0.89) | 57.0 | $52 |
|  | LED Surface & Suspended Linear Fixture, 4501-6000 lumens | 43.5 | 3-Lamp 32w T8 (BF < 0.88) | 84.5 | $78 |
|  | LED Surface & Suspended Linear Fixture, 6001-7500 lumens | 56.3 | T5HO 2L-F54T5HO - 4' | 120.0 | $131 |
|  | LED Surface & Suspended Linear Fixture, > 7500 lumens | 82.8 | T5HO 3L-F54T5HO - 4' | 180.0 | $173 |
| LED High & Low Bay Fixtures | LED Low-Bay Fixtures, <= 10,000 lumens | 61.6 | 3-Lamp T8HO Low-Bay | 157.0 | $44 |
|  | LED High-Bay Fixtures, 10,001-15,000 lumens | 99.5 | 4-Lamp T8HO High-Bay | 196.0 | $137 |
|  | LED High-Bay Fixtures, 15,001-20,000 lumens | 140.2 | 6-Lamp T8HO High-Bay | 294.0 | $202 |
|  | LED High-Bay Fixtures, 20,001-30,000 lumens | 193.8 | 8-Lamp T8HO High-Bay | 392.0 | $264 |
|  | LED High-Bay Fixtures, 30,001-40,000 lumens | 250 | 750 Watts Metal Halide | 850 | $400 |
|  | LED High-Bay Fixtures 40,001-50,000 lumens | 295 | 1000 Watts Metal Halide | 1080 | $425 |
|  | LED High-Bay Fixtures >50,000 lumens | 435 | 1500 Watts Metal Halide | 1610 | $550 |
| LED Agricultural Interior Fixtures | LED Ag Interior Fixtures, <= 2,000 lumens | 12.9 | 25% 73 Watt EISA Inc, 75% 1L T8 | 42.0 | $18 |
|  | LED Ag Interior Fixtures, 2,001-4,000 lumens | 29.7 | 25% 146 Watt EISA Inc, 75% 2L T8 | 81.0 | $48 |
|  | LED Ag Interior Fixtures, 4,001-6,000 lumens | 45.1 | 25% 217 Watt EISA Inc, 75% 3L T8 | 121.0 | $57 |
|  | LED Ag Interior Fixtures, 6,001-8,000 lumens | 59.7 | 25% 292 Watt EISA Inc, 75% 4L T8 | 159.0 | $88 |
|  | LED Ag Interior Fixtures, 8,001-12,000 lumens | 84.9 | 200W Pulse Start Metal Halide | 227.3 | $168 |
|  | LED Ag Interior Fixtures, 12,001-16,000 lumens | 113.9 | 320W Pulse Start Metal Halide | 363.6 | $151 |
|  | LED Ag Interior Fixtures, 16,001-20,000 lumens | 143.7 | 350W Pulse Start Metal Halide | 397.7 | $205 |
|  | LED Ag Interior Fixtures, > 20,000 lumens | 193.8 | (2) 320W Pulse Start Metal Halide | 727.3 | $356 |
| LED Exterior Fixtures | LED Exterior Fixtures, <= 5,000 lumens | 34.1 | 100W Metal Halide | 113.6 | $80 |
|  | LED Exterior Fixtures, 5,001-10,000 lumens | 67.2 | 175W Pulse Start Metal Halide | 198.9 | $248 |
|  | LED Exterior Fixtures, 10,001-15,000 lumens | 108.8 | 250W Pulse Start Metal Halide | 284.1 | $566 |
|  | LED Exterior Fixtures, 15,001-30,000 lumens | 183.9 | 400W Pulse Start Metal Halide | 454.5 | $946 |
|  | LED Exterior Fixtures, 30,001-40,000 lumens | 250 | 750 W Metal Halide | 850 | $700 |
|  | LED Exterior Fixtures, 40,001-50,000 lumens | 295 | 1000 W Metal Halide | 1080 | $850 |
|  | LED Exterior Fixtures, > 50,000 lumens | 435 | 1500 W Metal Halide | 1610 | $1100 |

LED Fixture Component Costs & Lifetime

|  |  | EE Measure |  |  |  | Baseline |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LED Category | EE Measure Description | Lamp Life (hrs) | Total Lamp Replacement Cost | LED Driver Life (hrs) | Total LED Driver Replacement Cost | Lamp Life (hrs) | Total Lamp Replacement Cost | Ballast Life (hrs) | Total Ballast Replacement Cost |
| LED Downlight Fixtures | LED Recessed, Surface, Pendant Downlights | 50,000 | $30.75 | 70,000 | $47.50 | 2,500 | $8.86 | 40,000 | $14.40 |
| LED Interior Directional | LED Track Lighting | 50,000 | $39.00 | 70,000 | $47.50 | 2,500 | $12.71 | 40,000 | $11.00 |
|  | LED Wall-Wash Fixtures | 50,000 | $39.00 | 70,000 | $47.50 | 2,500 | $9.17 | 40,000 | $27.00 |
| LED Display Case | LED Display Case Light Fixture | 50,000 | $9.75/ft | 70,000 | $11.88/ft | 2,500 | $6.70 | 40,000 | $5.63 |
|  | LED Undercabinet Shelf-Mounted Task Light Fixtures | 50,000 | $9.75/ft | 70,000 | $11.88/ft | 2,500 | $6.70 | 40,000 | $5.63 |
|  | LED Refrigerated Case Light, Horizontal or Vertical | 50,000 | $8.63/ft | 70,000 | $9.50/ft | 15,000 | $1.13 | 40,000 | $8.00 |
|  | LED Freezer Case Light, Horizontal or Vertical | 50,000 | $7.88/ft | 70,000 | $7.92/ft | 12,000 | $0.94 | 40,000 | $6.67 |
| LED Linear Replacement Lamps | T8 LED Replacement Lamp (TLED), < 1200 lumens | 50,000 | $5.76 | 70,000 | $13.67 | 30,000 | $6.17 | 40,000 | $11.96 |
|  | T8 LED Replacement Lamp (TLED), 1200-2400 lumens | 50,000 | $8.57 | 70,000 | $13.67 | 24,000 | $6.17 | 40,000 | $11.96 |
|  | T8 LED Replacement Lamp (TLED), > 2400 lumens | 50,000 | $8.57 | 70,000 | $13.67 | 18,000 | $6.17 | 40,000 | $11.96 |
| LED Troffers | LED 2x2 Recessed Light Fixture, 2000-3500 lumens | 50,000 | $78.07 | 70,000 | $40.00 | 24,000 | $26.33 | 40,000 | $35.00 |
|  | LED 2x2 Recessed Light Fixture, 3501-5000 lumens | 50,000 | $89.23 | 70,000 | $40.00 | 24,000 | $39.50 | 40,000 | $35.00 |
|  | LED 2x4 Recessed Light Fixture, 3000-4500 lumens | 50,000 | $96.10 | 70,000 | $40.00 | 24,000 | $12.33 | 40,000 | $35.00 |
|  | LED 2x4 Recessed Light Fixture, 4501-6000 lumens | 50,000 | $114.37 | 70,000 | $40.00 | 24,000 | $18.50 | 40,000 | $35.00 |
|  | LED 2x4 Recessed Light Fixture, 6001-7500 lumens | 50,000 | $137.43 | 70,000 | $40.00 | 24,000 | $24.67 | 40,000 | $35.00 |
|  | LED 1x4 Recessed Light Fixture, 1500-3000 lumens | 50,000 | $65.43 | 70,000 | $40.00 | 24,000 | $6.17 | 40,000 | $35.00 |
|  | LED 1x4 Recessed Light Fixture, 3001-4500 lumens | 50,000 | $100.44 | 70,000 | $40.00 | 24,000 | $12.33 | 40,000 | $35.00 |
|  | LED 1x4 Recessed Light Fixture, 4501-6000 lumens | 50,000 | $108.28 | 70,000 | $40.00 | 24,000 | $18.50 | 40,000 | $35.00 |
| LED Linear Ambient Fixtures | LED Surface & Suspended Linear Fixture, <= 3000 lumens | 50,000 | $62.21 | 70,000 | $40.00 | 24,000 | $6.17 | 40,000 | $35.00 |
|  | LED Surface & Suspended Linear Fixture, 3001-4500 lumens | 50,000 | $93.22 | 70,000 | $40.00 | 24,000 | $12.33 | 40,000 | $35.00 |
|  | LED Surface & Suspended Linear Fixture, 4501-6000 lumens | 50,000 | $114.06 | 70,000 | $40.00 | 24,000 | $18.50 | 40,000 | $35.00 |
|  | LED Surface & Suspended Linear Fixture, 6001-7500 lumens | 50,000 | $152.32 | 70,000 | $40.00 | 30,000 | $26.33 | 40,000 | $60.00 |
|  | LED Surface & Suspended Linear Fixture, > 7500 lumens | 50,000 | $183.78 | 70,000 | $40.00 | 30,000 | $39.50 | 40,000 | $60.00 |
| LED High & Low Bay Fixtures | LED Low-Bay Fixtures, <= 10,000 lumens | 50,000 | $90.03 | 70,000 | $62.50 | 18,000 | $64.50 | 40,000 | $92.50 |
|  | LED High-Bay Fixtures, 10,001-15,000 lumens | 50,000 | $122.59 | 70,000 | $62.50 | 18,000 | $86.00 | 40,000 | $92.50 |
|  | LED High-Bay Fixtures, 15,001-20,000 lumens | 50,000 | $157.22 | 70,000 | $62.50 | 18,000 | $129.00 | 40,000 | $117.50 |
|  | LED High-Bay Fixtures, 20,001 – 30,000 lumens | 50,000 | $228.52 | 70,000 | $62.50 | 18,000 | $172.00 | 40,000 | $142.50 |
|  | LED High-Bay Fixtures, 30,001-40,000 lumens | 50,000 | $294.00 | 70,000 | $62.50 | 15,000 | $82.00 | 40,000 | $143.00 |
|  | LED High-Bay Fixtures, 40,001-50,000 lumens | 50,000 | $324.00 | 70,000 | $62.50 | 15,000 | $88.00 | 40,000 | $149.00 |
|  | LED High-Bay Fixtures, > 50,000 lumens | 50,000 | $382.00 | 70,000 | $62.50 | 15,000 | $96.00 | 40,000 | $200.00 |
| LED Agricultural Interior Fixtures | LED Ag Interior Fixtures, <= 2,000 lumens | 50,000 | $41.20 | 70,000 | $40.00 | 1,000 | $1.23 | 40,000 | $26.25 |
|  | LED Ag Interior Fixtures, 2,001-4,000 lumens | 50,000 | $65.97 | 70,000 | $40.00 | 1,000 | $1.43 | 40,000 | $26.25 |
|  | LED Ag Interior Fixtures, 4,001-6,000 lumens | 50,000 | $80.08 | 70,000 | $40.00 | 1,000 | $1.62 | 40,000 | $26.25 |
|  | LED Ag Interior Fixtures, 6,001-8,000 lumens | 50,000 | $105.54 | 70,000 | $40.00 | 1,000 | $1.81 | 40,000 | $26.25 |
|  | LED Ag Interior Fixtures, 8,001-12,000 lumens | 50,000 | $179.81 | 70,000 | $62.50 | 15,000 | $63.00 | 40,000 | $112.50 |
|  | LED Ag Interior Fixtures, 12,001-16,000 lumens | 50,000 | $190.86 | 70,000 | $62.50 | 15,000 | $68.00 | 40,000 | $122.50 |
|  | LED Ag Interior Fixtures, 16,001-20,000 lumens | 50,000 | $237.71 | 70,000 | $62.50 | 15,000 | $73.00 | 40,000 | $132.50 |
|  | LED Ag Interior Fixtures, > 20,000 lumens | 50,000 | $331.73 | 70,000 | $62.50 | 15,000 | $136.00 | 40,000 | $202.50 |
| LED Exterior Fixtures | LED Exterior Fixtures, <= 5,000 lumens | 50,000 | $73.80 | 70,000 | $62.50 | 15,000 | $58.00 | 40,000 | $102.50 |
|  | LED Exterior Fixtures, 5,001-10,000 lumens | 50,000 | $124.89 | 70,000 | $62.50 | 15,000 | $63.00 | 40,000 | $112.50 |
|  | LED Exterior Fixtures, 10,001-15,000 lumens | 50,000 | $214.95 | 70,000 | $62.50 | 15,000 | $68.00 | 40,000 | $122.50 |
|  | LED Exterior Fixtures, 15,000- 30,000 lumens | 50,000 | $321.06 | 70,000 | $62.50 | 15,000 | $73.00 | 40,000 | $132.50 |
|  | LED Exterior Fixtures, 30,001-40,000 lumens | 50,000 | $546.00 | 70,000 | $62.50 | 15,000 | $82.00 | 40,000 | $143.00 |
|  | LED Exterior Fixtures, 40,001-50,000 lumens | 50,000 | $722.00 | 70,000 | $62.50 | 15,000 | $88.00 | 40,000 | $149.00 |
|  | LED Exterior Fixtures, > 50,000 lumens | 50,000 | $870.00 | 70,000 | $62.50 | 15,000 | $96.00 | 40,000 | $200.00 |

###### Measure Code: CI-LTG-LEDB-V13-220101

###### Review Deadline: 1/1/2023

### Commercial LED Exit Signs

###### Description

This measure characterizes the savings associated with installing a Light Emitting Diode (LED) exit sign in place of a fluorescent or incandescent exit sign in a Commercial building. Light Emitting Diode exit signs have a string of very small, typically red or green, glowing LEDs arranged in a circle or oval. The LEDs may also be arranged in a line on the side, top or bottom of the exit sign. LED exit signs provide the best balance of safety, low maintenance, and very low energy usage compared to other exit sign technologies.

This measure was developed to be applicable to the following program types:  RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is assumed to be an exit sign illuminated by LEDs.

###### Definition of Baseline Equipment

The baseline equipment is assumed to be an existing fluorescent or incandescent model.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 5 years.

###### Deemed Measure Cost

The actual material and labor costs should be used if available. If actual costs are unavailable, assume a total installed cost of at $32.50.

###### Loadshape

Loadshape C53 - Flat

###### Coincidence Factor

The summer peak coincidence factor for this measure is assumed to be 100%.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh	= ((WattsBase - WattsEE) / 1000)  * HOURS * WHFe

Where:

WattsBase 	= Actual wattage if known, if unknown assume the following:

| Baseline Type | WattsBase |
| --- | --- |
| Incandescent | 35W |
| CFL (dual sided) | 14W |
| CFL (single sided) | 7W |
| Unknown | 7W |

WattsEE	= Actual wattage if known, if unknown assume 2W for signle sided or unknown type and 4W for dual sided

HOURS		= Annual operating hours

= 8766

WHFe	= Waste heat factor for energy to account for cooling energy savings from efficient lighting are provided for each building type in the Referecne Table in Section 4.5.  If unknown, use the Miscellaneous value.

For example, replacing incandescent fixture in an office:

ΔkWH	= ((35 – 2)/1000) * 8766 * 1.25

= 362 kWh

Replacing single sided fluorescent fixture in a hospital:

ΔkWH	= ((7– 2)/1000) * 8766 * 1.35

= 59.2 kWh

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = (((WattsBase-WattsEE)/1000) * Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

For example, replacing incandescent fixture in a heat pump heated office:

ΔkWhheatpenalty	= ((35 – 2)/1000) * 8766 * -0.151

= -43.7 kWh

Replacing single sided fluorescent fixture in a heat pump heated hospital:

ΔkWhheatpenalty	= ((7 – 2)/1000) * 8766 * -0.104

= -4.6 kWh

###### Summer Coincident Peak Demand Savings

ΔkW 	= ((WattsBase - WattsEE) / 1000) * WHFd * CF

Where:

WHFd	= Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings is provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

CF		= Summer Peak Coincidence Factor for measure

= 1.0

For example, replacing incandescent fixture in an office:

ΔkW	= ((35 – 2)/1000) * 1.3 * 1.0

= 0.043 kW

Replacing single sided fluorescent fixture in a hospital:

ΔkW	= ((7 – 2)/1000) * 1.69 * 1.0

= 0.0085 kW

###### Natural Gas Savings

Heating Penalty if natural gas heated building (or if heating fuel is unknown):

Δtherms = ((WattsBase-WattsEE)/1000) * Hours *- IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting.  Values are provided in the Referecne Table in Section 4.5.  If unknown, use the Miscellaneous value.

For example, replacing incandescent fixture in an office:

ΔTherms	= ((35 – 2)/1000) * 8766 * -0.016

= -4.63 Therms

Replacing single sided fluorescent fixture in a hospital:

ΔTherms	= ((7 – 2)/1000) * 8766 * -0.011

= - 0.48 Therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

The annual O&M Cost Adjustment savings should be calculated using the following component costs and lifetimes.

|  | Baseline Measures |  |
| --- | --- | --- |
| Component | Cost | Life (yrs) |
| Lamp | $12.45 | 1.37 years |

###### Measure Code: CI-LTG-LEDE-V03-190101

###### Review Deadline: 1/1/2024

### LED Traffic and Pedestrian Signals

###### Description

Traffic and pedestrian signals are retrofitted to be illuminated with light emitting diodes (LED) instead of incandescent lamps. Incentive applies for the replacement or retrofit of existing incandescent traffic signals with new LED traffic and pedestrian signal lamps.  Each lamp can have no more than a maximum LED module wattage of 25. Incentives are not available for spare lights. Lights must be hardwired and single lamp replacements are not eligible, with the exception of pedestrian hand signals. Eligible lamps must meet the Energy Star Traffic Signal Specification and the Institute for Transportation Engineers specification for traffic signals.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Refer to the Table titled ‘Traffic Signals Technology Equivalencies’ for efficient technology wattage and savings assumptions.

###### Definition of Baseline Equipment

Refer to the Table titled ‘Traffic Signals Technology Equivalencies’ for baseline efficiencies and savings assumptions.

###### Deemed Lifetime of Efficient Equipment

The assumed lifetime of an LED traffic signal is 10 years. The life in years is calculated by dividing 100,000 hrs (manufacturer’s estimate) by the annual operating hours for the particular signal type and is capped at 10 years..

###### Deemed Measure Cost

The actual measure installation cost should be used (including material and labor).

###### Loadshape

Loadshape C24 - Traffic Signal - Red Balls, always changing or flashing

Loadshape C25 - Traffic Signal - Red Balls, changing day, off night

Loadshape C26 - Traffic Signal - Green Balls, always changing

Loadshape C27 - Traffic Signal - Green Balls, changing day, off night

Loadshape C28 - Traffic Signal - Red Arrows

Loadshape C29 - Traffic Signal - Green Arrows

Loadshape C30 - Traffic Signal - Flashing Yellows

Loadshape C31 - Traffic Signal - “Hand” Don’t Walk Signal

Loadshape C32 - Traffic Signal - “Man” Walk Signal

Loadshape C33 - Traffic Signal - Bi-Modal Walk/Don’t Walk

###### Coincidence Factor

The summer peak coincidence factor (CF) for this measure is dependent on lamp type as below:

| Lamp Type | CF |
| --- | --- |
| Red Round, always changing or flashing | 0.55 |
| Red Arrows | 0.90 |
| Green Arrows | 0.10 |
| Yellow Arrows | 0.03 |
| Green Round, always changing or flashing | 0.43 |
| Flashing Yellow | 0.50 |
| Yellow Round, always changing | 0.02 |
| “Hand” Don’t Walk Signal | 0.75 |
| “Man” Walk Signal | 0.21 |

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh	= (Wbase - Weff) x HOURS / 1000

Where:

Wbase		=The connected load of the baseline equipment

= see Table ‘Traffic Signals Technology Equivalencies’

Weff		=The connected load of the baseline equipment

= see Table ‘Traffic Signals Technology Equivalencies’

HOURS 		= annual operating hours of the lamp

= see Table ‘Traffic Signals Technology Equivalencies’

1000		= conversion factor (W/kW)

For example, an 8 inch red, round signal:

ΔkWh 	= ((69 - 7) x 4818) / 1000

= 299 kWh

###### Summer Coincident Peak Demand Savings

ΔkW 	= (Wbase– Weff) x CF / 1000

Where:

Wbase		=The connected load of the baseline equipment

= see Table ‘Traffic Signals Technology Equivalencies’

Weff		=The connected load of the efficient equipment

= see Table ‘Traffic Signals Technology Equivalencies’

CF 		= Summer Peak Coincidence Factor for measure

For example, an 8 inch red, round signal:

ΔkW 	= ((69 – 7) x 0.55) / 1000

= 0.0341 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Reference Tables

Traffic Signals Technology Equivalencies

| Traffic Fixture Type | Fixture Size and Color | Efficient Lamps | Baseline Lamps | HOURS | Efficient Fixture Wattage | Baseline Fixture Wattage | Energy Savings (in kWh) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Round Signals | 8” Red | LED | Incandescent | 4818 | 7 | 69 | 299 |
| Round Signals | 12” Red | LED | Incandescent | 4818 | 6 | 150 | 694 |
| Flashing Signal | 8” Red | LED | Incandescent | 4380 | 7 | 69 | 272 |
| Flashing Signal | 12” Red | LED | Incandescent | 4380 | 6 | 150 | 631 |
| Flashing Signal | 8” Yellow | LED | Incandescent | 4380 | 10 | 69 | 258 |
| Flashing Signal | 12” Yellow | LED | Incandescent | 4380 | 13 | 150 | 600 |
| Round Signals | 8” Yellow | LED | Incandescent | 175 | 10 | 69 | 10 |
| Round Signals | 12” Yellow | LED | Incandescent | 175 | 13 | 150 | 24 |
| Round Signals | 8” Green | LED | Incandescent | 3767 | 9 | 69 | 226 |
| Round Signals | 12” Green | LED | Incandescent | 3767 | 12 | 150 | 520 |
| Turn Arrows | 8” Yellow | LED | Incandescent | 701 | 7 | 116 | 76 |
| Turn Arrows | 12” Yellow | LED | Incandescent | 701 | 9 | 116 | 75 |
| Turn Arrows | 8” Green | LED | Incandescent | 701 | 7 | 116 | 76 |
| Turn Arrows | 12” Green | LED | Incandescent | 701 | 7 | 116 | 76 |
| Pedestrian Sign | 12” Hand/Man | LED | Incandescent | 8766 | 8 | 116 | 947 |

Reference specifications for above traffic signal wattages are from the following manufacturers:

- 8” Incandescent traffic signal bulb: General Electric Traffic Signal Model 17325-69A21/TS

- 12” Incandescent traffic signal bulb: General Electric Signal Model 35327-150PAR46/TS

- Incandescent Arrows & Hand/Man Pedestrian Signs: General Electric Traffic Signal Model 19010-116A21/TS

- 8” and 12” LED traffic signals: Leotek Models TSL-ES08 and TSL-ES12

- 8” LED Yellow Arrow: General Electric Model DR4-YTA2-01A

- 8” LED Green Arrow: General Electric Model DR4-GCA2-01A

- 12” LED Yellow Arrow: Dialight Model 431-3334-001X

- 12: LED Green Arrow: Dialight Model 432-2324-001X

- LED Hand/Man Pedestrian Sign: Dialight 430-6450-001X

###### Measure Code: CI-LTG-LEDT-V03-220601

###### Review Deadline: 1/1/2024

### Lighting Power Density

###### Description

This measure relates to installation of efficient lighting systems in new construction or substantial renovation of commercial buildings excluding low rise (three stories or less) residential buildings. Substantial renovation is when two or more building systems are renovated, such as shell and heating, heating and lighting, etc. State Energy Code specifies a lighting power density level by building type for both the interior and the exterior. Either the Building Area Method or Space by Space method as defined in 2015 or 2018, depending on the IECC in effect on the date of the building permit (if unknown assume IECC 2018), can be used for calculating the Interior Lighting Power Density. The measure consists of a design that is more efficient (has a lower lighting power density in watts/square foot) than code requires. The IECC applies to both new construction and renovation.

This measure was developed to be applicable to the following program types: NC.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the lighting system must be more efficient than the baseline Energy Code lighting power density in watts/square foot for either the interior space or exterior space.

###### Definition of Baseline Equipment

The baseline is assumed to be a lighting power density that meets the IECC in effect on the date of the building permit (if unknown assume IECC 2018).

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

###### Deemed Calculation for this Measure

Annual kWh Savings

ΔkWh 	= (WSFbase-WSFeffic )/1000* SF* Hours * WHFe

Summer Coincident Peak kW Savings

ΔkW 	= (WSFbase-WSFeffic )/1000* SF* CF * WHFd

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years.

###### Deemed Measure Cost

The actual incremental cost over a baseline system will be collected from the customer if possible or developed on a fixture by fixture basis.

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the building type.

Algorithm

###### Calculation of Savings

###### Energy Savings

ΔkWh = (WSFbase-WSFeffic )/1000* SF* Hours * WHFe

Where:

WSFbase 		= Baseline lighting watts per square foot or linear foot as determined by building or space type.   Whole building analysis values are presented in the Reference Tables below.

WSFeffic		= The actual installed lighting watts per square foot or linear foot.

SF 		= Provided by customer based on square footage of the building area applicable to the lighting design for new building.

Hours 		= Annual site-specific hours of operation of the lighting equipment collected from the customer. If not available, use building area type as provided in the Reference Table in Section 4.5, Fixture annual operating hours.

WHFe 		= Waste Heat Factor for Energy to account for cooling savings from efficient lighting is as provided in the Reference Table in Section 4.5 by buidling type.  If building is not cooled WHFe is 1.

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = (WSFbase-WSFeffic )/1000* SF* Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

###### Summer Coincident Peak Demand Savings

ΔkW = (WSFbase-WSFeffic )/1000* SF* CF * WHFd

Where:

WHFd		= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is as provided in the Reference Table in Section 4.5 by buidling type. If building is not cooled WHFd is 1.

CF  		= Summer Peak Coincidence Factor for measure is as provided in the Reference Table in Section 4.5 by buidling type. If the building type is unknown, use the Miscellaneous value of 0.66.

Other factors as defined above

###### Natural Gas Energy Savings

ΔTherms = (WSFbase-WSFeffic )/1000* SF* Hours * - IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting.  This value is provided in the Reference Table in Section 4.5 by buidling type.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Reference Tables

Lighting Power Density Values from 2015 and 2018 for Interior Commercial New Construction and Substantial Renovation Building Area Method:

| Building Area Type | IECC 2015 Lighting Power Density (w/ft2) | IECC 2018 Lighting Power Density (w/ft2) |
| --- | --- | --- |
| Automotive Facility | 0.80 | 0.71 |
| Convention Center | 1.01 | 0.76 |
| Court House | 1.01 | 0.9 |
| Dining: Bar Lounge/Leisure | 1.01 | 0.9 |
| Dining: Cafeteria/Fast Food | 0.9 | 0.79 |
| Dining: Family | 0.95 | 0.78 |
| Dormitory | 0.57 | 0.61 |
| Exercise Center | 0.84 | 0.65 |
| Fire station | 0.67 | 0.53 |
| Gymnasium | 0.94 | 0.68 |
| Healthcare – clinic | 0.90 | 0.82 |
| Hospital | 1.05 | 1.05 |
| Hotel | 0.87 | 0.75 |
| Library | 1.19 | 0.78 |
| Manufacturing Facility | 1.17 | 0.90 |
| Motel | 0.87 | 0.75 |
| Motion Picture Theater | 0.76 | 0.83 |
| Multifamily | 0.51 | 0.68 |
| Museum | 1.02 | 1.06 |
| Office | 0.82 | 0.79 |
| Parking Garage | 0.21 | 0.15 |
| Penitentiary | 0.81 | 0.75 |
| Performing Arts Theater | 1.39 | 1.18 |
| Police Station | 0.87 | 0.80 |
| Post Office | 0.87 | 0.67 |
| Religious Building | 1.0 | 0.94 |
| Retail | 1.26 | 1.06 |
| School/University | 0.87 | 0.81 |
| Sports Arena | 0.91 | 0.87 |
| Town Hall | 0.89 | 0.80 |
| Transportation | 0.70 | 0.61 |
| Warehouse | 0.66 | 0.48 |
| Workshop | 1.19 | 0.90 |

Lighting Power Density Values from IECC 2018 for Interior Commercial New Construction and Substantial Renovation Building Area Method:

Lighting Power Density Values from IECC 2015 for Interior Commercial New Construction and Substantial Renovation Space by Space Method:

Lighting Power Density Values from IECC 2018 for Interior Commercial New Construction and Substantial Renovation Space by Space Method:

The exterior lighting design will be based on the building location and the applicable “Lighting Zone” as defined in

IECC 2015 Table C405.5.2(1) which follows. This table is identical to IECC 2018 Table C405.4.2(1).

The lighting power density savings will be based on reductions below the allowable design levels as specified in IECC 2015 Table C405.5.2(2) or 2018 Table C405.2.2(2).

Allowable Design Levels from IECC 2015

Allowable Design Levels from IECC 2018

Table C405.2.2(2)

Lighting Power Allowances for Building Exteriors

###### Measure Code: CI-LTG-LPDE-V07-220101

###### Review Deadline: 1/1/2024

### Miscellaneous Commercial/Industrial Lighting

###### Description

This measure is designed to calculate savings from energy efficient lighting upgrades that are not captured in other measures within the TRM. If a lighting project fits the measure description in other lighting measures, then those criteria, definitions, and calculations should be used.

Unlike other lighting measures this one applies only to RF applications (because there is no defined baseline for TOS or NC applications).

###### Definition of Efficient Equipment

A lighting fixture that replaces an existing fixture to provide the same or greater lumen output at a lower kW consumption.

###### Definition of Baseline Equipment

The definition of baseline equipment is the existing lighting fixture.

###### Deemed Lifetime of Efficient Equipment

The lifetime of the efficient equipment fixture is the rated fixture life divided by hours of use. If unknown the default lifetime, regardless of program type is 15 years.

###### Deemed Measure Cost

The actual cost of the efficient light fixture should be used.

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the location type. Values are provided for each building type in section 4.5.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh  = ((Wattsbase-WattsEE)/1000)  * Hours * WHFe * ISR

Where:

Wattsbase 	= Input wattage of the existing system which  depends on the baseline fixture configuration (number and  type of lamp) and ballast factor (if applicable) and number of fixtures.

= Actual

WattsEE	= New Input wattage of EE fixture which depends on new fixture configuration (number of lamps) and ballast factor (if applicable) (if applicable) and number of fixtures.

= Actual

Hours	= Average hours of use per year as provided by the customer or selected from the Reference Table in Section 4.5, Fixture annual operating hours,  by building type.  If hours or building type are unknown, use the Miscellaneous value.

WHFe 	= Waste heat factor for energy to account for cooling energy savings from efficient lighting is selected from the Reference Table in Section 4.5 for each building type. If building is un-cooled, the value is 1.0.

ISR 		= In Service Rate or the percentage of units rebated that get installed.

=100% if application form completed with sign off that equipment is not placed into storage. If sign off form not completed assume the following 3 year ISR assumptions:

| Weighted Average 1st year In Service Rate (ISR) | 2nd year Installations | 3rd year Installations | Final Lifetime In Service Rate |
| --- | --- | --- | --- |
| 93.4% | 2.5% | 2.1% | 98.0% |

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = (((WattsBase-WattsEE)/1000) * ISR * Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

###### Deferred Installs

As presented above, if a sign off form is not completed the characterization assumes that a percentage of bulbs purchased are not installed until Year 2 and Year 3 (see ISR assumption above). The Illinois Technical Advisory Committee has determined the following methodology for calculating the savings of these future installs.

Year 1 (Purchase Year) installs:	Characterized using assumptions provided above or evaluated assumptions if available.

Year 2 and 3 installs: 	Characterized using delta watts assumption and hours of use from the Install Year, i.e., the actual deemed (or evaluated if available) assumptions active in Year 2 and 3 should be applied.

The NTG factor for the Purchase Year should be applied.

###### Summer Coincident Demand Savings

ΔkW  = ((Wattsbase-WattsEE)/1000)  * WHFd * CF * ISR

Where:

WHFd 	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is selected from the Reference Table in Section 4.5 for each building type. If the building is not cooled WHFd is 1.

CF	= Summer Peak Coincidence Factor for measure is selected from the Reference able in Section 4.5 for each building type. If the building type is unknown, use the Miscellaneous value of 0.66.

Other factors as defined above.

###### Natural Gas Energy Savings

ΔTherms  =  (((WattsBase-WattsEE)/1000) * ISR * Hours * - IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting.  This value is selected from the Reference Table in Section 6.5 for each building type.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

If there are differences between the maintenance of the efficient and baseline lighting system then they should be evaluated on a project-by-project basis.

###### Measure Code: CI-LTG-MSCI-V04-210101

###### Review Deadline: 1/1/2026

### Multi-Level Lighting Switch

###### Description

This measure relates to the installation new multi-level lighting switches on an existing lighting system.

This measure can only relate to the adding of a new control in an existing building, since multi-level switching is required in the Commercial new construction building energy code (IECC 2012/2015/2018).

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient system is assumed to be a lighting system controlled by multi-level lighting controls.

###### Definition of Baseline Equipment

The baseline equipment is assumed to be an uncontrolled lighting system where all lights in a given area are on the same circuit or all circuits come on at the same time.

###### Deemed Lifetime of Efficient Equipment

The expected measure life for all lighting controls is assumed to be 10 years.

###### Deemed Measure Cost

When available, the actual cost of the measure shall be used.  When not available, the incremental capital cost for this measure is assumed to be $274.

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the location type. Values are provided for each building type in the reference section below.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh 	= KWControlled* Hours * ESF * WHFe

Where:

KWControlled  	= Total lighting load connected to the control in kilowatts.

= Actual

Hours	= total operating hours of the controlled lighting circuit before the lighting controls are installed. This number should be collected from the customer.  Average hours of use per year are provided in the Reference Table in Section 4.5, Fixture annual operating hours,  for each building type if customer specific information is not collected.  If unknown buidling type, use the Miscellaneous value.

ESF	=  Energy Savings factor (represents the percentage reduction to the KWcontrolled due to the use of multi-level switching).

= Dependent on building type:

| Building Type | Energy Savings Factor (ESF) |
| --- | --- |
| Private Office | 21.6% |
| Open Office | 16.0% |
| Retail | 14.8% |
| Classrooms | 8.3% |
| Unknown, average | 15% |

WHFe	= Waste heat factor for energy to account for cooling energy savings from efficient lighting is provided in the Reference Table in Section 4.5 for each building type.  If building is un-cooled, the value is 1.0.

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = KWControlled* Hours * ESF * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

###### Summer Coincident Peak Demand Savings

ΔkW  = KWcontrolled  * ESF * WHFd* CF

Where:

WHFd	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is provided in the Reference Table in Section 4.5. If the  building is un-cooled WHFd is 1.

CF	= Summer Peak Coincidence Factor for measure is provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value of 0.66.

###### Natural Gas Energy Savings

Δtherms = KWControlled* Hours * ESF  * - IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting and provided in the Reference Table in Section 4.5 by building type.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-LTG-MLLC-V05-210101

###### Review Deadline: 1/1/2025

### Lighting Controls

###### Description

This measure relates to the installation of new occupancy or daylighting sensors and controls on a new or existing lighting system.  Lighting control types covered by this measure include wall, ceiling, fixture mounted or integrated controls in addition to Luminaire Level Lighting Controls (LLLCs) or Networked Lighting Controls (NLC) which have additional high-end trim and networking capabilities. Passive infrared, ultrasonic detectors and fixture-mounted sensors or sensors with a combination thereof are eligible.  Lighting controls required by state energy codes are not eligible.  This must be a new installation with additional control features and may not soley be a replacement of an existing lighting control with the same control features.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Lighting that is controlled by any of the control strategies characterized in this measure; occupancy, daylighting or dual (occupancy and daylighting) controls with or without high-end trim, and Luminaire-level lighting controls (LLLCs) / Networked Lighting Controls (NLC).

LLLCs or NLCs are defined according to DesignLights Consortium (DLC) Networked Lighting Controls definition, which requires systems to have fixture networking capabilities, individual addressability, occupancy sensing, daylight harvesting, high-end trim, flexible zoning, continuous dimming, scheduling and cybersecurity. The network ability allows building managers to group lights with specific zonal control and scheduling strategies, energy monitoring and high-end trim resulting in a higher savings capability. While DLC listing is not a requirement for any control type characterized in this measure, programs should consider eligibility requirements that ensure quality product is installed.

A subset of occupancy sensors are those that are programmed as “vacancy” sensors. To qualify as a vacancy sensor, the control must be configured such that manual input is required to turn on the controlled lighting and the control automatically turns the lighting off. Additional savings are achieved compared to standard occupancy sensors because lighting does not automatically turn on and occupants may decide to not turn it on. Note that vacancy sensors are not a viable option for many applications where standard occupancy sensors should be used instead.

###### Definition of Baseline Equipment

The baseline is assumed to be the existing lighting system and can include manual or no controls or an existing control strategy that is being improved. Note where an existing inefficient fixture is replaced with an efficient fixture with control, use the fixture measure to calculate savings from the wattage reduction first, then assume the efficient fixture without control as the baseline for the control measure.

###### Deemed Lifetime of Efficient Equipment

The expected measure life for Luminaire-level lighting controls (LLLCs) / Networked Lighting Controls (NLC) is assumed to be 15 years, consistent with the average expected lifetime of the fixture. For all other lighting controls, measure life is assumed to be 10 years.

###### Deemed Measure Cost

When available, the actual cost of the measure shall be used.  When not available, the following default values are provided:

| Lighting Control Type | Incremental Cost |
| --- | --- |
| Interior Wall Switch Occupancy Sensor | $55.00 |
| Interior Fixture-Mounted Occupancy Sensor | $67.00 |
| Interior Remote or Wall-Mounted Occupancy Sensor | $125.00 |
| Interior Fixture-Mounted Daylight Sensor | $50.00 |
| Interior Remote or Wall-Mounted Daylight Sensor | $65.00 |
| Interior Integrated Occupancy for LED Interior Fixtures < 10,000 Lumens | $40.00 |
| Interior Integrated Occupancy for LED Interior Fixtures >= 10,000 Lumens | $40.00 |
| Interior Integrated Dual Occupancy & Daylight Sensor for LED Interior Fixtures < 10,000 Lumens | $50.00 |
| Interior Integrated Dual Occupancy & Daylight Sensor for LED Interior Fixtures >= 10,000 Lumens | $50.00 |
| Interior Fixture-Mounted Dual Occupancy & Daylight Sensor for LED Interior Fixtures < 10,000 Lumens | $ 100.00 |
| Interior Fixture-Mounted Dual Occupancy & Daylight Sensor for LED Interior Fixtures >= 10,000 Lumens | $ 100.00 |
| Luminaire-Level Lighting Controls | $56.00 |
| Interior Networked Lighting Controls <10,000 sqft building |  | $0.86 per ft2 |  |
| Interior Networked Lighting Controls 10,000-100,000 sqft building |  | $0.59 per ft2 |  |
| Interior Networked Lighting Controls >100,000 sqft building |  | $0.40 per ft2 |  |
| High End Trim or Institutional Tuning | $0.06 per ft2 |
| Exterior Occupancy Sensor | $82.00 |

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on building type and can be found in the Reference Table in Section 4.5.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh 	= KWControlled* Hours * (ESFEE – ESFBase) * WHFe

Where:

KWControlled  	= Total lighting load connected to the control in kilowatts.  The total connected load per control should be collected from the customer or the default values presented below used. Note where an existing inefficient fixture is replaced with an efficient fixture with control, use the fixture measure to calculate savings from the wattage reduction first, then assume the efficient fixture without control as the baseline for the control measure.

| Lighting Control Type | Wattage Unit | Default kW Controlled |
| --- | --- | --- |
| Interior Wall Switch Occupancy Sensor | per control | 0.084 |
| Interior Fixture-Mounted Occupancy Sensor | per fixture | 0.081 |
| Interior Remote or Wall-Mounted Occupancy Sensor | per control | 0.338 |
| Interior Fixture-Mounted Daylight Sensor | per fixture | 0.095 |
| Interior Wall-Mounted Daylight Sensor | per control | 0.239 |
| Interior Integrated Occupancy for LED Interior Fixtures < 10,000 Lumens | per fixture | 0.031 |
| Interior Integrated Occupancy for LED Interior Fixtures >= 10,000 Lumens | per fixture | 0.118 |
| Interior Integrated Dual Occupancy & Daylight Sensor for LED Interior Fixtures < 10,000 Lumens | per control | 0.031 |
| Interior Integrated Dual Occupancy & Daylight Sensor for LED Interior Fixtures >= 10,000 Lumens | per control | 0.118 |
| Interior Fixture-Mounted Dual Occupancy & Daylight Sensor for LED Interior Fixtures < 10,000 Lumens | per control | 0.031 |
| Interior Fixture-Mounted Dual Occupancy & Daylight Sensor for LED Interior Fixtures >= 10,000 Lumens | per control | 0.118 |
| Interior Luminaire-Level Lighting Controls < 10,000 Lumens | per control | 0.031 |
| Interior Luminaire-Level Lighting Controls >= 10,000 Lumens | per control | 0.118 |
| Interior Networked Lighting Controls | kilowatts controlled per sqft | 0.00061 |
| Refrigerated Case Occupancy Sensor – Freezer and Cooler | per control | 0.090 |
| Exterior Occupancy Sensor | per fixture | 0.086 |

Hours	= total operating hours of the controlled lighting circuit before the lighting controls are installed. This number should be collected from the customer if possible.  If not possible, assume hours as prescribed below:

| Control Type |  | General Building Type |  | Reference Table in Section 4.5 Mapped Building/Space Types |  | Hours |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Networked Lighting Controls and Luminaire-Level Lighting Controls | Education | Childcare/Pre-School, College, Elementary School, High School | 4,231 |
|  | Manufacturing | Manufacturing Facility | 5,365 |
|  | Office | Office - High Rise - CAV no econ, Office - High Rise- CAV econ, Office- High Rise- VAV econ, Office- High Rise - FCU, Office- Low Rise, Office - Mid Rise | 4,453 |
|  | Retail | Convenience Store, Drug Store, Grocery, Retail - Department Store, Retail - Strip Mall | 6,936 |
|  | Warehouse | Warehouse | 5,116 |
|  | All Other | All other building/space types in the Reference Table in Section 4.5 | Use Fixture Annual Operating Hours in the Reference Table in Section 4.5 |
| All other | All | All | Use Fixture Annual Operating Hours in the Reference Table in Section 4.5 |

ESF	=  Energy Savings Factor (represents the percentage reduction to the operating Hours from the non-controlled lighting system) from the new lighting controls installed. Where available and with building owner consent, custom savings from controls may be used via networked trending software. If unavailable or consent not provided, defaults are provided below which assume installation is appropriate to provide the savings described. For dual controls and fixtures with high-end trim this should be reviewed and verified via representative spot checks to ensure daylighting capabilities will provide savings and fixture tuning is being performed.

| Lighting Control Type | Energy Savings Factor |
| --- | --- |
| Fixture Measurement of Control savings through Networked Trending (Interior or Exterior) | Custom |
| Interior Occupancy Sensor (Switch, Wall, Fixture or Remote Mounted or Integrated in Fixture) | 24% 37% with High End Trim |
| Interior Occupancy Sensor configured as “Vacancy Sensor” (Switch, Wall, Fixture or Remote Mounted or Integrated in Fixture) | 31% 44% with High End Trim |
| Interior Daylight Sensor (Wall, Fixture or Remote Mounted) | 28% 41% with High End Trim |
| Interior Dual Occupancy & Daylight Sensor (Integrated of Fixture Mounted) | 38% 51% with High End Trim |
| Interior Networked Luminaire-Level Lighting Controls | 61% |
| Interior Networked Lighting Controls Only with No LLLCs | 35% |
| Interior Networked Lighting Controls (unknown or mixed LLLCs) | 49% |
| Refrigerated Case Occupancy Sensor – Freezer and Cooler | 27% |
| Exterior Occupancy Sensor | 41% |
| No Lighting Control | 0% |

ESFBase	=  Energy Savings Factor of the lighting controls that existed before the new lighting controls were installed. If prior existence of lighting controls is unknown, assume 0.

WHFe	= Waste heat factor for energy to account for cooling energy savings from efficient lighting is provided in the Reference Table in Section 4.5 for each building type.  If building is un-cooled, the value is 1.0.

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = KWControlled* Hours * (ESFEE – ESFBase) * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5. If unknown, use the Miscellaneous value.

###### Summer Coincident Peak Demand Savings

ΔkW  = KWcontrolled  * WHFd * (CFbaseline – CFLC)

Where:

WHFd	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is provided in the Reference Table in Section 4.5. If the  building is un-cooled WHFd is 1.

CFbaseline 	= Baseline Summer Peak Coincidence Factor for the lighting system without lighting controls installed selected from the Reference Table in Section 4.5 for each building type. If the building type is unknown, use the Miscellaneous value of 0.66

CFLC 	= Retrofit Summer Peak Coincidence Factor the lighting system with lighting controls installed is 0.15 regardless of building type.

###### Natural Gas Energy Savings

Δtherms = KWControlled* Hours * (ESFEE – ESFBase) * - IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting and provided in the Reference Table in Section 4.5 by buidling type.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-LTG-OSLC-V07-220101

###### Review Deadline: 1/1/2024

### Solar Light Tubes

###### Description

A tubular skylight which is 10” to 21” in diameter with a prismatic or translucent lens is installed on the roof of a commercial facility.  The lens reflects light captured from the roof opening through a highly specular reflective tube down to the mounted fixture height.  When in use, a light tube fixture resembles a metal halide fixture.  Uses include grocery, school, retail and other single story commercial buildings.

In order that the savings characterized below apply, the electric illumination in the space must be automatically controlled to turn off or down when the tube is providing enough light.

This measure was developed to be applicable to the following program types:  TOS, NC, RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is assumed to be a tubular skylight that concentrates and directs light from the roof to an area inside the facility.

###### Definition of Baseline Equipment

The baseline equipment for this measure is a fixture with comparable luminosity.  The specifications for the baseline lamp depend on the size of the Light Tube being installed.

###### Deemed Lifetime of Efficient Equipment

The estimated useful life for a light tube commercial skylight is 10 years.

###### Deemed Measure Cost

If available, the actual incremental cost should be used.  For analysis purposes, assume an incremental cost for a light tube commercial skylight is $750.

###### Loadshape

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on location.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh	= kWf * HOURS * WHFe

Where:

kWf		= Connected load of the fixture the solar tube replaces

| Size of Tube | Average Lumen output for Chicago Illinois (minimum) | Equivalent fixture | kW |
| --- | --- | --- | --- |
| 21” | 9,775 (4,179) | 50% 3 x 2 32W lamp CFL (207W, 9915 lumens) 50% 4 lamp F32 w/Elec 4’ T8 (114W, 8895 lumens) | 0.161 |
| 14” | 4,392 (1,887) | 50% 2 42W lamp CFL (94W, 4406 lumens) 50% 2 lamp F32 w/Elec 4’ T8 (59W, 4448 lumens) | 0.077 |
| 10” | 2,157 (911) | 50% 1 42W lamp CFL (46W, 2203 lumens) 50% 1 lamp F32 w/Elec 4’ T8 (32W, 2224 lumens) | 0.039 |
|  |  | AVERAGE | 0.092 |

HOURS		= Equivalent full load hours

= 2400

WHFe 	= Waste heat factor for energy to account for cooling energy savings from efficient lighting is selected from the Reference Table in Section 4.5 for each building type.  If building is un-cooled, the value is 1.0.

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = kWf * HOURS * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5. If unknown, use the Miscellaneous value.

###### Summer Coincident Peak Demand Savings

∆kW 	= ∆kWf * WHFd *CF

Where:

WHFd 	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is selected from the Reference Table in Section 4.5 for each building type.   If the building is not cooled WHFd is 1.

CF	= Summer Peak Coincidence Factor for measure is selected from the Reference Table in Section 4.5 for each building type. If the building type is unknown, use the Miscellaneous value of 0.66.

###### Natural Gas Savings

ΔTherms  =  ∆kWf * HOURS *- IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting. Please select from the Reference Table in Section 4.5 for each building type.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-LTG-STUB-V03-200101

###### Review Deadline: 1/1/2025

### T5 Fixtures and Lamps

###### Description

T5 Lamp/ballast systems have higher lumens per watt than a standard T8 or an existing T8 or T12 system. The smaller lamp diameter allows for better optical systems, and more precise control of lighting. These characteristics result in light fixtures that produce equal or greater light than standard T8 or T12 fixtures, while using fewer watts.

This measure applies to the installation of new equipment with efficiencies that exceed that of the equipment that would have been installed following standard market practices and is applicable to time of sale as well as retrofit measures.

If the implementation strategy does not allow for the installation location to be known, a deemed split of 99% Commercial and 1% Residential should be used.

This measure was developed to be applicable to the following program types: TOS, EREP, DI.

If applied to other program types, the measure savings should be verified.

The measure applies to all commercial T5 installations excluding new construction and substantial renovation or change of use measures (see lighting power density measure).  Lookup tables have been provided to account for various installations. Actual existing equipment wattages should be compared to new fixture wattages whenever possible while maintaining lumen equivalent designs.  Default new and baseline assumptions are provided if existing equipment cannot be determined.  Actual costs and hours of use should be utilized when available. Default component costs and lifetimes have been provided for Operating and Maintenance Calculations. Please see the Definition Table to determine applicability for each program. Configurations not included in the TRM may be included in custom program design using the provided algorithms as long as energy savings is achieved. The following table defines the applicability for different programs:

| Time of Sale (TOS) | Early Replacement (EREP) and DI |
| --- | --- |
| This program applies to installations where customer and location of equipment is not known, or at time of burnout of existing equipment. T5 Lamp/ballast systems have higher lumens per watt than a standard T8 system. The smaller lamp diameter allows for better optical systems, and more precise control of lighting. These characteristics result in light fixtures that produce equal or greater light than standard T8 fixtures, while using fewer watts. | For installations that upgrade installations before the end of their useful life. T5 Lamp/ballast systems have higher lumens per watt than a standard T8 or T12 system. The smaller lamp diameter allows for better optical systems, and more precise control of lighting. These characteristics result in light fixtures that produce equal or greater light than standard T8 or T12 fixtures, while using fewer watts and having longer life. |

###### Definition of Efficient Equipment

The definition of efficient equipment varies based on the program and is defined below:

| Time of Sale (TOS) | Early Replacement (EREP) and DI |
| --- | --- |
| 4' fixtures must use a T5 lamp and ballast configuration. 1' and 3' lamps are not eligible. High Performance Troffers must be 85% efficient or greater. T5 HO high bay fixtures must be 3, 4 or 6 lamps and 90% efficient or better. | 4' fixtures must use a T5 lamp and ballast configuration. 1' and 3' lamps are not eligible. High Performance Troffers must be 85% efficient or greater. T5 HO high bay fixtures must be 3, 4 or 6 lamps and 90% efficient or better. |

###### Definition of Baseline Equipment

The definition of baseline equipment varies based on the program and is defined below:

| Time of Sale (TOS) | Early Replacement (EREP) and DI |
| --- | --- |
| The baseline is T8 with equivalent lumen output. In high-bay applications, the baseline is pulse start metal halide systems. | The baseline is the existing system. In July 14, 2012, Federal Standards were enacted that were expected to eliminate T-12s as an option for linear fluorescent fixtures. Through v3.0 of the TRM, it was assumed that the T-12 would no longer be baseline for retrofits from 1/1/2016. However, due to significant loopholes in the legislation, T-12 compliant product is still freely available and in Illinois T-12s continue to hold a significant share of the existing and replacement lamp market. Therefore the timing of the sunsetting of T-12s as a viable baseline has been pushed back in v7.0 until 1/1/2020 and will be revisited in future update sessions. There will be a baseline shift applied to all measures installed before 2020 in years remaining in the measure life. See table C-1. |

###### Deemed Lifetime of Efficient Equipment

The lifetime of the efficient equipment fixture should be the rated life of the fixture divided by hours of use. If unknown default is, regardless of program type is 12 years.

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh  =( (Wattsbase-WattsEE)/1000)  * Hours *WHFe*ISR

Where:

Wattsbase 	= Input wattage of the existing system which depends on the baseline fixture configuration (number and  type of lamp) and number of fixtures.  Value can be selected from the appropriate reference table as shown below, of a custom value can be entered if the configurations in the tables is not representative of the exisitng system.

WattsEE	= New Input wattage of EE fixture which depends on new fixture configuration (number of lamps) and ballast factor and number of fixtures.  Value can be selected from the appropriate reference table as shown below, of a custom value can be entered if the configurations in the tables is not representative of the exisitng system.

| Program | Reference Table |
| --- | --- |
| Time of Sale | A-1: T5 New and Baseline Assumptions |
| Early Replacement, DI | A-2: T5 New and Baseline Assumptions |

Hours	= Average hours of use per year as provided by the customer or selected from the Reference Table in Section 4.5, Fixture annual operating hours,  by building type.  If hours or building type are unknown, use the Miscellaneous value.

WHFe 	= Waste heat factor for energy to account for cooling energy savings from efficient lighting is selected from the Reference Table in Section 4.5 for each building type.  If building is un-cooled, the value is 1.0.

ISR 	 	= In Service Rate or the percentage of units rebated that get installed.

=100% if application form completed with sign off that equipment is not placed into storage. If sign off form not completed assume the following 3 year ISR assumptions:

| Weighted Average 1st year In Service Rate (ISR) | 2nd year Installations | 3rd year Installations | Final Lifetime In Service Rate |
| --- | --- | --- | --- |
| 98% | 0% | 0% | 98.0% |

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = (((WattsBase-WattsEE)/1000) * ISR * Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

###### Summer Coincident Demand Savings

ΔkW  =((Wattsbase-WattsEE)/1000)  * WHFd*CF*ISR

Where:

WHFd 	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is selected from the Reference Table in Section 4.5 for each building type. If the building is not cooled WHFd is 1.

CF	= Summer Peak Coincidence Factor for measure is selected from the Reference Table in Section 4.5 for each building type. If the building type is unknown, use the Miscellaneous value.

###### Natural Gas Energy Savings

ΔTherms  =  (((WattsBase-WattsEE)/1000) * ISR * Hours *- IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting.  This value is selected from the Reference Table in Section 4.5 for each building type.

Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

See Reference tables for Operating and Maintenance Values

| Program | Reference Table |
| --- | --- |
| Time of Sale | B-1: T5 Component Costs and Lifetime |
| Early Replacement, DI | B-2: T5 Component Costs and Lifetime |

###### Reference Tables

See following page.

A-1:  Time of Sale:  T5 New and Baseline Assumptions

A-2:  EaT5 New and Baseline Assumptions

| EE Measure Description | EE Cost | WattsEE |  | Baseline Description | WattsBASE |
| --- | --- | --- | --- | --- | --- |
| 3-Lamp T5 High-Bay | $200.00 | 180 |  | 200 Watt Pulse Start Metal-Halide | 232 |
| 4-Lamp T5 High-Bay | $225.00 | 234 |  | 250 Watt Metal-Halide | 295 |
| 6-Lamp T5 High-Bay | $250.00 | 358 |  | 320 Watt Pulse Start Metal-Halide | 350 |
|  |  |  |  | 400 Watt Metal-Halide | 455 |
| 1-Lamp T5 Troffer/Wrap | $100.00 | 32 |  | 400 Watt Pulse Start Metal-Halide | 476 |
| 2-Lamp T5 Troffer/Wrap | $100.00 | 64 |  |  |  |
|  |  |  |  | 1-Lamp F34T12 w/ EEMag Ballast | 40 |
| 1-Lamp T5 Industrial/Strip | $70.00 | 32 |  | 2-Lamp F34T12 w/ EEMag Ballast | 68 |
| 2-Lamp T5 Industrial/Strip | $70.00 | 64 |  | 3-Lamp F34T12 w/ EEMag Ballast | 110 |
| 3-Lamp T5 Industrial/Strip | $70.00 | 96 |  | 4-Lamp F34T12 w/ EEMag Ballast | 139 |
| 4-Lamp T5 Industrial/Strip | $70.00 | 128 |  |  |  |
|  |  |  |  | 1-Lamp F40T12 w/ EEMag Ballast | 48 |
| 1-Lamp T5 Indirect | $175.00 | 32 |  | 2-Lamp F40T12 w/ EEMag Ballast | 82 |
| 2-Lamp T5 Indirect | $175.00 | 64 |  | 3-Lamp F40T12 w/ EEMag Ballast | 122 |
|  |  |  |  | 4-Lamp F40T12 w/ EEMag Ballast | 164 |
|  |  |  |  | 1-Lamp F40T12 w/ Mag Ballast | 57 |
|  |  |  |  | 2-Lamp F40T12 w/ Mag Ballast | 94 |
|  |  |  |  | 3-Lamp F40T12 w/ Mag Ballast | 147 |
|  |  |  |  | 4-Lamp F40T12 w/ Mag Ballast | 182 |
|  |  |  |  | 1-Lamp F32T8 | 32 |
|  |  |  |  | 2-Lamp F32T8 | 59 |
|  |  |  |  | 3-Lamp F32T8 | 88 |
|  |  |  |  | 4-Lamp F32T8 | 114 |

B-1:  Time of Sale T5 Component Costs and Lifetime

B-2:  T5 Early Replacement Component Costs and Lifetime

C-1:  T12 Baseline Adjustment:

For early replacement measures replacing existing T12 fixtures the full savings (as calculated above in the Algorithm section) will be claimed for the remaining useful life of the T12 fixture. This should be calculated as follows:

RUL of existing T12 fixture = (1/3 * 40,000)/Hours.

A savings adjustment should then be applied to the annual savings for the remainder of the measure life.  The adjustment to be applied for each measure should be calculated as:

% Adjustment = (TOS Base Watts – Efficient Watts)/(Existing T12 Watts – Efficient Watts)

The adjustment to be applied for each default measure described above is listed in the reference table below:

| Savings Adjustment Factors |  |  |  |
| --- | --- | --- | --- |

###### Measure Code: CI-LTG-T5FX-V08-200101

###### Review Deadline: 1/1/2025

### Occupancy Controlled Bi-Level Lighting Fixtures

###### Description

This measure relates to replacing existing uncontrolled continuous lighting fixtures with new bi-level lighting fixtures. This measure can only relate to replacement in an existing building, since multi-level switching is required in the Commercial new construction building energy code (IECC 2012/2015/2018).

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient system is assumed to be an occupancy controlled lighting fixture that reduces light level during unoccupied periods.

###### Definition of Baseline Equipment

The baseline equipment is assumed to be an uncontrolled lighting system on continuously, e.g. in stairwells and corridors for health and safety reasons.

###### Deemed Lifetime of Efficient Equipment

The expected measure life for all lighting controls is assumed to be 10 years.

###### Deemed Measure Cost

When available, the actual cost of the measure shall be used.  When not available, the assumed measure cost is $274.

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the location type. Values are provided for each building type in the reference section below.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh 	= (KWBaseline  - (KWControlled *(1 –ESF))) * Hours * WHFe

Where:

KWBaseline 	= Total baseline lighting load of the existing/baseline fixture

= Actual

Note that if the existing fixture is only being retrofit with bi-level occupancy controls and not being replaced KWBaseline will equal KWControlled  .

KWControlled	= Total contolled lighting load at full light output of the new bi-level fixture

= Actual

Hours	= Number of hours lighting is on. This measure is limited to 24/7 operation.

= 8,766

ESF	=  Energy Savings factor (represents the percentage reduction to the KWControlled due to the occupancy control).

= % Standby Mode * (1 - % Full Light at Standby Mode)

% Standby Mode	= Represents the percentage of the time the fixture is operating in standby (i.e. low-wattage) mode.

% Full Light at Standby Mode 	= Represents the assumed wattage consumption during standby mode relative to the full wattage consumption. Can be achieved either through dimming or a stepped control strategy.

= Dependent on application. If participant provided or metered data is available for both or either of these inputs a custom savings factor should be calculated. If not defaults are provided below:

| Application | % Standby Mode | % Full Light at Standby Mode | Energy Savings Factor (ESF) |
| --- | --- | --- | --- |
| Stairwells | 78.5% | 50% | 39.3% |
|  |  | 33% | 52.6% |
|  |  | 10% | 70.7% |
|  |  | 5% | 74.6% |
| Corridors | 50.0% | 50% | 25.0% |
|  |  | 33% | 33.5% |
|  |  | 10% | 45.0% |
|  |  | 5% | 47.5% |
| Other 24/7 Space Type | 50.0% | 50% | 25.0% |
|  |  | 33% | 33.5% |
|  |  | 10% | 45.0% |
|  |  | 5% | 47.5% |

WHFe	= Waste heat factor for energy to account for cooling energy savings from efficient lighting is provided in the Reference Table in Section 4.5 for each building type.  If building is un-cooled, the value is 1.0.

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = (KWBaseline  - (KWControlled *(1 –ESF))) * Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

###### Summer Coincident Peak Demand Savings

ΔkW  = (KWBaseline  - (KWControlled * (1 –ESF))) * WHFd * (CFbaseline - CFos)

Where:

WHFd	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is provided in the Reference Table in Section 4.5. If the  building is un-cooled WHFd is 1.

CFbaseline 	= Baseline Summer Peak Coincidence Factor for the lighting system without Occupancy Sensors installed selected from the Reference Table in Section 4.5 for each building type. If the building type is unknown, use the Miscellaneous value of 0.66

CFos 	= Retrofit Summer Peak Coincidence Factor the lighting system with Occupancy Sensors installed  is 0.15 regardless of building type.

###### Natural Gas Heating Penalty

If natural gas heating:

Δtherms = (KWBaseline  - (KWControlled *(1 –ESF))) * Hours * - IFTherms

Where:

IFTherms 	= Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting and provided in the Reference Table in Section 4.5 by buidling type.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-LTG-OCBL-V04-210101

###### Review Deadline: 1/1/2025

### Commercial ENERGY STAR Specialty Compact Fluorescent Lamp (CFL) – Retired 12/31/2018, Removed in v8

### LED Open Sign

###### Description

LED open signs must replace an existing neon open sign. LED drivers can be either electronic switching or linear magnetic, with the electronic switching supplies being the most efficient. The on/off power switch may be found on either the power line or load side of the driver, with the line side location providing significantly lower standby losses when the sign is turned off and is not operating. All new open signs must meet UL-84 (UL-844) requirements.

Replacement signs cannot use more than 20% of the input power of the sign that is being replaced.

This measure was developed to be applicable to the following program types:  RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient product is an LED type illuminated open sign.

###### Definition of Baseline Equipment

The baseline equipment is a neon type illuminated open sign.

###### Deemed Lifetime of Efficient Equipment

The estimated useful life is 15 years.

###### Deemed Measure Cost

The actual measure installation cost should be used (including material and labor).

###### Loadshape

Loadshape C06 - Commercial Indoor Lighting

Loadshape C07 - Grocery/Conv. Store Indoor Lighting

Loadshape C08 - Hospital Indoor Lighting

Loadshape C09 - Office Indoor Lighting

Loadshape C10 - Restaurant Indoor Lighting

Loadshape C11 - Retail Indoor Lighting

Loadshape C12 - Warehouse Indoor Lighting

Loadshape C13 - K-12 School Indoor Lighting

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

Loadshape C18 - Industrial Indoor Lighting

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the location type. Values are provided for each building type in the reference section in Section 4.5.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

The following equation was used to determine the energy savings from installing LED open signs:

ΔkWh = (Wattsbase – Wattsee) / 1,000 * Hours * WHFe

Where:

Wattsbase	= Wattage of neon sign with magnetic high voltage transformer

= Actual; if unknown use 46.0W

Wattsee		= Wattage of LED sign with low voltage transformer

= Actual; if unknown use 14.9W

Hours	= Annual hours of operation, assumed to be consistent with operating hours. Values are provided in the Reference Table in Section 4.5.

WHFe	= Waste heat factor for energy to account for cooling energy savings from efficient lighting are provided below for each building type in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

###### Heating Penalty

If electrically heated building:

ΔkWhheatpenalty  = ((WattsBase-WattsEE)/1000) * Hours * -IFkWh

Where:

IFkWh	= Lighting-HVAC Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

###### Demand Savings

ΔkW 	= ((Wattsbase – Wattsee)/ 1000) * CF * WHFd

Where:

WHFd	= Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings is provided in Referecne Table in Section 4.5.  If unknown, use the Miscellaneous value.

CF	= Summer Peak Coincidence Factor for measure is provided in the Reference Table in Section 4.5.  If unknown, use the Miscellaneous value.

Other variables as provided above.

Based on defaults provided above, the deemed energy savings are provided below:

Electric Energy and Coincident Peak Demand Savings

| Building Types | Energy Savings (kWh) | ΔkWhheatpenalty (if electric heat) | Coincident Demand Savings (kW) |
| --- | --- | --- | --- |
| Convenience Store | 158 | -120 | 0.0298 |
| Grocery | 152 | -74 | 0.0277 |
| Healthcare Clinic | 169 | -17 | 0.0374 |
| Hotel/Motel - Common | 229 | -143 | 0.0282 |
| Movie Theater | 121 | -73 | 0.0227 |
| Restaurant | 203 | -85 | 0.0277 |
| Retail - Department Store | 191 | -88 | 0.0387 |
| Miscellaneous | 115 | -55 | 0.0245 |

###### Natural Gas Savings

Heating Penalty if fossil fuel heated building (or if heating fuel is unknown):

ΔTherms  = ((WattsBase-WattsEE)/1000) * Hours *- IFTherms

Where:

IFTherms	= Lighting-HVAC Interation Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficent lighting. Values are provided in the Reference Table in Section 4.5. If unknown, use the Miscellaneous value.

Other factors as defined above

Based on defaults provided above, the deemed penalty is provided below:

| Building Type | ΔThermsheatpenalty (if gas heat) |
| --- | --- |
| Convenience Store | -5.1 |
| Grocery | -3.2 |
| Healthcare Clinic | -0.7 |
| Hotel/Motel - Common | -6.1 |
| Movie Theater | -3.2 |
| Restaurant | -3.6 |
| Retail - Department Store | -3.7 |
| Miscellaneous | -2.3 |

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-LTG-OPEN-V02-220101

###### Review Deadline: 1/1/2026

### LED Streetlighting

###### Description

Existing streetlights are retrofitted to be illuminated with light emitting diodes (LED) instead of less efficient lamps. Incentive applies for the replacement or retrofit of existing streetlights with new LED lamps.

This measure was developed to be applicable to the following program types: EREP, TOS*.

If applied to other program types, the measure savings should be verified.

* It is recommended to consider likely high freeridership for time of sale applications of this measure.

###### Definition of Efficient Equipment

The efficient equipment is the installed LED streetlight.

###### Definition of Baseline Equipment

For early replacement, the baseline equipment is the existing streetlight for its’ remaining useful life, and a new baseline High Pressure Sodium lamp for the remainder of the measure life. For TOS, baseline is assumed to be High Pressure Sodium lamp.

###### Deemed Lifetime of Efficient Equipment

The assumed effective useful life (EUL) of a new LED streetlight is 20 years for standard operation or 10 years for 8766 hour lighting.

For early replacement, it is assumed the existing unit has a remaining useful life (RUL) of 3 years for standard operation and 1.5 year for 8760 operation.

###### Deemed Measure Cost

The actual measure installation cost should be used (including material and labor). The assumed deferred cost (after 3 years for standard operation and 1.5 year for 8760 operation) of replacing the existing lamp with a new High Pressure Sodium lamp is assumed to be $44. This cost should be discounted to present value using the nominal discount rate.

###### Loadshape

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is assumed to be 0 for standard usage or 1.0 for 8766 hour lighting.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

For remaining useful life (1st 3 years for standard operation and 1.5 year for 8760 operation) of existing equipment:

(1)	ΔkWh	= (Wexist - Weff) * HOURS / 1000

For remaining life of measure (next 17 years for standard operation and 8.5 years for 8760 operation) or time of sale:

(2)	ΔkWh	= (Wbase - Weff) * HOURS / 1000

Where:

Wexist		=the connected load of the existing equipment

= actual existing equipment wattage

Wbase		=the connected load of the baseline equipment

= assume appropriate High Pressure Sodium lamp wattage for application.

Weff		=the connected load of the efficient equipment

= actual efficient equipment wattage

EFLH 		= annual operating hours of the lamp

= 4,303 hours for standard operation

= 8,766 hours for always on lighting

1000		= conversion factor (W/kW)

Mid Life Baseline Adjustment

To calculate the mid life adjustment, divide the savings for remaining life of measure (1), by the first year savings (2) as provided above.

For example, an existing 469 watts mercury vapor streetlight is replaced by an LED light of 161 watts with standard operation. High Pressure Sodium equivalent is 295 watts:

ΔkWh (first three years) 	= ((469 - 161) * 4,303) / 1000

= 1,325.3 kWh

ΔkWh (remaining seventeen years) 	= ((295 - 161) * 4,303) / 1000

= 576.6 kWh

Therefore, a midlife adjustment of 43.5% (576.6/1325.3) would be applied after 3 years.

###### Summer Coincident Peak Demand Savings

ΔkW	= (Wbase - Weff) / 1000 * CF

Where:

CF	= Summer Peak Coincidence Factor for measure

= 0 for Standard operation

= 1 for 8766 lighting

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

For EREP: to calculate an O&M adjustment, in addition to the deferred HPS replacement after 3 years, assume one additional HPS replacement lamp costing $44 in year nine and year fifteen for standard operation or every 2.7 years for 8,766 hour lighting.

For TOS: Assume one additional HPS replacement costing $44 every 6 years for standard operation or every 2.7 years for 8,766 hour lighting.

###### Measure Code: CI-LTG-STRT-V03-220101

###### Review Deadline: 1/1/2025

### Exterior Photocell Repair

###### Description

This measure characterizes the repair of a photocell on an existing exterior light. A photocell is designed to switch exterior lights off during daylight hours, but if broken the fixtures may remain on 8760 hours.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient condition is an exterior light with a repaired or replaced photocell. The specifications and location of exterior lighting fixtures must be verified.

###### Definition of Baseline Equipment

The baseline condition is an exterior light with a broken photocell.

###### Deemed Lifetime of Efficient Equipment

The assumed measure life is 2 years.

###### Deemed Measure Cost

The deemed measure cost is $65.52 per lighting sensor.

###### Loadshape

Loadshape C19 - Industrial Outdoor Lighting

Loadshape C20 - Commercial Outdoor Lighting

###### Coincidence Factor

The summer peak coincidence factor for this measure is assumed to be 1.0.  The savings for this measure will be throughout the daytime hours.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

∆kWh = (Wattsfixture/1000) * (HOUPRE – HOUPOST)

Where:

Wattsfixture	= Input wattage of exterior lighting fixture(s) controlled by photocell

HOUPRE		= Fixture Annual Operating Hours before Photocell repair/replacement

= 8,766 hours

HOUPOST		= Fixture Annual Operating Hours with Photocell repaired / replaced

= 4,303 hours

###### Summer Coincident Peak Demand Savings

ΔkW	= ∆kWh / (HOUPRE – HOUPOST) * CF

Where:

CF	= Summer Peak Coincidence Factor for measure

= 1

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-LTG-PHRP-V01-210101

###### Review Deadline: 1/1/2025

## Refrigeration End Use

### Automatic Door Closer for Walk-In Coolers and Freezers

###### Description

This measure is for installing an auto-closer to the main insulated opaque door(s) of a walk-in cooler or freezer. The auto-closer must firmly close the door when it is within 1 inch of full closure.

This measure was developed to be applicable to the following program types:  RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

This measure consists of the installation of an automatic, hydraulic-type door closer on main walk-in cooler or freezer doors. These closers save energy by reducing the infiltration of warm outside air into the refrigeration itself.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline condition is assumed to be a walk in cooler or freezer without an automatic closure.

###### Deemed Lifetime of Efficient Equipment

The deemed measure life is 8 years.

###### Deemed Measure Cost

The deemed measure cost is $156.82 for a walk-in cooler or freezer.

###### Loadshape

Loadshape C22 - Commercial Refrigeration

###### Coincidence Factor

The measure has deemed kW savings therefore a coincidence factor does not apply.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Savings calculations are based on values from through PG&E’s Workpaper PGECOREF110.1 – Auto-Closers for Main Cooler or Freezer Doors. Savings are averaged across all California climate zones and vintages.

| Annual Savings | kWh |
| --- | --- |
| Walk in Cooler | 943 |
| Walk in Freezer | 2307 |

###### Summer Coincident Peak Demand Savings

| Annual Savings | kW |
| --- | --- |
| Walk in Cooler | 0.137 |
| Walk in Freezer | 0.309 |

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-ATDC-V02-190101

###### Review Deadline: 1/1/2023

### Beverage and Snack Machine Controls

###### Description

This measure relates to the installation of new controls on refrigerated beverage vending machines, non-refrigerated snack vending machines, and glass front refrigerated coolers. Controls can significantly reduce the energy consumption of vending machine and refrigeration systems. Qualifying controls must power down these systems during periods of inactivity but, in the case of refrigerated machines, must always maintain a cool product that meets customer expectations. This measure relates to the installation of a new control on a new or existing unit. This measure should not be applied to ENERGY STAR qualified vending machines, as they already have built-in controls.

Vending machine categories are as defined below:

- Refrigerated Beverage Vending Machine: A commercial refrigerator that cools bottled and/or canned beverages and dispenses the bottled and/or canned beverages on payment. Bottled or canned beverages means a beverage in a sealed container.

  - Class A Machine: A refrigerated bottled and/or canned beverage vending machine that is not a combination vending machine and in which 25 percent or more of the surface area on the front side of the beverage vending machine is transparent.

  - Class B Machine: Any refrigerated bottled and/or canned beverage vending machine not considered to be Class A, and is not a combination vending machine.

- Combination Vending Machine: A bottled and/or canned beverage vending machine containing two or more compartments separated by a solid partition, that may or may not share a product delivery chute, in which at least one compartment is designed to be refrigerated, as demonstrated by the presence of temperature controls, and at least one compartment is not.

  - Combination A: Combination vending machine where 25 percent or more of the surface area on the front side of the beverage vending machine is transparent.

  - Combination B: Combination vending machine that is not considered to be Combination A.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be a standard efficiency refrigerated beverage vending machine, non-refrigerated snack vending machine, or glass front refrigerated cooler with a control system capable of powering down lighting and refrigeration systems during periods of inactivity.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to be a standard efficiency refrigerated beverage vending machine, non-refrigerated snack vending machine, or glass front refrigerated cooler without a control system capable of powering down lighting and refrigeration systems during periods of inactivity

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 5 years.

###### Deemed Measure Cost

The actual measure installation cost should be used (including material and labor), but the following control costs can be assumed for analysis purposes:

Refrigerated Vending Machine and Glass Front Cooler: $245

Non-Refrigerated Vending Machine: $233

###### Loadshape

Loadshape C52 - Beverage and Snack Machine Controls

###### Coincidence Factor

The summer peak coincidence factor for this measure is assumed to be 0.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

∆kWh=ΔkWhLighting + ΔkWhRef BMC

ΔkWhLighting =8760 – DEEROccSnsrBldgHrsOccHours*x WBulb1000

ΔkWhRef BMC = MDEC x* (SleepHours / 24) Usage Reduction Rate x* Days

Usage Reduction Rate (%) = (SleepHours / 24) x 100

Where:

OccHours  	=  Average Annual Hours facility is occupied

= Actual, if unknown assume 3,379 hrs

WBulb	= Wattage of bulb in Refrigerated Beverage Vending Machine.

= Actual. If unknown use 56.4 W for fluorescent T8 bulbs and 31.6 W for TLEDs.

MDEC	= Maximum Daily Energy Consumption per Federal regulations. Refrigerated Volume of 21 (ft3) used in the calculations. If unknown, assume Class B, post-2019:

| Class | Vintage | EQN | MDEC (kWh/d) |
| --- | --- | --- | --- |
| A | post-2019 | 0.052 * V + 2.43 | 3.52 |
| B |  | 0.052 * V + 2.20 | 3.29 |
| Combination A |  | 0.086 * V + 2.66 | 4.47 |
| Combination B |  | 0.111 * V + 2.04 | 4.37 |
| A | pre-2019 | 0.055 * V + 2.56 | 3.72 |
| B |  | 0.073 * V + 3.16 | 4.69 |

SleepHours	 = Maximum hours of sleep mode per day.

= 4 hrs

Days                      = Operating Days/yr.

= 365

For example, adding controls to a Class B post-2019 Vintage refrigerated beverage vending machine in an unknown location:

ΔkWh	= ΔkWhligthing + ΔkWhRef BMC

ΔkWhligthing 	= (8760 – OccHours) * WBulb

= ((8760 – 3,379 ) * 72 W) / 1,000

= 387 kWh/yr

ΔkWhRef BMC 	= MDEC * SleepHours/24 * Days

= 3.29 * 4/24 * 365

= 200 kWh/yr

ΔkWh	      	= 587 kWh/yr

For example, adding controls to a refrigerated beverage vending machine:

ΔkWh	= WATTSbase / 1000 * HOURS * ESF

=400/1000* 8766* 0.46

= 1613 kWh

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-BEVM-V04-220101

###### Review Deadline: 1/1/2025

### Door Heater Controls for Cooler or Freezer

###### Description

By installing a control device to turn off door heaters when there is little or no risk of condensation, one can realize significant energy savings. There are two commercially available control strategies that achieve “on-off” control of door heaters based on either (1) the relative humidity of the air in the store, or (2) the “conductivity” of the door (which drops when condensation appears). In the first strategy, the system activates your door heaters when the relative humidity in your store rises above a specific setpoint, and turns them off when the relative humidity falls below that setpoint. In the second strategy, the sensor activates the door heaters when the door conductivity falls below a certain setpoint, and turns them off when the conductivity rises above that setpoint.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be a door heater control on a commercial glass door cooler or refrigerator utilizing humidity or conductivity control.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline condition is assumed to be a commercial glass door cooler or refrigerator with a standard heated door with no controls installed.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

###### Deemed Measure Cost

The incremental capital cost, including labor costs, for a refrigeration door heater control, regardless of the control strategy, on a per door basis is $79.50 per cooler door and $90.77 per freezer door.

###### Loadshape

Loadshape C51 - Door Heater Control

###### Coincidence Factor

The summer peak coincidence factor for this measure is assumed to be 44%.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWH	= kWbase * NUMdoors * ESF * BF * 8766

Where:

kWbase	= connected load kW for typical reach-in refrigerator or freezer door and frame with a heater.

= If actual kWbase is unknown, assume 0.230 kW for freezers and 0.066 kW for coolers.

NUMdoors 	= number of reach-in refrigerator or freezer doors controlled by sensor

= Actual installed

ESF	= Energy Savings Factor; represents the percentage of hours annually that the door heater is powered off due to the controls.

= 45% for all control types

BF 	= Bonus Factor; represents the increased savings due to reduction in cooling load inside the cases, and the increase in cooling load in the building space to cool the additional heat generated by the door heaters.

| Definition | Representative Evaporator Temperature Range, °F | Typical Uses | BF |
| --- | --- | --- | --- |
| Low | -35 to 0 | Freezers for times such as frozen pizza, ice cream, etc. | 1.50 |
| Medium | 0 – 20 | Coolers for items such as meat, milk, dairy, etc | 1.30 |
| High | 20 – 45 | Coolers for items such as floral, produce and meat preparation rooms | 1.30 |

8766  		= annual hours of operation

###### Summer Coincident Peak Demand Savings

ΔkW	= (ΔkWH / 8766) * CF

Where:

CF	= Summer Coincident Factor for the measure

= 0.44

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-DHCT-V04-220101

###### Review Deadline: 1/1/2027

### Electronically Commutated Motors (ECM) for Walk-in and Reach-in Coolers / Freezers

###### Description

This measure is applicable to the replacement of an existing, uncontrolled, and continuously operating standard-efficiency shaded-pole evaporator fan motor in refrigerated display cases or fan coil in walk-ins.

This measure achieves savings by installing a more efficient motor, the result of which produces less waste heat that the cooling system must reject.

If applicable, savings from this measure may be claimed in combination with measure 4.6.6 Evaporator Fan Control for Electrically Commutated Motors.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

This measure applies to the replacement of an existing standard-efficiency shaded-pole evaporator fan motor in refrigerated display cases or fan coil in walk-ins. The replacement unit must be an electronically commutated motor (ECM) with a minimum efficiency of 66%. If controls are added as part of the motor upgrade to reduce annual run time, additional savings may potentially be claimed using measure 4.6.6 Evaporator Fan Control.

###### Definition of Baseline Equipment

The baseline is the existing shaded-pole motor(s) with no fan control operating 8760 hours continuously in a refrigerated display case or fan coil unit of a walk-in cooling unit.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years.

###### Deemed Measure Cost

The measure cost is assumed to be $230.94 (EC Motor equipment) plus $73.65 (EC Motor labor) = $304.59  per motor for a walk in cooler and walk in freezer.

###### Loadshape

Loadshape C53 - Flat

###### Coincidence Factor

The peak kW coincidence factor is 100%.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh = Savings per motor * motors

Where:

Savings per motor 	= based on the motor rating of the ECM motor:

| Evaporator Fan Motor Rating (of ECM) | Annual kWh Savings/motor |
| --- | --- |
| 16W | 652 |
| 1/15 - 1/20HP | 1,586 |
| 1/5HP | 2,320 |
| 1/3HP | 3,380 |
| 1/2HP | 4,481 |
| 3/4HP | 5,293 |

= If unknown, assume 1/15 HP, therefore 1,586 kWh saved / motor

motors			= number of fan motors replaced

###### Summer Coincident Peak Demand Savings

∆kW 	= ∆kWh/ Hours * CF * motors

Where:

∆kWh		= Gross customer annual kWh savings for the measure, as listed above

= If unknown, assume 1,586 kWh

Hours		= Full Load hours per year

= 8760

CF		= Summer Peak Coincident Factor

= 1.0

Other variables as defined above.

The following table provides the resulting kW savings (per motor), if unknown assume 0.181 kW saved / motor:

| Evaporator Fan Motor Rating (of ECM) | Peak kW Savings/motor |
| --- | --- |
| 16W | 0.074 |
| 1/15 - 1/20HP | 0.181 |
| 1/5HP | 0.265 |
| 1/3HP | 0.386 |
| 1/2HP | 0.512 |
| 3/4HP | 0.604 |

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-ECMF-V04-220101

###### Review Deadline: 1/1/2025

### ENERGY STAR Refrigerated Beverage Vending Machine

###### Description

ENERGY STAR qualified new and rebuilt vending machines incorporate more efficient compressors, fan motors, and lighting systems as well as low power mode option that allows the machine to be placed in low-energy lighting and/or low-energy refrigeration states during times of inactivity.

This measure was developed to be applicable to the following program types: TOS, NC .

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The refrigerated vending machine can be new or rebuilt but must meet the ENERGY STAR specifications, as outlined below.

A. Refrigerated Beverage Vending Machine: A commercial refrigerator that cools bottled and/or canned beverages and dispenses the bottled and/or canned beverages on payment. Bottled or canned beverages means a beverage in a sealed container.

a. Class A Machine: A refrigerated bottled and/or canned beverage vending machine that is not a combination vending machine and in which 25 percent or more of the surface area on the front side of the beverage vending machine is transparent.

b. Class B Machine: Any refrigerated bottled and/or canned beverage vending machine not considered to be Class A, and is not a combination vending machine

B. Combination Vending Machine: A bottled and/or canned beverage vending machine containing two or more compartments separated by a solid partition, that may or may not share a product delivery chute, in which at least one compartment is designed to be refrigerated, as demonstrated by the presence of temperature controls, and at least one compartment is not.

a. Combination A Machine: A combination vending machine where 25 percent or more of the surface area on the front side of the beverage vending machine is transparent.

b. Combination B Machine: A combination vending machine that is not considered to be Combination A.

###### Definition of Baseline Equipment

The baseline vending machine is a standard unit.

###### Deemed Lifetime of Efficient Equipment

The deemed lifetime of this measure is 14 years.

###### Deemed Measure Cost

The incremental cost of this measure is $500..

###### Loadshape

Loadshape C22 - Commercial Refrigeration

###### Coincidence Factor

It is assumed that controls are only effective during off-peak hours and so have no peak-kW savings.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Using the ENERGY STAR MDEC Equations, as specified in the above paragraph and the Baseline Equipment DOE Standards, the theoretical energy savings are calculated as:

kWh =  (MDECBaseline – MDEC Efficient) * Days

Where:

MDECBaseline  	= Maximum Daily Energy Consumption calculated using the equation from the table below, specific for the baseline equipment class and the volume range

MDECEfficient  	= Maximum Daily Energy Consumption calculated using the equation from the table below, specific for the ENERGY STAR Specification 4.0 equipment class and the volume range

Days		= Days per year

= Actual. If unknown, assume 365.

Maximum Daily Energy Consumption (MDEC) equations for Baseline Equipment and ENERGY STAR equipment compliant with ENERGY STAR Specification V4.0 are outline in the table below:

| Product Class | Refrigerated Volume Range (ft3) | MDEC Equation (kWh/day) Federal Standard: Baseline Equipment | MDEC Equation (kWh/day) ENERGY STAR Specification V 4.0 |
| --- | --- | --- | --- |
| Class A | 11.5 - 38.5 | 0.052 * V + 2.43 | 0.04836 * V + 2.2599 |
| Class B | 21.8 - 30.5 | 0.052 * V + 2.20 | 0.04576 * V + 1.936 |
| Combination A | 9.7 - 16 | 0.086 * V + 2.66 | 0.07998 * V + 2.4738 |
| Combination B | N/A | 0.111 * V + 2.04 | 0.09768 * V + 1.7952 |

Where:

V = the refrigerated volume (ft3) of the refrigerated bottled or canned beverage vending machine, as specified in Appendix C.

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-ESVE- V04-210101

###### Review Deadline: 1/1/2025

### Evaporator Fan Control for Electrically Commutated Motors

###### Description

This measure is for the installation of controls for Electronically Commutated Motors in existing medium temperature walk-in coolers. The controller reduces airflow of the evaporator fans when there is no refrigerant flow.

This measure achieves savings by controlling the motor(s) to run at lower speeds (or shut off entirely) when there is no refrigerant flow, the result of which produces less waste heat that the cooling system must reject.

If eligible, this measure may be claimed in combination with 4.6.4 Electronically Commutated Motors (ECM) for Walk-in and Reach-in Coolers / Freezers.

This measure was developed to be applicable to the following program types:  RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The measure must control a minimum of 1/20 HP where fans operate continuously at full speed. The measure also must reduce fan motor power by at least 75% during the off cycle. This measure is not applicable if any of the following conditions apply:

- The compressor runs more than 4380 hours annually

- The evaporator fan does not run at full speed all the time

- The evaporator fan motor runs on poly-phase power

- Evaporator does not use off-cycle or time-off defrost.

###### Definition of Baseline Equipment

In order for this characterization to apply, the existing condition must be a reach-in or walk-in freezer or cooler with continuously running evaporator fans driven by Electrically Commutated Motors

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 13 years.

###### Deemed Measure Cost

The measure cost is assumed to be $69.69 (controller equipment) plus $92.06 (controller labor) = $161.75 per motor controlled.

###### Loadshape

Loadshape C46 - Evaporator Fan Control

###### Coincidence Factor

The measure has deemed kW savings therefore a coincidence factor does not apply.

Algorithm

###### Calculation of Savings

Savings are based on a measure created by Energy & Resource Solutions for the California Municipal Utilities Association and supported by a PGE workpaper. Note that climate differences across all California climate zones result in negligible savings differences, which indicates that the average savings for the California study should apply equally as well to Illinois. Savings found in the aforementioned source are presented in combination with savings from an ECM upgrade, however for the purposes of this measure only those associated with the controller are considered.

###### Electric Energy Savings

ΔkWh = Savings per motor * motors

Where:

Savings per motor 	= based on the motor rating of the ECM motor:

| Evaporator Fan Motor Rating (of ECM) | Annual kWh Savings/motor |
| --- | --- |
| 16W | 198 |
| 1/15 - 1/20HP | 293 |
| 1/5HP | 856 |
| 1/3HP | 1,419 |
| 1/2HP | 2,126 |
| 3/4HP | 3,209 |

motors			= number of fan motors controlled

###### Summer Coincident Peak Demand Savings

ΔkW = Peak kW savings per motor (as listed in the table below) * motors (as defined above)

| Evaporator Fan Motor Rating (of ECM) | Peak kW Savings/motor |
| --- | --- |
| 16W | 0.023 |
| 1/15 - 1/20HP | 0.033 |
| 1/5HP | 0.098 |
| 1/3HP | 0.162 |
| 1/2HP | 0.243 |
| 3/4HP | 0.366 |

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-EVPF-V05-220101

###### Review Deadline: 1/1/2025

### Strip Curtain for Walk-in Coolers and Freezers

###### Description

This commercial measure pertains to the installation of infiltration barriers (strip curtains) on walk-in coolers or freezers.  Strip curtains impede heat transfer from adjacent warm and humid spaces into walk-ins when the main door is opened, thereby reducing the cooling load. As a result, compressor run time and energy consumption are reduced. The engineering assumption is that the walk-in door is open for varying durations per day based on facility type, and the strip curtain covers the entire door frame. All algorithms and assumptions are based on prescriptive methodologies detailed by the Regional Technical Forum, whose source calculations are outlined in ASHRAE’s Refrigeration Handbook for calculating refrigeration load from infiltration by air exchange.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is a strip curtain at least 0.06 inches thick added to a walk-in cooler or freezer.  The new strip curtain must cover the entire area of the doorway when the door is opened.

###### Definition of Baseline Equipment

The baseline assumption is a walk-in cooler or freezer that previously had either no strip curtain installed or an old, ineffective strip curtain installed.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 4 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $10.22/sq ft of door opening.

###### Loadshape

Loadshape C22 - Commercial Refrigeration

###### Coincidence Factor

The summer peak coincidence factor for this measure is 100%.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh	= ∆kWh/sq ft * A

Where:

∆kWh/sq ft	= Average annual kWh savings per square foot of infiltration barrier. Deemed values can be found in the table below

A	= Doorway area in square feet.

= Actual. If the actual doorway area in square feet is unknown, then use the values found in the table below

Default Energy Savings and Door Area for Strip Curtains

| Type | Pre-Existing Curtains | Energy Savings ΔkWh/sq ft | Doorway Area (sqft) |
| --- | --- | --- | --- |
| Supermarket - Cooler | Yes | 40.9 | 21 |
| Supermarket - Cooler | No | 119.9 |  |
| Supermarket - Freezer | Yes | 168.5 | 21 |
| Supermarket - Freezer | No | 494.3 |  |
| Convenience Store - Cooler | Yes | 6.3 | 21 |
| Convenience Store - Cooler | No | 23.6 |  |
| Convenience Store - Freezer | Yes | 10.0 | 21 |
| Convenience Store - Freezer | No | 33.2 |  |
| Restaurant - Cooler | Yes | 6.2 | 21 |
| Restaurant - Cooler | No | 22.5 |  |
| Restaurant - Freezer | Yes | 32.4 | 21 |
| Restaurant - Freezer | No | 114 |  |
| Refrigerated Warehouse | Yes | 53.4 | 120 |
| Refrigerated Warehouse | No | 153.4 |  |

###### Summer Coincident Peak Demand Savings

ΔkW 	= ΔkWh  / 8766 * CF

Where:

8766	= hours per year

CF	= Summer Peak Coincidence Factor for the measure

= 1.0

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-CRTN-V05-220101

###### Review Deadline: 1/1/2027

### Refrigeration Economizers

###### Description

This measure applies to commercial walk in refrigeration systems and includes two components, outside air economizers and evaporator fan controllers. Economizers save energy by bringing in outside air when weather conditions allow, rather than operating the compressor. Walk-in refrigeration systems evaporator fans run almost all the time; 24 hrs/day, 365 days/yr.  This is because they must run constantly to provide cooling when the compressor is running, and to provide air circulation when the compressor is not running.  However, evaporator fans are a very inefficient method of providing air circulation.  Installing an evaporator fan control system will turn off evaporator fans while the compressor is not running, and instead turn on an energy-efficient 35 watt fan to provide air circulation, resulting in significant energy savings. This measure allows for economizer systems with evaporator fan controls plus a circulation fan and without a circulation fan.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified. IECC code requires economizers in certain instances and therefore projects relying on code baseline definitions must verify eligibility.

###### Definition of Efficient Equipment

To qualify for this measure an economizer is installed on a walk in refrigeration system.

###### Definition of Baseline Equipment

###### The baseline condition is a walk-in refrigeration system without an economizer

###### Deemed Lifetime of Efficient Equipment

The estimated life of this measure is 15 years.

###### Deemed Measure Cost

Installation costs can vary considerably depending on system size (larger systems may require multiple economizer units), physical site layouts (locating economizer intakes and ductwork), and controls elected. Therefore, actual site-specific costs should be used.

###### Loadshape

Loadshape C22 - Commercial Refrigeration

###### Coincidence Factor

###### The summer peak coincidence factor for this measure is assumed to be 0%.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Electric energy savings is calculated based on whether evaporator fans run all.

With Fan Control Installed

ΔkWh 	= [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon * Hours]

Without Fan Control Installed

ΔkWh 	= [HP * kWhCond] – [kWEcon * DCEcon * Hours]

Where:

HP 		= Horsepower of Compressor

= actual installed

kWhCond 	= Condensing unit savings, per hp. (value from savings table)

|  | Hermetic / Semi-Hermetic | Scroll | Discus |
| --- | --- | --- | --- |
| kWh/HP | 1,256 | 1,108 | 1,051 |

Hours 		= Number of annual hours that economizer operates

| Region (city) | Hours |
| --- | --- |
| 1 (Rockford) | 2,376 |
| 2 (Chicago/O’Hare) | 1,968 |
| 3 (Springfield) | 1,728 |
| 4 (Belleview) | 1,488 |
| 5 (Marion) | 1,224 |

DCComp 	= Duty cycle of the compressor

= 50%

kWEvap 		= Connected load kW of each evaporator fan

= If known, actual installed. Otherwise assume 0.123 kW

kWCirc 		= Connected load kW of the circulating fan

= If known, actual installed. Otherwise assume 0.035 kW

nFans 		= Number of evaporator fans

= actual number of evaporator fans

DCEcon 	= Duty cycle of the economizer fan on days that are cool enough for the economizer to be working

= If known, actual installed. Otherwise assume 63%

BF 		= Bonus factor for reduced cooling load from running the evaporator fan less or (1.3)

kWEcon 		= Connected load kW of the economizer fan

= If known, actual installed. Otherwise assume 0.227 kW.

For example, adding an outdoor air economizer and fan controls in Rockford to a 5 hp walk in refrigeration unit with 3 evaporator fans would save:

ΔkWh	= [HP * kWhCond] + [((kWEvap * nFans) – kWCirc) * Hours * DCComp * BF] – [kWEcon * DCEcon * Hours]

= [5 * 1256] + [((0.123 * 3) – 0.035) * 2376 *0.5 * 1.3] – [0.227 * 0.63 * 2376]

= 6456 kWh

###### Summer Coincident Peak Demand Savings

kW = kWh / Hours

###### Natural Gas Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-ECON-V06-200101

###### Review Deadline: 1/1/2024

### Night Covers for Open Refrigerated Display Cases

###### Description

This measure is the installation of fitted covers on existing open-type refrigerated and freezer display cases that are deployed during the facility unoccupied hours. Night covers are designed to reduce refrigeration energy consumption by reducing the work done by the compressor. Night covers reduce the heat and moisture entry into the refrigerated space through various heat transfer mechanisms. By fully or partially covering the case opening, night covers reduce the convective heat transfer into the case through reduced air infiltration. Additionally, they provide a measure of insulation, reducing conduction into the case, and also decrease radiation into the case by blocking radiated heat from entering the refrigerated space.

###### Definition of Efficient Equipment

Curtains or covers on top of open refrigerated or freezer display cases that are applied at least six hours (during off-hours) in a 24-hour period.

###### Definition of Baseline Equipment

Refrigerated and freezer, open-type display case in vertical, semi-vertical, and horizontal displays, with no night cover.

###### Deemed Lifetime of Efficient Equipment

The measure life is 5 years, based on DEER 2014.

###### Deemed Measure Cost

The incremental capital cost for this measure is $42 per linear foot of cover installed including material and labor.

###### Loadshape

Loadshape 22: Commercial Refrigeration

###### Coincidence Factor

N/A – savings occur at night only.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

∆kWh 	= ES * L

Where:

ES 		= the energy savings (∆kWh/ft) found in table below:

| Display Case Description | Case Temperature Range (°F) | Annual Electricity Use kWh/ft | ES ∆kWh/ft reduction (= 9% reduction of electricity use,) |
| --- | --- | --- | --- |
| Vertical Open, Remote Condensing, Medium Temperature | 35°F to 55°F | 1453 | 131 |
| Vertical Open, Remote Condensing, Low Temperature | 0°F to 30°F | 3292 | 296 |
| Vertical Open, Self-Contained Medium Temperature | 35°F to 55°F | 2800 | 252 |
| Horizontal Open, Remote Condensing, Medium Temperature | 35°F to 55°F | 439 | 40 |
| Horizontal Open, Remote Condensing, Low Temperature | 0°F to 30°F | 1007 | 91 |
| Horizontal Open, Self-Contained, Medium Temperature | 35°F to 55°F | 1350 | 121 |
| Horizontal Open, Self-Contained, Low Temperature | 0°F to 30°F | 2749 | 247 |

L		= the length of the refrigerated case in linear feet

= Actual

###### Summer Coincident Peak Demand Savings

Peak savings are null because savings occur at night only.

###### Natural Gas Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-NCOV-V01-150601

###### Review Deadline: 1/1/2024

### High Speed Rollup Doors

###### Description

This measure entails the installation of High Speed Doors in refrigerated warehouses. High speed doors can save energy by lowering infiltration through a reduction in time that cooled spaces are exposed to ambient outdoor conditions.  This in turn can lower the demand on refrigeration systems.

This measure was developed to be applicable to the following program types:  RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure the installed equipment must be a High Speed Door installed on the loading dock doorway of a refrigerated space. The high speed door is assumed to act as a primary door. It should be noted that for high-traffic applications (about 45 door passages per hour, using the defaults for this measure) a custom analysis is necessary to ensure that high-speed rollup doors will provide savings, because strip curtains may outperform the high speed door, if no other open-door protection device is installed.

###### Definition of Baseline Equipment

The baseline equipment is existing strip curtains on doorways to a loading dock. During times of traffic, primary doors are left open, leaving just the strip curtains as open-doorway protection.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 16 years.

###### Deemed Measure Cost

The incremental measure cost is $150/sqft.

###### Loadshape

Loadshape C22 - Commercial Refrigeration

###### Coincidence Factor

The coincidence factor is assumed to be 1.00.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Electric savings consider the change in loading on the refrigeration system as well as the consumption of the drive on the high speed door. The following algorithms are based heavily on those derived and described in chapter 24 Refrigerated-Facility Loads of the ASHRAE Refrigeration Handbook.

ΔkWh= 0.00008333* q*Df* η*DtB(1-EB)- DtE(1-EE)-DtMM*t

Where:

0.00008333 	= conversion from Btu/h to tons

q 		= sensible and latent refrigeration load for fully established flow, Btu/h

= 3790*W*H1.5*QsA*1Rs

W 	= width of doorway, in feet. Custom input.

H 	= height of doorway, in feet. Custom input.

QsA 	= Sensible heat load of infiltration air per square foot of door way opening, as read from the following figure and dependent on infiltration air temperature and cooled space temperature. If unknown, infiltration temperature can be assumed to be 50⁰ F, cooler temperature 35⁰F, and freezer temperature -10⁰F, resulting in values of 0.06 for a cooler and 0.5 for a freezer.

Rs	= Sensible heat ratio of the infiltration air heat gain, as read or interpolated from the chart below or from a psychometric chart, dependent on temperature and relative humidity of infiltration air and cooled space temperature. If unknown, use the same assumptions as previously, with a warm space relative humidity value of 70%, resulting in values of 0.685 (interpolated) for coolers and 0.73 (interpolated) for freezers.

Df 	= doorway flow factor. Equal to 0.8 for a doorway between a freezer and a dock and 1.1 for a doorway between a cooler and a dock.

η 	= Efficiency of refrigeration system (kW/ton). Custom input, if unknown assume 1.6 kW/ton for coolers and 2.4 kW/ton for freezers.

DtB 	= decimal portion of time doorway is open in the baseline condition. If during facility operating hours, the primary doors are left open, leaving only open-doorway protective devices (e.g., strip curtains) as a barrier, this is considered 1.0. If primary doors are actively operated and do not remain open for the entire time the facility is in operation, refer to the following calculation.

DtB= (P θpB + 60 θoB)3600 θd

P	=	Number of passages through doorway per hour.

ΘpB	=	Door open to close time in seconds.

ΘoB	=	Time door remains open in minutes.

Θd	=	Period of time considered in hours, 1 hr.

DtE 	= decimal portion of time doorway is open in the efficient condition.

DtE= (P θpE + 60 θoE)3600 θd

P	= Number of passages through doorway per hour. Custom input; assume 5.9 if unknown.

ΘpE	= Door open to close time in seconds. Custom input; assume 7.5 seconds if unknown.

ΘoE	= Time door remains open in minutes. Custom input; assume 3 minutes if unknown.

Θd	= Period of time considered in hours, 1 hr.

DtM 	= decimal portion of time high speed door motor is operational.

DtM= P θpE3600 θd

Variables defined above.

EB 	= effectiveness of baseline open-doorway protective device (strip curtains). Equal to 0.85.

EE 	= effectiveness of efficient open-doorway protective device. Equal to 0, unless an additional protective device exists to limit infiltration during times when the high-speed door is open.

M 	= operating input power of the high speed door motor, in kW.

= Custom input; assume 1.49kW if unknown.

t 	= hours per year when primary doors to the cooled space are open.

= Custom input; assume 2,959 hrs/yr if unknown.

###### Summer Coincident Peak Demand Savings

ΔkW 	= (ΔkWh / t) * CF

Where

CF 	= Summer peak coincidence factor for this measure

=  1.0

All other variables as defined above.

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

Manufacturers suggest annual inspection and maintenance (such as patching tears) of high speed doors. At a minimum, greasing of fittings and oil top-off should be carried out annually. This is estimated at a cost of $150 per year.

###### Measure Code: CI-RFG-HSRD-V03-220101

###### Review Deadline: 1/1/2026

### Q-Sync Motors for Walk-in and Reach-in Coolers/Freezers

###### Description

This measure is applicable to replacement of an existing, uncontrolled, and continuously operating standard-efficiency shaded-pole, permanent split capacitor (PSC),  and electronically commutated (EC) evaporator fan motors in reach-in refrigerated display cases as well as walk-in coolers and freezers.

This measure achieves energy savings by installing a more efficient Q-Sync motor in these scenarios (accompanied with replacement fan assembly as necessary). In addition to motor energy savings, the measure also results in less waste heat for the refrigeration equipment to reject and improves the power factor of the equipment.

This measure is limited to a typical reach-in refrigerated display case with the evaporator fan power of 9-12 Watts and walk-in coolers and freezers with the evaporator fan power of 38-50 Watts. In addition to the motor, replacement of the evaporator fan is necessary to ensure matching airflow is provided (because the fan’s speed has been modified). Care must be taken by the installer to ensure airflows remain within the specified range, otherwise fan performance could suffer, causing reliability issues. Q-Sync motors are commonly purchased as a kit, which includes replacement fan blades and shrouds when replacement is necessary.

This measure was developed to be applicable to the following program types: RF, NC.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The replacement unit must be a 9-12 Watt Q-Sync motor with a minimum of 73% motor efficiency or a 38-50 Watt Q-Sync motor with a minimum of 81% motor efficiency (as listed by manufacturer).

###### Definition of Baseline Equipment

Depending on existing conditions, one of three baselines is chosen:

Baseline 1 is the existing shaded-pole motor(s) with no fan control operating 8760 hours continuously in a refrigerated reach-in display case, walk-in cooler, or walk-in freezer.

Baseline 2 is an EC motor with no fan control operating 8760 hours continuously in a refrigerated reach-in display case.

Baseline 3 is the existing PSC motor(s) with no fan control operating 8760 hours continuously in a walk-in cooler or freezer.

Baseline 4 is a blended baseline, consisting of a mix of shaded-pole motors and EC motors that are assumed to be present in retrofit project where accurate counts are unknown or difficult to determine. It is assumed that existing motors have no fan control and operate 8760 hours continuously in refrigerated reach-in display cases.

###### Deemed Lifetime of Efficient Equipment

The deemed measure life is ten years.

###### Deemed Measure Cost

Actual measure costs should be used if available. If costs are not available, the following deemed measure cost can be used.

| Measure | Material Unit (Each) | Material Cost / Unit | Labor Unit (Hours) | Labor Rate / Unit | Total Cost / Unit |
| --- | --- | --- | --- | --- | --- |
| 9-12-watt Q-Sync motor (including replacement fan kit) | 1 | $52 | 0.25 | $120 | $82 |
| 38-50-watt Q-Sync motor (including replacement fan kit) | 1 | $50 | 0.50 | $120 | $110 |

Note: the material unit cost is based on a large-scale retrofit project.

###### Loadshape

Loadshape C53 - Flat

###### Coincidence Factor

The peak kW coincidence factor is 100%

Algorithm

###### Calculation of Energy Savings

To determine the savings associated with the Q-Sync motor measure we utilized the field study results provided by Oak Ridge National Laboratory (ORNL) and Alternative Energy Systems Consulting (AESC) for refrigerated display cases, and the field study results provided by Slipstream and ORNL for walk-in coolers and freezers.

For refrigerated display cases, in 2015, ORNL conducted a side-by-side comparison of Q-Sync motors with EC motors in a 16 ft medium-temperature vertical multi-deck refrigerated display case at an Hy-Vee Supermarket in the Kansas City metropolitan area. A retrofit was done on the display case that contained four 12 W EC evaporator fan motors, two in each 8 ft section. Two existing EC motors in one of the 8 ft sections were replaced with two 12 W Q-Sync motors. The initial results show that Q-Sync motors consumed approximately 16.4 watts per motor, and EC motors consumed approximately 22.6 watts per motor.

In comparison, the 2011 study by Navigant and PNNL determined that a 12 w shade-pole motor ‘s actual power is 60.0 watts for use in commercial refrigration equipment at design condition, even though some manufacturers also pointed out that “there could be significant variations in efficiency between motors of the same type but different models.” In the AESC study, the field test showed that the average input power for each of the 13 shaded pole motors retrofitted is 41.6 watts. As a compromise between the two studies, we use 50.0 watts as a representative number for shaded pole motors in our calculation. The average evaporator fan motor powers in refrigerated cases are summarized in the following table.

|  | Shaded-pole motor | PSC motor | Q-Sync motor |
| --- | --- | --- | --- |
| Average evaporator fan motor power in refrigerated display cases (watt) | 50.0 | 22.6 | 16.4 |

For walk-in coolers and freezers, in 2019, Slipstream conducted a field study in three small businesses in Illinois retrofitting a total of 18 evaporator fan motors in 7 walk-in coolers or freezers. The average input power for each of the existing 16 shaded-pole motors was 131.6 watts, and 58.4 watts for each of the existing two PSC motors. The average input power for each of the 18 Q-Sync motors post-retrofit was 40.1 watts. In the ORNL 2018 field study on walk-in cooler/freezers in two supermarkets, the average input power for each of the existing 20 shaded-pole fan motors was 111.5 watts, and 61.4 watts for each of the existing 73 PSC motors. The average input power for each of the 93 Q-Sync motors post-retrofit was 36.6 watts. Combining both studies’ results, the average powers for evaporator fan motors pre- and post-retrofit are listed in the following table:

|  | Shaded-pole motor | PSC motor | Q-Sync motor |
| --- | --- | --- | --- |
| Average evaporator fan motor power in walk-in coolers/freezers (watt) | 120.4 | 61.3 | 37.2 |

For refrigerated display cases:

The electrical energy savings for replacing a shaded-pole motor with a Q-Sync motor in a retrofit project is calculated by the difference of the two motors demonstrated power draw multiplied by the annual operating hours. For med-temperature cases, T is 8,760 hours. For low-temp freezer cases, T is 8,578 hours considering daily 30-minute defrost cycles during which fans are not powered.

Motor energy savings (Baseline 1, med-temp, per motor) = (50 w – 16.4 w) x 8760 hours / 1000 = 294.336 kWh

Motor energy savings (Baseline 1, low-temp, per motor) = (50 w – 16.4 w) x 8578 hours /1000 = 288.221 kWh

The electrical energy savings for replacing an EC motor with a Q-Sync motor in a retrofit project is calculated by the difference of the two motors demonstrated power draw multiplied by the annual operating hours (8760 hours):

Motor energy savings (Baseline 2, med-temp, per motor) = (22.6 w – 16.4 w) x 8760 hours / 1000 = 54.312 kWh

Motor energy savings (Baseline 2, low-temp, per motor) = (22.6 w – 16.4 w) x 8578 hours / 1000  = 53.184 kWh

The reduced motor power will also reduce refrigeration load. Assuming the power to drive the evaporator fan is converted to heat inside the display cases at 100% rate, the reduction in refrigeration system compressor power can be calculated using the following equation:

∆kWhrefrigeration= ∆kWhmotorCOP,

where COP is the Coefficient of Performance of refrigeration systems in the supermarket display cases. For med-temperature cases, the average COP is 2.5. For low-temp freezer cases, the average COP is 1.3.

The refrigeration energy savings can be calculated based on above numbers:

Refrigeration energy savings (Baseline 1, med-temp, per motor) = 117.734 kWh

Refrigeration energy savings (Baseline 1, low-temp, per motor) = 221.708 kWh

Refrigeration energy savings (Baseline 2, med-temp, per motor) = 21.724 kWh

Refrigeration energy savings (Baseline 2, low-temp, per motor) = 40.910 kWh

The overall energy savings are the sums of the motor energy savings and the refrigeration energy savings:

Overall energy savings (Baseline 1, med-temp, per motor) = 412.070 kWh

Overall energy savings (Baseline 1, low-temp, per motor) = 509.929 kWh

Overall energy savings (Baseline 2, med-temp, per motor) = 76.036 kWh

Overall energy savings (Baseline 2, low-temp, per motor) = 94.094 kWh

For walk-in coolers and freezers:

The electrical energy savings for replacing a shaded-pole motor with a Q-Sync motor in a retrofit project is calculated by the difference of the two motors demonstrated power draw multiplied by the annual operating hours. For coolers, T is 8,760 hours. For freezers, T is 8,578 hours considering daily 30-minute defrost cycles during which fans are not powered.

Motor energy savings (Baseline 1, med-temp, per motor) = (120.4 w – 37.2 w) x 8760 hours / 1000 = 728.832 kWh

Motor energy savings (Baseline 1, low-temp, per motor) = (120.4 w – 37.2 w) x 8578 hours /1000 = 713.690 kWh

The electrical energy savings for replacing a PSC motor with a Q-Sync motor in a retrofit project is calculated by the difference of the two motors demonstrated power draw multiplied by the annual operating hours (8760 hours):

Motor energy savings (Baseline 3, med-temp, per motor) = (61.3 w – 37.2 w) x 8760 hours / 1000 = 211.116 kWh

Motor energy savings (Baseline 3, low-temp, per motor) = (61.3 w – 37.2 w) x 8578 hours / 1000  = 206.730 kWh

The reduced motor power will also reduce refrigeration load. Assuming the power to drive the evaporator fan is converted to heat inside the display cases at 100% rate, the reduction in refrigeration system compressor power can be calculated using the following equation:

∆kWhrefrigeration= ∆kWhmotorCOP,

where COP is the Coefficient of Performance of refrigeration systems in the supermarket display cases. For med-temperature cases, the average COP is 2.5. For low-temp freezer cases, the average COP is 1.3.

The refrigeration energy savings can be calculated based on above numbers:

Refrigeration energy savings (Baseline 1, med-temp, per motor) = 291.532 kWh

Refrigeration energy savings (Baseline 1, low-temp, per motor) = 548.992 kWh

Refrigeration energy savings (Baseline 3, med-temp, per motor) = 84.446 kWh

Refrigeration energy savings (Baseline 3, low-temp, per motor) = 159.023 kWh

The overall energy savings are the sums of the motor energy savings and the refrigeration energy savings:

Overall energy savings (Baseline 1, med-temp, per motor) = 1020.364 kWh

Overall energy savings (Baseline 1, low-temp, per motor) = 1262.682 kWh

Overall energy savings (Baseline 3, med-temp, per motor) = 295.562 kWh

Overall energy savings (Baseline 3, low-temp, per motor) = 365.753 kWh

###### Electric Energy Savings

If the numbers of existing shaded-pole motors, EC motors to be retrofitted are known (Baseline 1,2, & 3):

ΔkWh = Overall annual savings per motor * Motors

Where overall energy savings per motor can is as speficied in the following table:

| Evaporator Fan Motor Rating (of Q-Sync motor) | Baseline | Annual kWh Savings/motor |
| --- | --- | --- |
| 9-12W | shaded-pole motor, med-temp | 412.1 |
| 9-12W | shaded-pole motor, low-temp | 509.9 |
| 9-12W | EC motor, med-temp | 76.0 |
| 9-12W | EC motor, low-temp | 94.1 |
| 38-50W | shaded-pole motor, med-temp | 1020.364 |
| 38-50W | shaded-pole motor, low-temp | 1262.682 |
| 38-50W | PSC motor, med-temp | 295.562 |
| 38-50W | PSC motor, low-temp | 365.753 |

Motors		= number of fan motors replaced

For refrigerated display cases, if the numbers of existing shaded-pole motors and EC motors are unknown in a retrofit project (Baseline 3):

ΔkWh = [Wmed-temp (WSPM x SSPM-med + WECM x SECM-med) + Wlow-temp (WSPM x SSPM-low +  WECM x SECM-low )] * Motors

Motors		= number of fan motors replaced

S 	= annual energy savings per motor, by type. Savings for each different type (SSPM-med, SSPM-low, SECM-med, SECM-low) can be looked up from the table above.

W 	= weighting factors. The weights for the medium-temperature and low-temperature applications (Wmed-temp and Wlow-temp) should be calculated based on the actural numbers of motors in a retrofit project, and the sum of the two weights should equal to 1. If these weights cannot be accurately obtained, the estimated weights (Wmed-temp* and Wlow-temp*) from the table below can be used (the WSPM and WECM numbers are slightly adjusted by +/-5% based on national averages in the 2015 ORNL study, reflecting some shaded pole motors may have been replaced with EC motors in the past few years).

| Application | WSPM | WECM | Wmed-temp* | Wlow-temp* |
| --- | --- | --- | --- | --- |
| Supermarkets | 0.6 | 0.4 | 0.68 | 0.32 |
| Other Food Retail Formats | 0.8 | 0.2 | 0.68 | 0.32 |
| Other Retail Categories | 0.7 | 0.3 | 0.68 | 0.32 |
| Restaurants and Bars | 0.85 | 0.15 | 0.68 | 0.32 |
| Beverage Vending Machines | 0.85 | 0.15 | 0.68 | 0.32 |

For walk-in coolers and freezers, if the existing motor types are unknown in a retrofit project, it can be assumed they are PSC motors, as from industry survey in the 2018 ORNL study, 95% of the 38-50 watt evaporator fan motors are PSC motors.

###### Summer Coincident Peak Demand Savings

ΔkW = ΔkWh / Hours * CF

Where:

ΔkWh	= Gross customer annual kWh savings for the measure, as listed above

Hours	= Full Load hours per year

= 8,766 (med-temp); 8,578 (low-temp)

CF	= Summer Peak Coincident Factor

= 1.0

Other variables as defined above.

The following table provides the resulting kW savings (per motor):

| Evaporator Fan Motor Rating (of Q-Sync motor) | Baseline | kW Savings/motor |
| --- | --- | --- |
| 9-12W | shaded-pole motor, med-temp | 0.047 |
| 9-12W | shaded-pole motor, low-temp | 0.059 |
| 9-12W | EC motor, med-temp | 0.009 |
| 9-12W | EC motor, low-temp | 0.011 |
| 38-50W | shaded-pole motor, med-temp | 0.116 |
| 38-50W | shaded-pole motor, low-temp | 0.147 |
| 38-50W | PSC motor, med-temp | 0.034 |
| 38-50W | PSC motor, low-temp | 0.043 |

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

There is no O&M cost adjustment for replacing shaded pole or EC motors with Q-Sync motors in reach-in refrigerated display case applications. From the 2015 ORNL study, the 2016 AESC study, and the manufacturer, there is no expected degradation in equipment performance after the retrofits, and therefore no O&M cost differences are expected between baseline and efficient measures.

###### Measure Code: CI-RFG-QMF-V03-220101

###### Review Deadline: 1/1/2026

### Variable Speed Drive for Condenser Fans

###### Description

This measure is applicable to VFDs installed on condenser fan motors operating in supermarket refrigeration systems.

Where a baseline condenser motor load operates at a fixed-speed, VFDs generate energy and cost savings by modulating frequency and voltage to match the load on the condensers. Savings result from the resulting fan speed variation.

This measure is applicable to motors between 0.5 horsepower and 1.5 horsepower.

This measure was developed to be applicable to the following program types: RF, TOS.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

This measure applies to retrofitted installation of condenser fan motors in supermarkets where no ability to modulate frequency and voltage for fan-speed variation exits. Savings are based on the application of VFDs to baseline load conditions defined as pre-installation load compared to post-installation load.

###### Definition of Baseline Equipment

The time-of-sale baseline is a new motor installed without a VFD or other methods of control. Retrofit baseline is an existing motor operating as is.

###### Deemed Lifetime of Efficient Equipment

The expected measure life for VFD condenser fan applications is 15 years.

###### Deemed Measure Cost

Customer costs will be used when available. For motor sizes 0.5 to 1.5 HP the default measure cost is $1,170/HP. Custom costs must be gathered for other motor sizes.

###### Loadshape

C22-commercial refrigeration.

###### Coincidence Factor

The demand savings factor (DSF) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Energy Savings

Energy savings is based on a pre- and post-treatment test. The pre-treatment period being nearly three months in duration with post-treatment of a similar period. Both periods include significant average outdoor temperature (OAT) changes. Measurement of energy savings relies on regression of condenser fan energy use against ambient temperature. These estimates were made on each condenser using both pre- and post-VFD installation; comparison of the two yields savings.

###### Electric Energy Savings

Annual ΔkWhcondenser = No. fans * HP/fan * kWh savings/HP/Zone

| # Zone | kWh savings/HP |
| --- | --- |
| 1 (Rockford) | 1,480 |
| 2 (Chicago) | 1,500 |
| 3 (Springfield) | 1,430 |
| 4 (Belleville) | 1,430 |
| 5 (Marion) | 1,480 |

For example, for a condenser with 5 fans, each rated at 1.5 HP in Chicago (Zone 2):

Annual ΔkWhcondenser = 5  * 1.5 * 1,500

= 11,250 kWh

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

Variable frequency drives, anecdotally, increase motor life because they allow for soft-start and soft shutdown. This would lead to O&M savings from replacing motors. Unfortunately, there is currently insufficient evidence to quantify this savings, so no deemed O&M savings can be claimed at this time.

###### Measure Code: CI-RFG-VSC-V02-200101

###### Review Deadline: 1/1/2025

### Add Doors to Open Refrigerated Display Cases

###### Description

Open display cases are typically found in grocery and convenience stores and have been a preference of store owners because they allow customers a clear view and easy access to refrigerated products. This measure is retrofitting existing, open, refrigerated display cases by adding and installing doors. The baseline equipment is an open vertical or horizontal display case with no doors or covering. The efficient equipment is the installation of solid doors on the existing display case. Replacement of open display cases with new display cases with doors is not covered under this measure characterization.

Energy savings are based on air infiltration reduction from the addition of doors to the open display cases. The air infiltration reductions assume a reduced heat gain and subsequent reduced load on the refrigeration compressors. Both radiant and conduction heat losses were factored into the analysis as well. Energy savings are based on a per linear foot of display case.

Interactive HVAC energy savings were also included in the measure savings analysis. The HVAC interactive effects calculation assesses the measure's impact on the heating and cooling equipment. With adding a door to an open refrigerated display case, excess cold air leaking into the conditioned space no longer has to be treated by the heating system, resulting in additive savings. Similarly, the reduction in cold air from the open refrigerated display case no longer supplements the efforts of the space cooling equipment, which results in an overall increase in its consumption.

High, medium, and low temperature cases are eligible for this measure; however, the measure assumptions detailed in this characterization are based on medium temperature display cases, with the installation of zero energy doors, as it was deemed the most likely candidate for participation in this measure. Open low temperature or freezer display cases are not common. If the retrofitted door has LED fixtures, it is recommended to leverage ‘4.5.4 LED Bulbs and Fixtures’ for quantifying savings and measure benefits.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient condition is retrofitting an existing open, refrigerated, display case by adding doors.

###### Definition of Baseline Equipment

The baseline condition is an open, refrigerated, display case without any covering.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is 15 years.

###### Deemed Measure Cost

The incremental cost, which includes both material and labor, differs depending on whether or not the installed door is equipped with LED lighting. The estimated incremental cost for doors without LED lighting is $390 per linear foot. The incremental cost for doors with LED lighting is $419 per linear foot.

###### Loadshape

Loadshape C03 - Commercial Cooling

Loadshape 22: Commercial Refrigeration

###### Coincidence Factor

There are two components to the demand savings of this measure, one that impacts the refrigeration equipment itself, and another that has an interactive impact on the space cooling equipment. As a result, the measure details two summer coincidence peak demand factors.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

∆kWh=(ΔHG*CL/ (EER*1000) *8760)+(MMBtuHVAC Cool *CL *(1 / SEER) *1000)- kWhNight Covers - kWhAdded Lights

Where:

∆kWh		= gross customer annual kWh savings

∆HG	= Heat Gain, the decreased load or the reduced heat gain on the open refrigerated display case with the installation of a door (Btu/hr-linear foot)

= 1,172 Btu/h-ft for vertical cases or 202.3 Btu/h-ft for horizontal cases.

CL		= Case Length, refrigerated case length in feet

= Actual

EER		= Energy Efficiency Ratio; display case compressor efficiency (Btu/hr-watt)

= 11.36

1000		= Conversion from watts to kilowatts (W / kW)

8760		= Annual operating hours of the refrigerated display case

MMBtuHVAC Cool	= Total cooling load increase on the HVAC equipment per linear foot of display case. Varies by location:

| Zone | MMBtuHVAC Cool Vertical | MMBtuHVAC Cool Horizontal |
| --- | --- | --- |
| 1 (Rockford) | -2.632 | -0.454 |
| 2 (Chicago) | -2.763 | -0.477 |
| 3 (Springfield) | -3.284 | -0.567 |
| 4 (Belleville) | -3.254 | -0.562 |
| 5 (Marion) | -3.335 | -0.576 |

SEER		= Seasonal Energy Efficiency Ratio; HVAC equipment operating efficiency (Btu/hr-watt)

= 13.00

kWhNight Covers	= Reduction in energy savings if existing display case utilizes night covers (kWh/linear-ft)

= 0 if no night covers are deployed. See table below if display case uses night covers.

| Display Case Description | Case Temperature Range (°F) | ∆kWh/ft reduction (= 9% reduction of electricity use,) |
| --- | --- | --- |
| Vertical Open, Remote Condensing, Medium Temperature | 35°F to 55°F | 131 |
| Vertical Open, Remote Condensing, Low Temperature | 0°F to 30°F | 296 |
| Vertical Open, Self-Contained Medium Temperature | 35°F to 55°F | 252 |

kWhAdded Lights	= Reduction in energy savings if new lighting is added to the case (kWh/linear-ft)

= 0 if no lighting is added, or if lighting is added but existing lighting is removed. If lighting is retrofit, determine case lighting savings using ‘4.5.4 LED Bulbs and Fixtures’.

= Actual installed equipment specifications or use case lighting values from ‘4.5.4 LED Bulbs and Fixtures'.

For example, a grocery store in Chicago installed zero energy doors on four open refrigerated cases that do not use night covers, which amounted to 12 linear feet of retrofitted display cases, savings the site:

ΔkWh 	= ((1172 * 12) / (11.36 * 1000) * 8760) + (-2.763 * 12 * (1 / 13) * 1000)

= 8,295 kWh

###### Summer Coincident Peak Demand Savings

∆kW=((ΔHG*CL / (EER*1000)-kWAdded Lights)*CFRefrigeration)+((MMBtuHVAC Cool / HoursCool *CL *(1 / SEER) *1000)*CFCool)

Where:

HoursCool 	= Total combined hours the site is providing cooling. Varies by location:

| Zone | Hours Cool |
| --- | --- |
| 1 (Rockford) | 2,994 |
| 2 (Chicago) | 3,143 |
| 3 (Springfield) | 3,736 |
| 4 (Belleville) | 3,702 |
| 5 (Marion) | 3,794 |

kWAdded Lights	= Reduction in demand savings if new lighting is added to the case (kW/linear-ft)

= 0 if no lighting is added, or if lighting is added but existing lighting is removed. If lighting is retrofit, determine case lighting savings using ‘4.5.4 LED Bulbs and Fixtures’.

= Actual installed equipment specifications or use case lighting values from ‘4.5.4 LED Bulbs and Fixtures'.

CFRefrigeration	= Summer peak coincidence factor for the refrigerated display case

= 0.964

CFCool	= Summer peak coincidence factor for the HVAC cooling system. This is the summer system peak coincidence factor for commercial dooling (during system peak hours)

= 0.913

###### Natural Gas Savings

ΔTherms= (MMBtuHVAC Heat*CL*(1 / AFUE) *10

Where:

∆Therms	= gross customer annual therms savings

MMBtuHVAC Heat	= Total heating load decrease on the HVAC equipment per linear foot of display case. Varies by locations:

| Zone | MMBtuHVAC Heat Vertical | MMBtuHVAC Heat Horizontal |
| --- | --- | --- |
| 1 (Rockford) | 5.068 | 0.875 |
| 2 (Chicago) | 4.937 | 0.852 |
| 3 (Springfield) | 4.416 | 0.762 |
| 4 (Belleville) | 4.446 | 0.767 |
| 5 (Marion) | 4.365 | 0.753 |

CL		= Case Length, refrigerated case length in feet

= Actual

AFUE		= 80%

10		= Conversion from MMBtu to therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-DOOR-V02-220101

###### Review Deadline: 1/1/2025

### Floating Head Pressure Control

###### Description

Installers conventionally design a refrigeration system to condense at a set pressure-temperature setpoint, typically 90 degrees. By installing a “floating head pressure control” condenser system, the refrigeration system can change condensing temperatures in response to different outdoor temperatures. This means that as the outdoor temperature drops, the compressor will not have to work as hard to reject heat from the cooler or freezer. This measure is for the application of floating head pressure controls for compressors ≤ 10HP and a condensing temperature set to 70ºF. This measure is strictly limited to single compressor systems.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified. IECC code requires economizers in certain instances and therefore projects relying on code baseline definitions must verify eligibility.

###### Definition of Efficient Equipment

High efficiency is a refrigeration system with floating head pressure control.

###### Definition of Baseline Equipment

The baseline is a refrigeration system without floating head pressure control.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is 15 years.

###### Deemed Measure Cost

Floating Head Pressure Control Costs, per Horsepower (condenser rating) are as follows ($/HP):

| Unit Type | Low Temperature (Freezer) | Medium Temperature (Refrigerator) | Unknown Temperature |
| --- | --- | --- | --- |
| Self- Contained Unit | $411.87 | $449.79 | $430.83 |
| Remote Condensing Unit | $411.87 | $449.79 | $430.83 |
| Unknown | $411.87 | $449.79 | $430.83 |

###### Loadshape

Loadshape C22 - Commercial Refrigeration

###### Coincidence Factor

###### The summer peak coincidence factor for this measure is assumed to be 0%, based on the fact that savings for this measure will occur during periods of coldest outdoor temperatures.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh 	= HP * kWhHP

Where:

HP 		= Horsepower of Compressor

= actual installed

kWhHP	 = Savings factor, kWh per horsepower of compressor rating. Per the tables below based on weather zone, condensing unit type, and temperature range:

Note: Self-contained condensing units assume heat is rejected to conditioned or semi-conditioned space. Therefore, outdoor air temperature is not considered a critical system variable resulting in identical savings across weather zones that are much lower compared to those realized by remove condensing units that reject heat to the outdoor environment.

Zone 1 (Rockford)

| Unit Type | Low Temperature (Freezer) | Medium Temperature (Refrigerator) | Unknown Temperature |
| --- | --- | --- | --- |
| Self- Contained Unit | 252 | 131 | 170 |
| Remote Condensing Unit | 482 | 451 | 461 |
| Unknown | 367 | 291 | 315 |

Zone 2 (Chicago)

| Unit Type | Low Temperature (Freezer) | Medium Temperature (Refrigerator) | Unknown Temperature |
| --- | --- | --- | --- |
| Self- Contained Unit | 252 | 131 | 170 |
| Remote Condensing Unit | 465 | 435 | 445 |
| Unknown | 358 | 283 | 307 |

Zone 3 (Springfield)

| Unit Type | Low Temperature (Freezer) | Medium Temperature (Refrigerator) | Unknown Temperature |
| --- | --- | --- | --- |
| Self- Contained Unit | 252 | 131 | 170 |
| Remote Condensing Unit | 403 | 377 | 385 |
| Unknown | 327 | 254 | 278 |

Zone 4 (Belleville)

| Unit Type | Low Temperature (Freezer) | Medium Temperature (Refrigerator) | Unknown Temperature |
| --- | --- | --- | --- |
| Self- Contained Unit | 252 | 131 | 170 |
| Remote Condensing Unit | 321 | 301 | 307 |
| Unknown | 287 | 216 | 239 |

Zone 5 (Marion)

| Unit Type | Low Temperature (Freezer) | Medium Temperature (Refrigerator) | Unknown Temperature |
| --- | --- | --- | --- |
| Self- Contained Unit | 252 | 131 | 170 |
| Remote Condensing Unit | 328 | 307 | 314 |
| Unknown | 290 | 219 | 242 |

For example, a low temperature remote condensing unit in Chicago (Zone 2) with a 3-horsepower condenser would annually save:

ΔkWh 	 = 3 * 465

= 1,395 kWh

###### Summer Coincident Peak Demand Savings

There are no expected summer coincident peak demand savings for this measure.

###### Fossil Fuel Impact Descriptions and Calculations

There are no expected fossil fuel gas savings for this measure.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-FHP-V01-220101

###### Review Deadline: 1/1/2026

## Compressed Air

### VSD Air Compressor

###### Description

This measure relates to the installation of an air compressor with a variable frequency drive, load/no load controls or variable displacement control.  Baseline compressors choke off the inlet air to modulate the compressor output, which is not efficient. Efficient compressors use a variable speed drive on the motor to match output to the load. Savings are calculated using representative baseline and efficient demand numbers for compressor capacities according to the facility’s load shape, and the number of hours the compressor runs at that capacity. Demand curves are as per DOE data for a Variable Speed compressor versus a Modulating compressor. This measure applies only to an individual compressor ≤ 200 hp. Only one compressor per compressed air distribution system is eligible.

This measure was developed to be applicable to the following program types: TOS.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The high efficiency equipment is a compressor ≤ 200 hp with variable speed control.

###### Definition of Baseline Equipment

The baseline equipment is either an oil-flooded compressor ≤ 200 hp with inlet modulating with blowdown or load/no-load controls.

###### Deemed Lifetime of Efficient Equipment

13 years

###### Deemed Measure Cost

IncrementalCost ($) = ((127 x hpcompressor) + 1,446) x 1.24

Where:

127 and 1,446	= compressor motor nominal hp to incremental cost conversion factor and offset

hpcompressor	= compressor motor nominal

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

Loadshape C35 - Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

kWh = 0.9 x hpcompressor x HOURS x (CFb – CFe)

Where:

kWh		= gross customer annual kWh savings for the measure

hpcompressor	= compressor motor nominal hp

0.9		= compressor motor nominal hp to full load kW conversion factor

HOURS		= compressor total hours of operation below depending on shift

| Shift | Hours |
| --- | --- |
| Single shift (8/5) | 1,976 hours 7 AM – 3 PM, weekdays, minus some holidays and scheduled down time |
| 2-shift (16/5) | 3,952 hours 7AM – 11 PM, weekdays, minus some holidays and scheduled down time |
| 3-shift (24/5) | 5,928 hours 24 hours per day, weekdays, minus some holidays and scheduled down time |
| 4-shift (24/7) | 8,320 hours 24 hours per day, 7 days a week minus some holidays and scheduled down time |
| Unknown / Weighted average | 5,702 hours |

CFb		= baseline compressor factor

| Baseline Compressor | Compressor Factor (≤ 40 hp) | Compressor Factor (50 – 200 hp) |
| --- | --- | --- |
| Modulating w/ Blowdown | 0.890 | 0.863 |
| Load/No Load w/ 1 Gallon/CFM | 0.909 | 0.887 |
| Load/No Load w/ 3 Gallon/CFM | 0.831 | 0.811 |
| Load/No Load w/ 5 Gallon/CFM | 0.806 | 0.786 |

CFe		= efficient compressor

=0.705 for units ≤ 40 hp

= 0.658 for units 50 – 200 hp

For example, a VSD compressor with 10 HP operating in a 1-shift facility would save

kWh 		= 0.9 x 10 x 1,976 x (0.890 – 0.705)

= 3,290 kWh

###### Summer Coincident Peak Demand Savings

kW 		= kWh / HOURS * CF

Where:

CF	= Summer peak coincidence factor for this measure

| Shift | Coincidence Factor |
| --- | --- |
| Single shift (8/5) | 0.59 |
| 2-shift (16/5) | 0.95 |
| 3-shift (24/5) | 0.95 |
| 4-shift (24/7) | 0.95 |
| Unknown / Weighted average | 0.89 |

For example, a VSD compressor with 10 HP operating in a 1 shift facility would save

kW 		= 3,290/1,976*0.59

= 0.98 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-CPA-VSDA-V04-220101

###### Review Deadline: 1/1/2027

### Compressed Air Low Pressure Drop Filters

###### Description

Low pressure drop filters remove solids and aerosols from compressed air systems with a longer life and lower pressure drop than standard coalescing filters, resulting in the ability to lower a compressed air systems pressure setpoints. This reduces the compressor work required resulting in energy savings.

This measure was developed to be applicable to the following program types: RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient condition is a low pressure drop filter with pressure drop not exceeding 1 psid when new and 3 psid at element change.

###### Definition of Baseline Equipment

The baseline condition is a standard coalescing filter with a pressure drop of 3 psid when new and 5 psid or more at element change

###### Deemed Lifetime of Efficient Equipment

10 years

###### Deemed Measure Cost

The incremental cost for this measure is estimated to be $1,000 Incremental cost per filter.

###### Loadshape

Loadshape C35 - Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

∆kWh		= (kWtypical  x ∆P x SF  x Hours / HPtypical) x HPreal

Where:

kWtypical 	= Adjusted compressor power (kW) based on typical compressor loading and operating profile. Use actual compressor control type if known:

| Compressor kWtypical |  |
| --- | --- |
| Control Type | kWtypical |
| Reciprocating - On/off Control | 70.2 |
| Reciprocating - Load/Unload | 74.8 |
| Screw - Load/Unload | 82.3 |
| Screw - Inlet Modulation | 82.5 |
| Screw - Inlet Modulation w/ Unloading | 82.5 |
| Screw - Variable Displacement | 73.2 |
| Screw - VFD | 70.8 |

= If the actual compressor control type is not known, use a weighted average based on the following market assumptions:

| Control Type | Share % | kWtypical |
| --- | --- | --- |
| Market share estimation for load/unload control compressors | 40% | 74.8 |
| Market share estimation for modulation w/unloading control compressors | 40% | 82.5 |
| Market share estimation for variable displacement control compressors | 20% | 73.2 |
| Weighted Average |  | 77.6 |

∆P 		= Reduction in pressure differential across the filter (psi)

=2 psi

SF	=1% reduction in power per 2 psi reduction in system pressure is equal to 0.5% reduction per 1 psi, or a Savings Factor of 0.005

Hours		= Compressor hours of operation below depending on shift

| Shift | Hours |
| --- | --- |
| Single shift (8/5) | 1,976 hours 7 AM – 3 PM, weekdays, minus three-weekday holidays and 10 days of scheduled down time |
| 2-shift (16/5) | 3,952 hours 7AM – 11 PM, weekdays, minus three-weekday holidays and 10 days of scheduled down time |
| 3-shift (24/5) | 5,928 hours 24 hours per day, weekdays, minus three-weekday holidays and 10 days of scheduled down time |
| 4-shift (24/7) | 8,320 hours 24 hours per day, 7 days a week minus three-week day holidays and 10 days of scheduled down time |
| Unknown / Weighted average | 5,702 |

HPtypical 		= Nominal HP for typical compressor = 100 hp

HPreal 	= Total HP of real compressors distibuting air through filter. This should include the total horsepower of the compressors that normally run through the filter, but not backup compressors.

###### Summer Coincident Peak Demand Savings

kW = kWh / Hours * CF

Where:

CF		= Summer peak coincidence factor for this measure

| Shift | Coincidence Factor |
| --- | --- |
| Single shift (8/5) | 0.59 |
| 2-shift (16/5) | 0.95 |
| 3-shift (24/5) | 0.95 |
| 4-shift (24/7) | 0.95 |
| Unknown / Weighted average | 0.89 |

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-CPA-LPDF-V04-220101

###### Review Deadline: 1/1/2027

### Compressed Air No-Loss Condensate Drains

###### Description

No-loss condensate drains remove condensate as needed without venting compressed air, resulting in less air demand and consequently better efficiency. Replacement or upgrades of existing no-loss drains are not eligible for the incentive.

This measure was developed to be applicable to the following program types: RF.  If applied to other program types, the measure savings should be verified

###### Definition of Efficient Equipment

The efficient condition is installation of no-loss condensate drains.

###### Definition of Baseline Equipment

The baseline condition is installation of standard condensate drains (open valve, timer, or both)

###### Deemed Lifetime of Efficient Equipment

10 years

###### Deemed Measure Cost

The average equipment cost per drain is $194 with an installation labor cost of $50 for a total incremental cost $244  per drain.

###### Loadshape

Loadshape C35 - Industrial Process

###### Coincidence Factor

The coincidence factor equals 0.95.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

∆kWh 	= CFMreduced x kWCFM x Hours

Where:

CFMreduced 	= Reduced air consumption (CFM) per drain

= 3 CFM

kWCFM	= System power reduction per reduced air demand (kW/CFM) depending on the type of compressor control:

System Power Reduction per Reduced Air Demand

| Control Type | kW / CFM |
| --- | --- |
| Reciprocating - On/off Control | 0.184 |
| Reciprocating - Load/Unload | 0.136 |
| Screw - Load/Unload | 0.152 |
| Screw - Inlet Modulation | 0.055 |
| Screw - Inlet Modulation w/ Unloading | 0.055 |
| Screw - Variable Displacement | 0.153 |
| Screw - VFD | 0.178 |

Or if compressor control type is unknown, then a weighted average based on market share can be used:

| Control Type | Share % | kW / CFM |
| --- | --- | --- |
| Market share estimation for load/unload control compressors | 40% | 0.136 |
| Market share estimation for modulation w/unloading control compressors | 40% | 0.055 |
| Market share estimation for variable displacement control compressors | 20% | 0.153 |
| Weighted Average |  | 0.107 |

Hours 		= Compressed air system pressurized hours

=6136 hours

###### Summer Coincident Peak Demand Savings

kW 		= kWh / HOURS * CF

Where:

CF		= Summer peak coincidence factor for this measure

= 0.95

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-CPA-NCLD-V03-200101

###### Review Deadline: 1/1/2025

### Efficient Compressed Air Nozzles

###### Description

This measure is for the replacement of standard air nozzle with high-efficiency air nozzle used in a compressed air system. High-efficiency air nozzles reduce the amount of air required to blow off parts or for drying. These nozzles utilize the Coandă effect to pull in free air to accomplish tasks with significantly less compressed air. High-efficiency nozzles often replace simple copper tubes. These nozzles have the added benefits of noise reduction and improved safety in systems with greater than 30 psig.

###### Definition of Efficient Equipment

The high-efficiency air nozzle must meet the following specifications:

- High-efficiency air nozzle must replace continuous open blow-offs

- High-efficiency air nozzle must meet SCFM rating at 80psig less than or equal to: 1/8” 11 SCFM, 1/4" 29 SCFM, 5/16” 56 SCFM, 1/2" 140 SCFM.

- Manufacturer’s specification sheet of the high-efficiency air nozzle must be provided along with the make and model

###### Definition of Baseline Equipment

The baseline condition is a standard air nozzle.

###### Deemed Lifetime of Efficient Equipment

The measure life is 15 years.

###### Deemed Measure Cost

The estimated incremental measure costs are presented in the following table:

| Nozzle Diameter | 1/8” | 1/4" | 5/16” | 1/2" |
| --- | --- | --- | --- | --- |
| Average IMC | $42 | $57 | $87 | $121 |

###### Loadshape

Loadshape C35 - Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = (SCFM * SCFM%Reduced) * kW/CFM * %USE * Hours

Where:

SCFM 	= Air flow through standard nozzle. Use actual rated flow at 80 psi if known. If unknown, the table below includes the CFM by orifice diameter.,

| Orifice Diameter | SCFM |
| --- | --- |
| 1/8” | 21 |
| 1/4” | 58 |
| 5/16” | 113 |
| 1/2" | 280 |

SCFM%Reduced 	= Percent in reduction of air loss per nozzle. Estimated at 50%.

kW/CFM 	= System power reduction per air demand (kW/CFM) depending on the type of air compressor found in table below:

| Air Compressor Type | kW/CFM |
| --- | --- |
| Reciprocating – On/off Control | 0.18 |
| Reciprocating – Load/Unload | 0.14 |
| Screw – Load/Unload | 0.15 |
| Screw – Inlet Modulation | 0.06 |
| Screw – Inlet Modulation w/ Unloading | 0.06 |
| Screw – Variable Displacement | 0.15 |
| Screw - VFD | 0.18 |

%USE                    = Percent of the compressor total operating hours that the nozzle is in use

= Custom; if unknown assume 5%

Hours 	= Compressed air system pressurized hours.

= Use actual hours if known, otherwise assume values in table below:

| Shift | Hours |
| --- | --- |
| Single Shift | 1,976 |
| Two Shifts | 3,952 |
| Three Shifts | 5,928 |
| Four Shifts or Continual Operation | 8,320 |
| Unknown / Weighted average | 5,702 |

###### Summer Coincident Peak Demand Savings

ΔkW = ΔkWh/Hours * CF

Where:

ΔkWh		= As calculated above

CF		= Summer peak coincidence factor

| Shift | Coincidence Factor |
| --- | --- |
| Single Shift | 0.59 |
| Two Shifts | 0.95 |
| Three Shifts | 0.95 |
| Four Shifts or Continual Operation | 0.95 |
| Unknown / Weighted average | 0.89 |

###### Natural Gas Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code CI-CPA-CNOZ-V02-190101

###### Review Deadline: 1/1/2023

### Efficient Refrigerated Compressed Air Dryer

###### Description

An air dryer is an essential component in a compressed air system that prevents condensate from being deposited in the compressed air supply lines of a facility.  If warm saturated compressed air is supplied directly to the plant, excess condensate will form in the compressed air supply lines.  Uncontrolled condensate can damage demand-side tools and process equipment. Secondly, in an oil-flooded rotary screw compressor, the residual oil from compression can be carried along the supply lines potentially damaging process equipment.  Industries that use compressed air for processes make use of various types of dryers including refrigerated dryers (both cycling and non-cycling). For this measure, three types of refrigerated air dryers will be considered: thermal mass, variable speed and digital scroll. All these technologies offer better part load performance compared to non-cycling refrigerated dryers, thereby offering energy savings during periods when the dryer is not operating at peak capacity.

This measure was developed to be applicable to the following program types: TOS.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

A new, high efficiency thermal mass dryer, variable speed dryer, or digital scroll dryer.

###### Definition of Baseline Equipment

A standard non-cycling refrigerated compressed air dryer of comparable capacity.

###### Deemed Lifetime of Efficient Equipment

The measure life is 13 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is $6 per CFM.

###### Loadshape

Loadshape C35 – Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

kWh = Ps x (EC50baseline - EC50efficient) x HOURS x CFM

Where:

Ps	 	= Full flow specific power of the dryer

= 0.007 kW/CFM (for both baseline and efficient equipment)

EC50baseline 	= Energy consumption ratio of baseline dryer at 50% inlet load capacity as compared to fully loaded operating conditions.

= 0.843

ECF50efficient 	= Energy consumption ratio of efficient dryer at 50% inlet load capacity as compared to fully loaded operating conditions.

= Dependent on efficient dryer type, refer to the following table:

| Dryer Type | EC50efficient |
| --- | --- |
| Thermal-Mass | 0.729 |
| VSD | 0.501 |
| Digital Scroll | 0.551 |

HOURS	= Compressed air system pressurized hours, depending on shift. If unknown, use weighted average. This value is the weighted average of facility owner responses from the DOE evaluation of the Compressed Air Challenge. Facility owners with compressed air systems were surveyed detailing the number of shifts their facilities operated.

| Shift | Hours | Distribution of Facilities by Hours of Operation | Weighted Hours |
| --- | --- | --- | --- |
| Single Shift 7 AM – 3 PM, weekdays, minus some holidays and scheduled down time | 1,976 | 16% | 316 |
| Two Shifts 7AM – 11 PM, weekdays, minus some holidays and scheduled down time | 3,952 | 23% | 909 |
| Three Shifts 24 hours per day, weekdays, minus some holidays and scheduled down time | 5,928 | 25% | 1,482 |
| Four Shifts or Continual Operation 24 hours per day, 7 days a week minus some holidays and scheduled down time | 8,320 | 36% | 2,995 |
|  |  | Total weighted average | 5,702 |

CFM		= Cubic feet per minute, rated capacity of refrigerated dryer

= Assume 100% of actual rated capacity.

###### Summer Coincident Peak Demand Savings

kW 	= kWh / HOURS * CF

Where:

CF		= Summer peak coincidence factor, depending on shift. If unknown, use weighted   				average.

| Shift | Coincidence Factor |
| --- | --- |
| Single Shift | 0.59 |
| Two Shifts | 0.95 |
| Three Shifts | 0.95 |
| Four Shifts or Continual Operation | 0.95 |
| Unknown / Weighted average | 0.89 |

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-CPA-CADR-V02-190101

###### Review Deadline: 1/1/2024

### Vortex Tube Thermostat - Provisional Measure

###### Description

Cabinets that house programmable controllers, relays, motor controls, or other electrical components can generate significant amounts of heat. Removing heat from these cabinets is necessary to ensure the operation and longevity of the electrical components inside. There are several common methods of cooling electrical cabinets: fans, open blowing of compressed air, direct-expansion cooling units, heat pipes, thermoelectric coolers, and compressed air vortex coolers. Compressed air vortex tubes (“Ranque-Hilsch vortex tubes”) are used because they are cost-effective, simple (no moving parts), and appropriate for dirty or dusty environments where filter fouling is a concern. Vortex tubes separate the compressed air stream into hot air and cold air streams that reach to 100°F below inlet air temperature, making them much more effective than open blowing.

If compressed air cooling is used and uncontrolled, it typically blows continuously at an unregulated pressure. In these cases, a thermostatic control is recommended to reduced unnecessary compressed air consumption. These controls are available as retrofit kits or integrated with new vortex coolers.

This measure was developed to be applicable to the following program types: TOS, RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The high efficiency equipment is a vortex tube cabinet cooler with valve and thermostatic control. Inlet modulating compressor systems are not eligible for this measure.

###### Definition of Baseline Equipment

The baseline equipment is a continuously operated vortex tube cabinet cooler without thermostatic control.

###### Deemed Lifetime of Efficient Equipment

5 years

###### Deemed Measure Cost

$340 per thermostat kit, $280 incremental cost of new cooler with thermostat, and $1,390 total cost of new cooler with thermostat.

###### Loadshape

Loadshape C35 - Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = CFMCooler * kWComp * Hours * SF

Where:

CFMCooler 	= Rated flow of the vortex cooler (CFM)

kWComp 	= System power reduction per air demand (kW/CFM) depending on the type of air compressor found in table below. If unknown, assume Screw – Load/Unload.

| Air Compressor Type | kWComp (kW/CFM) |
| --- | --- |
| Reciprocating – On/off Control | 0.18 |
| Reciprocating – Load/Unload | 0.14 |
| Screw – Load/Unload | 0.15 |
| Screw – Variable Displacement | 0.15 |
| Screw - VFD | 0.18 |

Hours 	= Compressed air system pressurized hours

= Use actual hours if known, otherwise assume values in table below:

| Shift | Hours |
| --- | --- |
| Single Shift | 1,976 |
| Two Shifts | 3,952 |
| Three Shifts | 5,928 |
| Four Shifts or Continual Operation | 8,320 |
| Unknown / Weighted average | 5,702 |

SF	= Savings Factor, representing the percentage of time the cooler is shut off by the thermostatic control.

= 25%

For example, a 20-CFM vortex cooler outfitted with a thermostat control would save

kWh 		= 20 * 0.152 * 5,702 * 25%

= 4,334 kWh

###### Summer Coincident Peak Demand Savings

ΔkW = ΔkWh/Hours * CF

Where:

ΔkW		= As calculated above

CF		= Summer peak coincidence factor

| Shift | Coincidence Factor |
| --- | --- |
| Single Shift | 0.59 |
| Two Shifts | 0.95 |
| Three Shifts | 0.95 |
| Four Shifts or Continual Operation | 0.95 |
| Unknown / Weighted average | 0.89 |

For example, a 20-CFM vortex cooler outfitted with a thermostat control would save

kW 		= 4,334 / 5,702 * 0.89

= 0.68 kW

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code CI-CPA-VTEX-V01-200101

###### Review Deadline: 1/1/2023

### Efficient Desiccant Compressed Air Dryer

###### Description

Compressed air is dried to reduce or eliminate condensation that can harm the compressed air system or end use equipment. For applications that require air to be dried below a dew point of 35°F, regenerative desiccant air dryers are typically used. Typically, regenerative desiccant dryers achieve pressure dew points as low as -40°F.

Regenerative desiccant dryers generally consist of two towers (or vertical tanks) filled with porous desiccant media. “Wet” compressed air flows through one tower, exiting as dried compressed air, while the other tower is dried out (or regenerated). This dryer alternates this process between towers to prevent compressed air flowing through saturated towers and damaging downstream equipment. The means of regeneration distinguishes the different types of regenerative dryer.

Heatless Desiccant Dryer: Uses compressed air (“purge air”) to dry out the regenerating tower. The amount of purge air is typically between 15-20% of the dryer’s rate flow (CFM), regardless of the flow rate that the compressor is supplying. This type of dryer alternates tower regeneration approximately every 5 minutes.

Heated Desiccant Dryer: Uses a combination of compressed purge air and heat for regeneration. The amount of purge air is typically 5-10% of the dryer’s rate flow (CFM), regardless of the flow rate that the compressor is supplying. This type of dryer alternates tower regeneration approximately every 8 hours.

Externally Heated Blower Purge Dryer: Uses an external blower and heat source for regeneration. This type of dryer requires a small amount (2%) of purge air or ambient air to cool the tower after heating. This type of dryer alternates tower regeneration approximately every 8 hours. There is also a type of blower purge dryer called a zero purge dryer that eliminates all compressed purge air.

The energy use of these dryers is primarily due to regeneration of the desiccant. Standard dryers come equipped with a fixed, timer regeneration control. However, the actual load on the dryer is variable. Optional dew point demand controls (DPDC) adjust the amount of regeneration to the moisture load on the dryer, reducing unnecessary purge energy.

This measure was developed to be applicable to the following program types: TOS, NC, ER.

###### Definition of Efficient Equipment

The efficient equipment is heated or externally-heated by a blower purge desiccant dryer without dew point demand controls. Dryers installed on inlet modulation compressors do not qualify for this measure.

###### Definition of Baseline Equipment

The baseline equipment is a heatless regenerative desiccant dryer without dew point demand controls.

###### Deemed Lifetime of Efficient Equipment

The lifetime of this measure is 15 years.

###### Deemed Measure Cost

The incremental equipment cost for heated and blower purge regenerative desiccant dryers is $3/CFM and $12/CFM, respectively.

###### Loadshape

Loadshape C35 – Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = CFMDryer * (PBase – PEE * PRF) * HOU

Where:

CFMDryer 	= rated capacity of the dryer in cubic feet per minute (CFM)

PBase	= power requirement of the baseline heatless regenerative dryer (kW/CFM)

= PFHeatless * kWcomp

PFHeatless	= purge flow of heatless model (%)

= 15%

kWcomp	= system power reduction per reduced air demand (kW/CFM) depending on the type of compressor control. If unknown, assume Screw – Load/Unload.

| Air Compressor Type | ΔkW/CFM |
| --- | --- |
| Reciprocating – On/off Control | 0.18 |
| Reciprocating – Load/Unload | 0.14 |
| Screw – Load/Unload | 0.15 |
| Screw – Variable Displacement | 0.15 |
| Screw - VFD | 0.18 |

Note: Dryers installed on inlet modulation compressors do not qualify for this measure.

PEE	= power requirement of the energy efficient (heated or blower purge) regenerative dryer (kW/CFM)

= (PFEE * kWcomp + kWHeater + kWBlower)

PFEE	= purge flow of energy efficient model (%)

= 7.5% for heated models

= 2% for blower purge models (with compressed air cooling)

= 0% for “zero purge” blower purge models

kWHeater	= average power of heater per CFM of dryer (kW/CFM),

= 0.007 kW/CFM for heated models

= 0.013 kW/CFM for blower purge models

kWBlower	= average power of blower per CFM of dryer (kW/CFM)

= 0 kW/CFM for heated models

= 0.003 kW/CFM for blower purge models

PRF	= purge reduction factor

= Assume 50% for heatless desiccant dryers%

= Assume 60% for externally-heated or heated blower purge desiccant dryers

HOU	= compressor total hours of operation below depending on shift

| Shift | Hours |
| --- | --- |
| Single Shift | 1,976 |
| Two Shifts | 3,952 |
| Three Shifts | 5,928 |
| Four Shifts or Continual Operation | 8,320 |
| Unknown / Weighted average | 5,702 |

###### Summer Coincident Peak Demand Savings

ΔkWpeak = ΔkWh / HOU * CF

Where:

CF	= summer peak coincidence factor

| Shift | Coincidence Factor |
| --- | --- |
| Single Shift | 0.59 |
| Two Shifts | 0.95 |
| Three Shifts | 0.95 |
| Four Shifts or Continual Operation | 0.95 |
| Unknown / Weighted average | 0.89 |

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code CI-CPA-DDRY-V02-210101

###### Review Deadline: 1/1/2024

### Desiccant Dryer Dew Point Demand Controls

###### Description

Compressed air is dried to reduce or eliminate condensation that can harm the compressed air system or end use equipment. For applications that require air to be dried below a dew point of 35°F, regenerative desiccant air dryers are typically used. Typically, regenerative desiccant dryers achieve pressure dew points as low as -40°F.

Regenerative desiccant dryers generally consist of two towers (or vertical tanks) filled with porous desiccant media. “Wet” compressed air flows through one tower, exiting as dried compressed air, while the other tower is dried out (or regenerated). This dryer alternates this process between towers to prevent compressed air flowing through saturated towers and damaging downstream equipment. The means of regeneration distinguishes the different types of regenerative dryer.

The energy use of these dryers is primarily due to regeneration of the desiccant. Standard dryers come equipped with a fixed, timer regeneration control. However, the actual load on the dryer is variable. Dew point demand controls (DPDC) adjust the amount of regeneration to the load on the dryer, reducing unnecessary purge energy.

DPDC can be retrofit on existing desiccant dryers or integrated in new desiccant dryers.

Heatless Desiccant Dryer: Uses compressed air (“purge air”) to dry out the regenerating tower. The amount of purge air is typically between 15-20% of the dryer’s rate flow (CFM), regardless of the flow rate that the compressor is supplying. This type of dryer alternates tower regeneration approximately every 5 minutes.

Heated Desiccant Dryer: Uses a combination of compressed purge air and heat for regeneration. The amount of purge air is typically 5-10% of the dryer’s rate flow (CFM), regardless of the flow rate that the compressor is supplying. This type of dryer alternates tower regeneration approximately every 8 hours.

Externally Heated Blower Purge Dryer: Uses an external blower and heat source for regeneration. This type of dryer requires a small amount (2%) of purge air or ambient air to cool the tower after heating. This type of dryer alternates tower regeneration approximately every 8 hours. There is also a type of blower purge dryer called a zero purge dryer that eliminates all compressed purge air.

This measure was developed to be applicable to the following program types: RF

###### Definition of Efficient Equipment

The efficient equipment is a heatless, externally-heated, or blower purge regenerative desiccant dryer without dew point demand controls. The controls should be able to respond to changes in flow and moisture loading. Dryers installed on inlet modulation compressors do not qualify for this measure.

###### Definition of Baseline Equipment

The baseline equipment is a heatless, externally-heated, or blower purge regenerative desiccant dryer with dew point demand controls.

###### Deemed Lifetime of Efficient Equipment

The lifetime of this measure is 5 years.

###### Deemed Measure Cost

The estimated cost of the controls retrofit is $4,000.

###### Loadshape

Loadshape C35 – Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = CFMDryer * (PF * kWComp + kWHeater + kWBlower) * HOU * PRF

Where:

CFMDryer 	= rated capacity of the dryer in cubic feet per minute (CFM)

PF	= purge flow of desiccant dryer (%)

| Air Compressor Type | Purge Flow |
| --- | --- |
| Heatless | 15% |
| Externally-Heated | 7.5% |
| Blower Purge | 2% |

kWcomp	= system power reduction per reduced air demand (kW/CFM) depending on the type of compressor control. If unknown, assume Screw – Load/Unload.

| Air Compressor Type | ΔkW/CFM |
| --- | --- |
| Reciprocating – On/off Control | 0.18 |
| Reciprocating – Load/Unload | 0.14 |
| Screw – Load/Unload | 0.15 |
| Screw – Variable Displacement | 0.15 |
| Screw - VFD | 0.18 |

Note: Dryers installed on inlet modulation compressors do not qualify for this measure.

kWHeater	= average power of heater per CFM of dryer (kW/CFM),

= 0.007 kW/CFM for heated models

= 0.013 kW/CFM for blower purge models

kWBlower	= average power of blower per CFM of dryer (kW/CFM)

= 0 kW/CFM for heated models

= 0.003 kW/CFM for blower purge models

HOU	= compressor total hours of operation below depending on shift

| Shift | Hours |
| --- | --- |
| Single Shift | 1,976 |
| Two Shifts | 3,952 |
| Three Shifts | 5,928 |
| Four Shifts or Continual Operation | 8,320 |
| Unknown / Weighted average | 5,702 |

PRF	= purge reduction factor

= Assume 50% for heatless desiccant dryers%

= Assume 60% for externally-heated or heated blower purge desiccant dryers

###### Summer Coincident Peak Demand Savings

ΔkWpeak = ΔkWh / HOU * CF

Where:

CF	= summer peak coincidence factor

| Shift | Coincidence Factor |
| --- | --- |
| Single Shift | 0.59 |
| Two Shifts | 0.95 |
| Three Shifts | 0.95 |
| Four Shifts or Continual Operation | 0.95 |
| Unknown / Weighted average | 0.89 |

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code CI-CPA-DPDC-V01-210101

###### Review Deadline: 1/1/2023

### Compressed Air Heat Recovery

###### Description

Air compressors are inherently inefficient, converting 80 to 93% of the electrical input energy into heat. Recovering this wasted heat for useful purposes is one method for reducing facility-level energy use. Typical air compressor heat recovery involves ducting air-cooled air compressor exhaust for space heat. Recovered heat can also be used for process heating, water heating, and boiler makeup water heating, but this workpaper only addresses the most common scenario.

This measure was developed to be applicable to the following program types: RF, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is an air-cooled air compressor that is ducted for heat recovery during the heating season. The ducting must include a thermostat that controls the heat recovery based on whether heating is needed.

###### Definition of Baseline Equipment

The baseline equipment is an air-cooled air compressor whose exhaust is ducted to the outdoors or to a space where heat is not needed (e.g., compressor room, unoccupied space).

###### Deemed Lifetime of Efficient Equipment

15 years

###### Deemed Measure Cost

$80/hp

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

Δtherms = ηHR * 2,545 * HP * PP * Hours * CHF / 100,000 / ηheat

Where:

ηHR 	= Efficiency of heat recovery

= 80%

2,545 	= Conversion factor, Btu/hp-hr

HP 	= Nominal horsepower of the compressor

PP 	= Percent power at average load (% flow or capacity) conditions. See table below

If average flow is unknown, assume 65%.

If compressor type is unknown, assume Load/No-load (1 gal/CFM)

= 93.5%

| % Capacity | On/Off Control | Load/No-Load (1 gal/cfm) | Load/No-Load (10 gal/cfm) | Inlet Valve Modulation (w/o Blowdown) | Inlet Valve Modulation (w/ Blowdown) | Variable Displacement | VSD w/ Unloading | VSD w/ Stopping |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0% | 0% | 27% | 27% | 71% | 26% | 25% | 12% | 0% |
| 10% | 10% | 32% | 35% | 74% | 40% | 34% | 20% | 12% |
| 20% | 20% | 63% | 42% | 76% | 54% | 44% | 28% | 24% |
| 30% | 30% | 74% | 52% | 79% | 62% | 52% | 36% | 33% |
| 40% | 40% | 81% | 60% | 82% | 82% | 61% | 45% | 41% |
| 50% | 50% | 87% | 68% | 86% | 86% | 63% | 53% | 53% |
| 60% | 60% | 92% | 76% | 88% | 88% | 69% | 60% | 60% |
| 65% | 65% | 94% | 80% | 90% | 90% | 73% | 66% | 66% |
| 70% | 70% | 95% | 83% | 92% | 92% | 77% | 71% | 71% |
| 80% | 80% | 98% | 89% | 94% | 94% | 85% | 80% | 80% |
| 90% | 90% | 100% | 96% | 97% | 97% | 91% | 89% | 89% |
| 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |

Hours 	= Compressor hours of operation below depending on shift

= Use actual hours if known, otherwise assume values in table below:

| Shift | Hours |
| --- | --- |
| Single Shift | 1,976 |
| Two Shifts | 3,952 |
| Three Shifts | 5,928 |
| Four Shifts or Continual Operation | 8,320 |
| Unknown / Weighted average | 5,702 |

CHF 	= Climate heating factor. This value represents the amount of time that the facility has a use for space heating. See table below for values.

| Zone | Climate Heating Factor |
| --- | --- |
| 1 - Rockford | 58% |
| 2 - Chicago | 55% |
| 3 - Springfield | 48% |
| 4 - Belleville | 49% |
| 5 - Marion | 46% |

100,000	= Conversion factor, Btu/therm

ηheat 	= Heating system efficiency

= If actual heating system efficiency is unknown, assume 80%

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code CI-CPA-CHR-V01-210101

###### Review Deadline: 1/1/2023

### Compressed Air Storage Receiver Tank

###### Description

Using an air receiver or storage tank will buffer the air demands of the system on the compressor, thus eliminating short cycling. Although a load/no load compressor unloads in response to lowered demand, it does so over a period of time to prevent lubrication oil from foaming. Therefore, reducing the number of cycles reduces the number of transition times from load to no load and saves energy.

To qualify for this measure an existing load/no load compressor with a 1 gal/cfm storage ratio or a modulating w/ blowdown compressor must be replaced with a load/no load compressor with an improved storage capacity and ratio.

This measure was developed to be applicable to the following program types: RF, NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is an oil-flooded load/no load compressor with an improved storage capacity and ratio compared to the existing system. The cfm should reflect the rated capacity (in cfm) of all active compressors. If that value cannot be determined, compressor power can be converted to capacity using the rule-of-thumb 4.5 cfm/hp.

###### Definition of Baseline Equipment

The baseline equipment is an oil-flooded load/no load compressor with a 1 gal/cfm storage ratio or a modulating w/ blowdown compressor.

###### Deemed Lifetime of Efficient Equipment

10 years

###### Deemed Measure Cost

Incremental cost ($) = 4.67 * (TANKE – TANKB)

Where:

4.67	= air receiver tank size, in gallons, to equipment cost conversion factor

TANKE	= efficient tank size (gallons)

TANKB	= baseline tank size (gallons)

###### Loadshape

Loadshape C35 – Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

kWh = 0.9 x hpcompressor x HOURS x (CFb – CFe)

Where:

kWh		= gross customer annual kWh savings for the measure

hpcompressor	= compressor motor nominal hp

0.9		= compressor motor nominal hp to full load kW conversion factor

HOURS		= compressor total hours of operation below depending on shift

| Shift | Hours |
| --- | --- |
| Single shift (8/5) | 1,976 hours 7 AM – 3 PM, weekdays, minus some holidays and scheduled down time |
| 2-shift (16/5) | 3,952 hours 7AM – 11 PM, weekdays, minus some holidays and scheduled down time |
| 3-shift (24/5) | 5,928 hours 24 hours per day, weekdays, minus some holidays and scheduled down time |
| 4-shift (24/7) | 8,320 hours 24 hours per day, 7 days a week minus some holidays and scheduled down time |
| Unknown / Weighted average | 5,702 hours |

CFb		= baseline compressor factor

= See table below for baseline compressor factor. If compressor type is unknown, default to a load/no load compressor with 1 gallon/cfm for the appropriate-sized compressor.

| Baseline Compressor | Compressor Factor (≤ 40 hp) | Compressor Factor (50 – 200 hp) |
| --- | --- | --- |
| Modulating w/ Blowdown | 0.890 | 0.863 |
| Load/No Load w/ 1 Gallon/CFM | 0.909 | 0.887 |
| Load/No Load w/ 3 Gallon/CFM | 0.831 | 0.811 |
| Load/No Load w/ 4 Gallon/CFM | 0.812 | 0.792 |
| Load/No Load w/ 5 Gallon/CFM | 0.806 | 0.786 |

CFe		= efficient compressor factor

= See table above for load/no load compressors with the adequate storage capacity installed. If unknown, default to load/no load compressors w/ 4 gallons/cfm.

For example, a 1-shift facility with a 100-hp modulating (with blowdown) adds a 2,000-gallon receiver to their compressed air system. This improvement brings the system storage over 4 gallons per cfm.

Capacity Check:		= 2,000 gallons / (100 hp * 4.5 cfm/hp)

= 4.4 gallons per cfm

kWh 		= 0.9 * 100 * 1,976 * (0.863 – 0.792)

= 12,627 kWh

###### Summer Coincident Peak Demand Savings

kW 		= kWh / HOURS * CF

Where:

CF	= Summer peak coincidence factor for this measure

| Shift | Coincidence Factor |
| --- | --- |
| Single shift (8/5) | 0.59 |
| 2-shift (16/5) | 0.95 |
| 3-shift (24/5) | 0.95 |
| 4-shift (24/7) | 0.95 |
| Unknown / Weighted average | 0.89 |

For example, a 1-shift facility with a 100-hp VSD modulating (with blowdown) compressor adds a 2,000-gallon receiver to their compressed air system. This improvement vrings the system storage over 4 gallons per cfm.

Capacity Checek:		= 2,000 gallons / (100 hp * 4.5 cfm/hp)

= 4.4 gallons per cfm

kW 		= 12,627 / 1,976 * 0.59

= 3.77 kW

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-CPA-CASRT-V01-210101

###### Review Deadline: 1/1/2023

### Reduce Compressed Air Setpoint

###### Description

This measure characterizes the energy savings associated with reducing the compressed air pressure setpoint. A lower setpoint pressure results in the reduction of work requirements on the compressor resulting in energy savings. The energy savings assumptions are based on compressors operating at 100 psi.

This measure was developed to be applicable to the following program types: RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment must meet the following requirements:

- Compressor setpoint must be decreased

- Specification and location of compressor must be known and verifiable

###### Definition of Baseline Equipment

The baseline equipment is an air compressor with a pressure setpoint higher than necessary (line pressure more than 115% of the highest end use requirement).

###### Deemed Lifetime of Efficient Equipment

The expected measure life is 5 years.

###### Deemed Measure Cost

The incremental cost is assumed to be $0.

###### Loadshape

Loadshape C35 – Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

kWh = (kWtypical * ΔP * SF * Hours / HPtypical) * HPreal

Where:

kWh		= gross customer annual kWh savings for the measure

kWtypical	= adjusted compressor power (kW) based on typical compressor loading and operating profile. Use actual compressor control type if known:

| Control Type | kWtypical |
| --- | --- |
| Reciprocating - On/off Control | 70.2 |
| Reciprocating - Load/Unload | 74.8 |
| Screw - Load/Unload | 82.3 |
| Screw - Inlet Modulation | 82.5 |
| Screw - Inlet Modulation w/ Unloading | 82.5 |
| Screw - Variable Displacement | 73.2 |
| Screw - VFD | 70.8 |

= if the actual compressor control type is not known, use a weighted average based on the following market assumptions:

| Control Type | Share % | kWtypical |
| --- | --- | --- |
| Market share estimation for load/unload control compressors | 56% | 74.8 |
| Market share estimation for modulation w/unloading control compressors | 27% | 82.5 |
| Market share estimation for variable displacement control compressors | 17% | 73.2 |
| Weighted Average |  | 76.6 |

∆P 		= reduction in pressure differential between efficient and base case (psi)

= actual

SF	=1% reduction in power per 2 psi reduction in system pressure is equal to 0.5% reduction per 1 psi, or a Savings Factor of 0.005

HOURS		= compressor total hours of operation below depending on shift

| Shift | Hours |
| --- | --- |
| Single shift (8/5) | 1,976 hours 7 AM – 3 PM, weekdays, minus some holidays and scheduled down time |
| 2-shift (16/5) | 3,952 hours 7AM – 11 PM, weekdays, minus some holidays and scheduled down time |
| 3-shift (24/5) | 5,928 hours 24 hours per day, weekdays, minus some holidays and scheduled down time |
| 4-shift (24/7) | 8,320 hours 24 hours per day, 7 days a week minus some holidays and scheduled down time |
| Unknown / Weighted average | 5,702 hours |

HPtypical 		= nominal HP for typical compressor

= 100 hp

HPreal 	= total HP of real compressors distibuting air through filter. This should include the total horsepower of the compressors that normally run through the filter, but not backup compressors.

###### Summer Coincident Peak Demand Savings

kW 		= kWh / HOURS * CF

Where:

CF	= Summer peak coincidence factor for this measure

| Shift | Coincidence Factor |
| --- | --- |
| Single shift (8/5) | 0.59 |
| 2-shift (16/5) | 0.95 |
| 3-shift (24/5) | 0.95 |
| 4-shift (24/7) | 0.95 |
| Unknown / Weighted average | 0.89 |

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-CPA-RCAS-V01-210101

###### Review Deadline: 1/1/2023

### AODD Pump Controls

###### Description

Diaphragm pumps are widely used for their numerous advantages, such as simplicity, serviceability, and durability. These pumps can tolerate fluids that are corrosive, viscous, or contain a significant portion of entrained solids (E.g., effluent and slurries). Diaphragm pumps can be driven by compressed air or electric motors. Air-operated double diaphragm (AODD) pumps are estimated to be present in up to 85-90% of manufacturing plants in the US. The intrinsic simplicity of AODDs allow them to have significantly lower upfront material costs than electric motor-driven diaphragm pumps since there is no electric motor.

Typically, AODDs are operated at a fixed capacity and do not have a controller attached. In this scenario, the pump consumes compressed air continuously when operating. An electronic stroke controller can reduce the amount of air that the AODD pump consumes while operating. This controller synchronizes the compressed air release with the pump so that the diaphragm experiences a burst of air rather than a continuous stream. This reduces the air consumption and noise generation of the pump. This technology increases the pressure variance experienced by the pump; however, the overall impact on fluid flow is negligible.

Typically, this technology is limited to larger AODD pump sizes (≥ 2”), higher pressures (≥ 60 psig) and applications with longer operation times. This technology might not be applicable for systems with highly viscous fluids.

This measure was developed to be applicable to the following program types: RF, TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is an AODD pump with an electronic stroke optimizing control.

###### Definition of Baseline Equipment

The baseline equipment is an AODD pump operating at a fixed capacity.

###### Deemed Lifetime of Efficient Equipment

10 years

###### Deemed Measure Cost

Total cost is $1,150. The material cost for this type of control is $950. Labor is $200, based on estimated time of 2 hours and $100 per hour rate.

###### Loadshape

Loadshape C35 – Industrial Process

###### Coincidence Factor

The summer peak coincidence factor for this measure is dependent on the industrial shift and corresponding hours of operation. Values are provided for each shift type in the variable definition section.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = CFMAODD * kWComp * Hours * SF

Where:

CFMAODD 	= Rated flow of the AODD (CFM). Use actual, if known.

If unknown, see below for guidance.

| Nominal Pump Size | Pressure Air Range (psig) | Range of Air Consumption (SCFM) | Default Air Consumption (SCFM) |
| --- | --- | --- | --- |
| 2” | 80 – 120 psig (average = 95 psig) | 90 – 120 | 105 |
| 3” & 4” | 90 – 110 psig (average = 100 psig) | 125 - 150 | 138 |

kWComp 	= System power reduction per air demand (kW/CFM) depending on the type of air compressor found in table below. If unknown, assume Screw – Load/Unload.

| Air Compressor Type | kWComp (kW/CFM) |
| --- | --- |
| Reciprocating – On/off Control | 0.18 |
| Reciprocating – Load/Unload | 0.14 |
| Screw – Load/Unload | 0.15 |
| Screw – Variable Displacement | 0.15 |
| Screw – VFD | 0.18 |

Hours 	= Compressed air system pressurized hours

= Use actual hours if known, otherwise assume values in table below:

| Shift | Hours |
| --- | --- |
| Single Shift | 1,976 |
| Two Shifts | 3,952 |
| Three Shifts | 5,928 |
| Four Shifts or Continual Operation | 8,320 |
| Unknown / Weighted average | 5,702 |

SF	= Savings Factor, representing the reduction of compressed air consumed by the pump

= 35%

For example, a 2-inch AODD is outfitted with a stroke-optimizing control

kWh 		= 105 * 0.15 * 5,702 * 35%

= 31,432 kWh

###### Summer Coincident Peak Demand Savings

ΔkW = ΔkWh/Hours * CF

Where:

ΔkWh		= As calculated above

CF		= Summer peak coincidence factor

| Shift | Coincidence Factor |
| --- | --- |
| Single Shift | 0.59 |
| Two Shifts | 0.95 |
| Three Shifts | 0.95 |
| Four Shifts or Continual Operation | 0.95 |
| Unknown / Weighted average | 0.89 |

For example, a 2-inch AODD is outfitted with a stroke-optimizing control

kW 		= 31,432 / 5,702 * 0.89

= 4.91 kW

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-CPA-AODD-V01-220101

###### Review Deadline: 1/1/2025

## Miscellaneous End Use

### Pump Optimization

###### Description

Pump improvements can be done to optimize the design and control of centrifugal water pumping systems, including water solutions with freeze protection up to 15% concentration by volume.  Other fluid and gas pumps cannot use this measure calculation.  The measurement of energy and demand savings for commercial and industrial applications will vary with the type of pumping technology, operating hours, efficiency, and existing and proposed controls.  Depending on the specific application slowing the pump, trimming or replacing the impeller may be suitable options for improving pumping efficiency. Pumps up to 40 HP are allowed to use this energy savings calculation. Larger motors should use a custom calculation (which may result in larger savings that this measure would claim).

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is proven to be an optimized centrifugal pumping system meeting the applicable program efficiency requirements:

- Pump balancing valves no more than 15% throttled

- Balancing valves on at least one load 100% open.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to be the existing pumping system including existing controls and sequence of operations.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 8 years.

###### Deemed Measure Cost

The incremental capital cost for this measure can vary considerably depending upon the strategy employed to achieve the required efficiency levels and should be determined on a site-specific basis.

###### Loadshape

Loadshape C14: Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15: Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16: Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17: Indust. 4-shift (24/7) (e.g., comp. air, lights)

###### Coincidence Factor

The summer peak coincidence factor for this measure is assumed to be 38%.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

ΔkWh 	= (HPmotor * 0.746 * LF / ηmotor) * HOURS * ESF

Where:

HPmotor		= Installed nameplate motor horsepower

= Actual

0.746 		= Conversion factor from horse-power to kW (kW/hp)

LF / ηmotor	= Combined as a single factor since efficiency is a function of load

= 0.65

Where:

LF 	= Load Factor; Ratio of the peak running load to the nameplate rating of the motor

ηmotor 	= Motor efficiency at pump operating conditions

HOURS 		= Annual operating hours of the pump

= Actual

ESF		= Energy Savings Factor; assume a value of 15%.

###### Summer Coincident Peak Demand Savings

ΔkW 	= (HPmotor * 0.746 *( LF / ηmotor)) * (ESF) * CF

Where:

CF		= Summer Coincident Peak Factor for measure

###### Natural Gas Energy Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-PMPO-V04-220101

###### Review Deadline: 1/1/2027

### Roof Insulation for C&I Facilities

###### Description

Energy and demand saving are realized through reductions in the building cooling and heating loads by way of improvements in roof assembly thermal resistance properties. This measure was developed to be applicable to the following program types:  RF and NC.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient condition is a roof assembly with thermal resistance that exceeds code requirements and should be determined by the program.

###### Definition of Baseline Equipment

The baseline condition in retrofit scenarios is the thermal resistance of the existing roof assembly.

The baseline for new construction scenarios is the thermal resistance of the roof assembly as mandated by applicable building code. Assembly R-values shall be referenced from IECC 2015 or ASHRAE – 90.1 – 2013, or IECC 2018 or ASHRAE 90.1-2016, depending on the IECC in effect on the date of the building permit (if unknown assume IECC 2015).

Note IECC 2018 (based on ASHRAE 90.1-2016) became effective July 1, 2019 and is baseline for all New Construction permits from that date.

###### Deemed Lifetime of Efficient Equipment

The measure expected useful life (EUL) is assumed to be 20 years per DEER 2008. This is consistent with SDG&E’s 9th Year Measure Retrofit Study (1996 & 1997 Residential Weatherization Programs), CPUC’s Energy Efficiency Policy Manual v.2, and GDS’s Measure Life Report Residential and Commercial/Industrial Lighting and HVAC Measures (June 2007).

###### Deemed Measure Cost

Costs can be highly variable due to differences in building type and structural assemblies and for that reason actual costs should be used when possible. Absent of actual cost information, estimated costs can be used. Per the W017 Itron California Measure Cost Study, the material cost for R-30 insulation is $0.59 per square foot. The installation cost is $0.81 per square foot. The total measure cost, therefore, is $1.40 per square foot of insulation installed.

###### Loadshape

Loadshape C03: Commercial Cooling

###### Coincidence Factor

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Electric energy savings is calculated as the sum of energy saved when cooling the building and energy saved when heating the building

∆kWh = ∆kWh_cooling + ∆kWh_heating

If central cooling, the electric energy saved in annual cooling due to the added insulation is

∆kWh_cooling = ((1/R_existing) - (1/R_new)) * Area * EFLHcooling * ΔTAVG,cooling / 1,000 / η_cooling

Where:

R_existing	= Roof assembly heat loss coefficient with existing (or code required) insulation [(hr-⁰F-ft2)/Btu]

= In retrofit scenarios, actual existing conditions prior to retrofit should be used. If unavailable, defualt values by building type can be used, as outlined in the following table and adopted from Ohio Energy Technical Reference Manual and expanded to cover all type of commercial buildings in the state of Illinois. In new construction scenarios, the applicable code requirements, per the following tables, should be used.

For retrofits, the R-value for the entire assembly:

| Building Type | Retrofit Assembly R-Value |
| --- | --- |
| Assembly | 13.5 |
| Assisted Living | 13.5 |
| College | 13.5 |
| Convenience Store | 13.5 |
| Elementary School | 13.5 |
| Garage | 13.5 |
| Grocery | 13.5 |
| Healthcare Clinic | 13.5 |
| High School | 13.5 |
| Hospital | 13.5 |
| Hotel/Motel | 13.5 |
| Manufacturing Facility | 12 |
| MF - High Rise | 13.5 |
| MF - Mid Rise | 13.5 |
| Movie Theater | 13.5 |
| Office - High Rise | 13.5 |
| Office - Low Rise | 13.5 |
| Office - Mid Rise | 13.5 |
| Religious Building | 13.5 |
| Restaurant | 13.5 |
| Retail - Department Store | 13.5 |
| Retail - Strip Mall | 13.5 |
| Warehouse | 12 |
| Unknown | 13.5 |

R-Values: ASHRAE – 90.1 – 2013 and 2016

|  | IL TRM Zones 1, 2, & 3 [ASHRAE/IECC Climate Zone 5 (A, B, C)] |  |  |  |
| --- | --- | --- | --- | --- |
|  | Nonresidential |  | Semiheated |  |
|  | Assembly Maximum | Insulation Min. R-Value | Assembly Maximum | Insulation Min. R-Value |
| Insulation Entirely Above Deck | 0.032 | R-30.0 c.i. | 0.063 | R-15 c.i. |
| Metal Building (Roof) | 0.037 | R-19 + R-11 Ls or R-25 + R-8 Ls | 0.082 | R-19 |
| Attic and Other | 0.021 | R-49 | 0.034 | R-30 |

|  | IL TRM Zones 4 & 5 [ASHRAE/IECC Climate Zone 4 (A, B, C)] |  |  |  | Table Notes c.i. = continuous insulation Ls = linear system, a continuous vapor barrier liner installed below the purlins and uninterrupted by framing members |
| --- | --- | --- | --- | --- | --- |
|  | Nonresidential |  | Semiheated |  |  |
|  | Assembly Maximum | Insulation Min. R-Value | Assembly Maximum | Insulation Min. R-Value |  |
| Insulation Entirely Above Deck | 0.032 | R-30.0 c.i. | 0.093 | R-10 c.i. |  |
| Metal Building (Roof) | 0.037 | R-19 + R-11 Ls or R-25 + R-8 Ls | 0.082 | R-19 |  |
| Attic and Other | 0.021 | R-49 | 0.034 | R-30 |  |

R_new		= Roof assembly heat loss coefficienty with new insulation [(hr-⁰F-ft2)/Btu]

Area 		= Area of the roof surface in square feet.

EFLHcooling	= Equivalent Full Load Hours for Cooling [hr] in Existing Buildings or New Construction are provided in Section 4.4, HVAC end use

ΔTAVG,cooling	= Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 75⁰F  indoor air temperature

| Climate Zone (City based upon) | OAAVG,cooling [°F] | ΔTAVG,cooling [°F] |
| --- | --- | --- |
| 1 (Rockford) | 81 | 6 |
| 2 (Chicago) | 81 | 6 |
| 3 (Springfield) | 81 | 6 |
| 4 (Belleville) | 82 | 7 |
| 5 (Marion) | 82 | 7 |

1,000		= Conversion from Btu to kBtu

η_cooling	= Seasonal energy efficiency ratio (SEER) of cooling system (kBtu/kWh).  Use actual if possible, if unknown and for planning purposes assume the following:

| Year Equipment was Installed | SEER estimate |
| --- | --- |
| Before 2006 | 10 |
| After 2006 | 13 |

If the building is heated with electric heat (resistance or heat pump), the electric energy saved in annual heating due to the added insulation is

∆kWh_heating = [(1/R_existing) - (1/R_new)] * Area * EFLHheating * ΔTAVG,heating / 3,412 / η_heating

Where:

EFLHheating	= Equivalent Full Load Hours for Heating [hr] in Existing Buildings or New Construction are provided in Section 4.4, HVAC end use

ΔTAVG,heating	= Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 55⁰F  heating base temperature

| Climate Zone (City based upon) | OAAVG,heating [°F] | ΔTAVG,heating [°F] |
| --- | --- | --- |
| 1 (Rockford) | 32 | 23 |
| 2 (Chicago) | 34 | 21 |
| 3 (Springfield) | 35 | 20 |
| 4 (Belleville) | 36 | 19 |
| 5 (Marion) | 39 | 16 |

3,142	= Conversion from Btu to kWh.

η_heating	= Efficiency of heating system.  Use actual efficiency.  If not available refer to default table below.

| System Type | Age of Equipment | HSPF Estimate | ηHeat (Effective COP Estimate) (HSPF/3.413)*0.85 |
| --- | --- | --- | --- |
| Heat Pump | Before 2006 | 6.8 | 1.7 |
|  | After 2006 | 7.7 | 1.92 |
| Resistance | N/A | N/A | 1 |

If the building is heated with a gas furnace, there will be some electric savings in heating the building attributed to extra insulation since the furnace fans will run less.

∆kWh_heating = ∆Therms * Fe * 29.3

Where:

∆Therms 	= Gas savings calculated with equation below.

Fe		= Percentage of heating energy consumed by fans, assume 7.7%

29.3		= Conversion from therms to kWh

###### Summer Coincident Peak Demand Savings

∆kW = (∆kWh_cooling / EFLH_cooling) * CF

Where:

EFLHcooling	= Equivalent full load hours of air conditioning in Existing Buildings or New Construction are provided in Section 4.4, HVAC end use

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

###### Natural Gas Savings

If building uses a gas furnace, the savings resulting from the insulation is calculated with the following formula.

∆Therms = ((1/R_existing) - (1/R_new)) * Area * EFLHheating * ΔTAVG,heating / 100,000 / η_heat

Where:

R_existing	= Roof assembly heat loss coefficient with existing (or code required) insulation [(hr-⁰F-ft2)/Btu], per guidance outlined in Electric Energy Savings section.

R_new		= Roof assembly heat loss coefficienty with new insulation [(hr-⁰F-ft2)/Btu]

Area 		= Area of the roof surface in square feet.  Assume 1000 sq ft for planning.

EFLHheating	= Equvalent Full Load Hours for Heating in Existing Buildings or New Construction are provided in Section 4.4, HVAC end use

ΔTAVG,heating	= Average temperature difference [⁰F] during heating season (see above)

100,000		= Conversion from BTUs to Therms

η_heat		= Efficiency of existing furnace.  Assume 0.78 for planning purposes.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure code: CI-MSC-RINS-V06-220101

###### Review Deadline: 1/1/2025

### Computer Power Management Software

###### Description

This measure characterizes the savings achieved through controlling the power management settings of a desktop computer, monitor or laptop. This can be achieved one of two ways; either a centralized computer power management software is installed on a network of computers to monitor and record usage and manage the power management settings of all units (referred to as Centralized Software) , or the settings are adjusted on each individual unit (refered to as Individual Settings).

###### Definition of Efficient Equipment

For Centralized Software, tthe efficient equipment is defined by the requirements listed below:

- Allow centralized control and override of computer power management settings of workstations which include both a computer monitor and CPU (i.e. a desktop or laptop computer on a distributed network)

- Be able to control on/off/sleep states on both the CPU and monitor according to the Network Administrator-defined schedules and apply power management policies to network groups

- Have capability to allow networked workstations to be remotely wakened from power-saving mode (e.g. for system maintenance or power/setting adjustments)

- Have capability to detect and monitor power management performance and generate energy savings reports

- Have capability to produce system reports to confirm the inventory and performance of equipment on which the software is installed.

For Individual Settings, each desktop, monitor or laptop requires power settings to be adjusted to appropriately place devices in a low-power standby, sleep or off mode after a predetermined period of inactivity (for example display sleep mode after 10 minutes of inactivity and computer sleep mode after 30 minutes).

This measure was developed to be applicable to the following program types: RF. If applied to other program types, the measure savings should be verified.

###### Definition of Baseline Equipment

Baseline is defined as a desktop computer, monitor or laptop without the power management settings enabled.

###### Deemed Lifetime of Efficient Equipment

For Centralized Software, the expected measure life is five years.

For Individual Settings, the expected measure life is two years.

###### Deemed Measure Cost

For Centralized Software, the deemed measure cost is $29 per networked computer, including labor.

For Individual Settings, the deemed measure cost is $10 per unit.

###### Loadshape

Loadshape C21: Commercial Office Equipment.

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = ((UECCompBase - UECCompEff )+(UECMonBase - UECMonEff))

Where:

UECComBase = 	Energy consumption of computer before adjusting power settings

(∑State PowerState x HoursBase,State) / 1,000

UECComEff =	Energy consumption of computer after adjusting power settings

(∑State PowerState x HoursEff,State) / 1,000

UECMonBase = 	Energy consumption of monitor before adjusting power settings

(∑State MpW x PowerState x HoursBase,State) / 1,000

UECMonEff = 	Energy consumption of monitor after adjusting power settings

(∑State MpW x PowerState x HoursEff,State) / 1,000

HoursBase,State = 	Annual hours in each power state

8,760 x BaseDutyCycle(%)

| Computer Power State | Base Duty Cycle |  |
| --- | --- | --- |
|  | Computer | Monitor |
| Unplugged | 5% | 22% |
| Off | 55% | 50% |
| Sleep | 2% | 2% |
| Idle | 35% | N/A |
| Active | 3% | 26% |

Hours Eff,State = 	Annual hours in each power state

8,760 x EfficientDutyCycle(%)

| Computer Power State | Efficient Duty Cycle |  |
| --- | --- | --- |
|  | Computer | Monitor |
| Unplugged | 5% | 22% |
| Off | 77% | 57% |
| Sleep | 2% | 2% |
| Idle | 13% | N/A |
| Active | 3% | 19% |

PowerState = 		Power (W) consumption in each power state

| Computer Power State | Power Draw (Watts) |  |  |
| --- | --- | --- | --- |
|  | Desktop Computer | Laptop Computer | Monitor |
| Unplugged | 0.0 | 0.0 | 0.0 |
| Off | 0.9 | 0.5 | 0.23 |
| Sleep | 2.1 | 0.9 | 0.32 |
| Idle | 39.9 | 8.9 | N/A |
| Active | 72.2 | 60.0 | 14.43 |

For example: Computer Savings:

kWh savings = (UECCompBase -UECCompEff )

UECCompBase = 0 x 5% x 8,760+0.9 x 55% x 8,760+2.1 x 2% x 8,760+39.9 x 35% x 8,760+72.2 x 3% x 8,760=146.2kWh

UECCompEff = 0 x 5% x 8760+0.9 x 77% x 8760+2.1 x 2% x 8760+39.9 x 13% x 8760+72.2 x 3% x 8760=70.5kWh

Computer kWh savings = (146.2-70.5) = 75.7kWh

For example: Laptop Savings:

UECCompBase = 0 x 5% x 8,760+0.5 x 55% x 8,760 + 0.9 x 2% x 8,760+8.9 x 35% x 8,760+60.0x 3% x 8,760= 45.6 kWh

UECCompEff = 0 x 5% x 8760+0.5 x 77% x 8760+ 0.9 x 2% x 8760+8.9 x 13% x 8760+60.0 x 3% x 8760=  29.4 kWh

Laptop kWh savings = (45.6 – 29.4) = 16.2 kWh

For example: Monitor Savings (assuming CPMS is controlling 2 monitors):

Monitor kWh savings = (UECMonBase - UECMonEff )

UECMonBase = (2 x 0 x 22% x 8,760+2 x 0.23 x 50% x 8,760+2 x 0.32 x 2% x 8,760+2 x 14.43 x 26% x 8,760)/1,000=67.9kWh

UECMonEff = (2 x 0 x 22% x 8760+2 x 0.23 x 57% x 8,760+2 x 0.32 x 2% x 8,760+2 x 14.43 x 19% x 8,760)/1,000=50.5kWh

Monitor kWh savings = (67.9-50.5) = 17.4kWh

###### Summer Coincident Peak Demand Savings

ΔkW 	= ΔkWh/8760

Computer peak kW savings 	= 75.7/8760 	= 0.009 kW

Laptop peak kW savings 		= 16.2/8760 	=  0.002 kW

Monitor (assuming CPMS is controlling 2 monitors) peak kW savings

=17.4/8760 	= 0.002 kW

###### Natural Gas Saving

NA

###### Water Impact Descriptions and Calculation

NA

###### Deemed O&M Cost Adjustment Calculation

For Centralized Software, assume $2/unit

For Individual Settings, no O&M impacts.

###### Measure code: CI-MSC-CPMS-V04-220101

###### Review Deadline: 1/1/2025

### Modulating Commercial Gas Clothes Dryer

###### Description

This measure relates to the installation of a two-stage modulating gas valve retrofit kit on a standard commercial non-modulating gas dryer. Commercial gas clothes dryers found in coin-operated laundromats or on-premise laundromats (hospitals, hotels, health clubs, etc.) traditionally have a single firing rate which is sized properly for highest heat required in initial drying stages but is oversized for later drying stages requiring lesser heat. This causes the burner to cycle on/off frequently, resulting in less efficient drying and wasted gas. Replacing the single stage gas valve with a two-stage gas valve allows the firing rate to adjust to the changing heat demand, thereby reducing overall gas consumption.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

A 30 to 250 pound capacity commercial gas dryer retrofitted with a two-stage modulating gas valve kit.

###### Definition of Baseline Equipment

A 30 to 250 pound capacity commercial gas dryer with no modulating capabilities.

###### Deemed Lifetime of Efficient Equipment

The deemed measure life for the retrofit kit is 14 years, assumed to be equal to that of a commercial gas dryer.

###### Deemed Measure Cost

The full retrofit cost is assumed to be $700, including the material cost for the basic modulating gas valve retrofit kit ($600) and the associated of labor for installation ($100).

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Energy Savings

Note: Accurately estimating dryer energy consumption is complicated and challenging due to a variety of factors that influence cycle times and characteristics and ultimately drying energy requirements. Clothing loads can vary by weight, volume, fiber composition, physical structure, and initial water content, meaning that for any given cycle drying energy requirements can differ. Additionally, dryer settings selected by the user as well as interactions with the site’s HVAC systems are known to influence dryer performance. As better information becomes available, this characterization can be modified to allow for a more site-specific estimation of savings.

ΔTherms 	= NCycles * SF

Where:

NCycles	= Number of dryer cycles per year. Refer to the table below if this value is not directly available.

| Application | Cycles per Year |
| --- | --- |
| Coin- Operated Laundromats | 1,483 |
| Multi-family Dryers | 1,074 |
| On-Premise Laundromats | 3,607 |

SF 	= Savings factor

= 0.18 therms/cycle

If using default cycles the savings are as follows:

| Application | ΔTherms |
| --- | --- |
| Coin- Operated Laundromats | 267 |
| Multi-family Dryers | 193 |
| On-Premise Laundromats | 649 |

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-MODD-V01-160601

###### Review Deadline: 1/1/2023

### High Speed Clothes Washer

###### Description

This measure applies to the installation of clothes washers with extraction speeds of 200G or greater, which is significantly higher than traditional hard-mount washers. Standard washer extractors in laundromats operate at speeds of 70-80G. The high-speed extraction process in the wash cycle removes more water from each compared to standard washers, reducing operating time and gas consumption of clothes dryers. Heat exposure and mechanical action are also reduced, resulting in less linen wear.

This measure was developed to be applicable to the following program types: TOS, NC, EREP.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is assumed to be a clothes washer with an extraction speed of 200G or greater, installed in a commercial laundromat. This measure is only applicable for sites utilizing gas dryers. Sites using electric dryers are not eligible for participation.

###### Definition of Baseline Equipment

The baseline equipment is assumed to be a clothes washer with an extraction speed of 100G or less, installed in a commercial laundromat.

###### Deemed Lifetime of Efficient Equipment

The measure lifetime is assumed to be the typical lifetime of a commercial clothes washer: 7 years.

For early replacement measures it is assumed the existing unit would last another 2.3 years.

###### Deemed Measure Cost

The incremental cost for time of sale is $9.70/lb capacity.

The full cost of the high speed washer for early replacement applications is $164.89/lb capacity. The deferred replacement cost of the baseline unit is $155.19/lb capacity. This future cost should be discounted to present value using the real discount rate.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

Natural Gas Savings

ΔTherms = (Ncycles * Days * Capacity * RMC * he / ηdryer /100,000) * DryerUse * LF

Where:
	Ncycles	= Average number of washer cycles per day

= Use values from table below, depending on application

| Application | Ncycles |
| --- | --- |
| Coin-operated Laundromats | 4.3 |
| Multi-family | 3.4 |
| Hotel/Motel/Hospital | 10.4 |

Days 	= Days per year of commercial laundromat operation

= Actual, or if unknown, assume 360 days

Capacity	= Clothes washer rated capacity (lb/cycle)

= Actual

RMC   	= Retained Moisture Content (%) reduction from replacing a low extraction speed washer

= Assume 15%

Figure 1

he 	= Heat required by a dryer to evaporate 1 lb of water

= Assume 1,200 Btu/lb

ηdryer       = Efficiency of the clothes dryer

= Actual, or if unknown, assume 60%

100,000 = Converts Btus to therms

DryerUse = % of washer loads dried in the field

= Assume 91%

LF            = Load Factor (%) to account for the pounds per washer load, as a percentage of rated capacity

= Assume 66%

For example, a clothes washer with a 14 lb/cycle capacity and installed at a coin-operated laundromat, using default assumptions, would save:

ΔTherms	= (Ncycles * Days * Capacity * RMC * he / ηdryer /100,000) * DryerUse * LF

= (4.3 * 360 * 14 * 0.25 * 1,200 / 0.60 /100,000) * 0.91 * 0.66

= 65 therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-HSCW-V02-210101

###### Review Deadline: 1/1/2024

### ENERGY STAR Computers

###### Description

This measure estimates savings for a desktop computer with ENERGY STAR (ES) Version 8.0 rating, ES 8.0 +20%, ES 8.0 with 80 PLUS Platinum PSUs, and ES 8.0 with 80 PLUS Titanium PSUs.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient product is a desktop with a rating of ENERGY STAR Version 8.0 rating, ES 8.0 +20%, ES 8.0 with 80 PLUS Platinum PSUs, or ES 8.0 with 80 PLUS Titanium PSUs.

###### Definition of Baseline Equipment

Non ENERGY STAR qualified equipment with standard efficiency power supply.

###### Deemed Lifetime of Efficient Equipment

The life of this measure is 4 years.

###### Deemed Measure Cost

The incremental cost for an 80 Plus Desktop PSU is $5.
The incremental cost for an ENERGY STAR desktop PSU is $20.

###### Loadshape

C21 Commercial Office Equipment

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

kWh	 = 8760/1000 * (((WattsBase,Off * %Time Off) + (Watts Base,Sleep * %Time Sleep) + (Watts Base,Long * %Time Long) + (Watts Base,Short * %Time Short)) - ((Watts Eff,Off * %TimeOff) + (Watts Eff,Sleep * %Time Sleep) + (Watts Eff,Long * %Time Long) + (Watts Eff,Short * %Time Short)))

Where (see assumptions in table below):

8760/1000	= Converts W to kWh

Watts Base,Off	= baseline equipment power in off mode

%Time Off	= typical percent of time a desktop, integrated desktop or notebook is in off mode during the year

Watts Base,Sleep	= baseline equipment power in sleep mode

%Time Sleep	= typical percent time in sleep mode

Watts Base,Long	= baseline equipment power in long idle mode

%Time Long	= typical percent time in long idle mode

Watts Base,Short	= baseline equipment power in short idle mode

%Time Short	= typical percent time in short idle mode

Watts Eff,Off	= efficient equipment power in off mode

Watts Eff,Sleep	= efficient equipment power in sleep mode

Watts Eff,Long	= efficient equipment power in long idle mode

Watts Eff,Short	= efficient equipment power in short idle mode

| Measure Annual Mode Time (%) | Off | Sleep | Long Idle | Short Idle |
| --- | --- | --- | --- | --- |
| Duty cycle – Commercial Desktop | 15% | 45% | 10% | 30% |

| Measure Watt Draw in Mode (Watts) | Off | Sleep | Long Idle | Short Idle |
| --- | --- | --- | --- | --- |
| Baseline | 0.88 | 2.1 | 26.5 | 27.9 |
| ES 8.0 Desktops | 0.64 | 1.54 | 14.97 | 19.62 |
| ES 8.0 +20% Desktops | 0.64 | 1.53 | 14.47 | 19.22 |
| ES 8.0 Desktops w/ 80 PLUS Platinum PSUs | 0.50 | 1.50 | 13.97 | 18.30 |
| ES 8.0 Desktops w/ 80 PLUS Titanium PSUs | 0.50 | 1.50 | 13.67 | 17.91 |

Calculated energy consumption in each mode, and savings provided below:

| Measure TEC by Mode - Commercial | Off | Sleep | Long Idle | Short Idle | TEC (kWh/yr) | Savings (kWh/yr) |
| --- | --- | --- | --- | --- | --- | --- |
| Baseline | 1.2 | 8.3 | 23.2 | 73.3 | 106.0 | N/A |
| ES 8.0 Desktops | 0.8 | 6.1 | 13.1 | 51.6 | 71.6 | 34.4 |
| ES 8.0 +20% Desktops | 0.8 | 6.0 | 12.7 | 50.5 | 70.1 | 35.9 |
| ES 8.0 Desktops w/ 80 PLUS Platinum PSUs | 0.7 | 5.9 | 12.2 | 48.1 | 66.9 | 39.1 |
| ES 8.0 Desktops w/ 80 PLUS Titanium PSUs | 0.7 | 5.9 | 12.0 | 47.1 | 65.6 | 40.3 |

Savings calculations can be referenced in “ENERGY STAR Computers Analysis_2020_Revised.xlsx”

###### Summer Coincident Peak Demand Savings

kW 	= (WattsBase - Watts Eff)/1000 * CF

Where:

WattsBase	= Assumed average baseline wattage during peak period (see table below)

WattsEff		= Assumed average efficient wattage during peak period (see table below)

CF		= Summer Peak Coincidence Factor

= 1.0

Calculated average demand during peak period, and savings provided below:

| Measure Demand Reduction by Mode | TEC (Watts) | Long Idle Demand Savings (kW) | Short Idle Demand Savings (kW) | Weighted Average Demand Savings (kW) |
| --- | --- | --- | --- | --- |
| Baseline | 14.1 | N/A | N/A | N/A |
| ES 8.0 Desktops | 9.5 | 0.0115 | 0.0083 | 0.0091 |
| ES 8.0 +20% Desktops | 9.3 | 0.0120 | 0.0087 | 0.0095 |
| ES 8.0 Desktops w/ 80 PLUS Platinum PSUs | 8.9 | 0.0125 | 0.0096 | 0.0103 |
| ES 8.0 Desktops w/ 80 PLUS Titanium PSUs | 8.7 | 0.0128 | 0.0100 | 0.0107 |

Please note, the last column is a weighted average of the Long & Short Idle Modes and should be the value used in calculations. All Savings calculations can be referenced in “ENERGY STAR Computers Analysis_2020_Revised.xlsx”

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-COMP-V03-210101

###### Review Deadline: 1/1/2025

### Advanced Power Strip – Tier 1 Commercial

###### Description

This measure relates to Advanced Power Strips – Tier 1 which are multi-plug power strips with the ability to automatically disconnect specific connected loads depending upon the power draw of a control load, also plugged into the strip. Power is disconnected from the switched (controlled) outlets when the control load power draw is reduced below a certain adjustable threshold, thus turning off the appliances plugged into the switched outlets. By disconnecting, the standby load of the controlled devices, the overall load of a centralized group of equipment (e.g. a desk workstation) can be reduced. In a commercial office space, savings generally occur during off-hours, when connected equipment continues to consume electricity while in standby mode or when off. Uncontrolled outlets are also provided that are not affected by the control device and so are always providing power to any device plugged into it.

This measure was developed to be applicable to the following program types: DI.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient case is an advanced power strip with a load-sensing master plug and at least two controlled plugs.

###### Definition of Baseline Equipment

The assumed baseline is a standard power strip with surge protection that does not control connected loads.

###### Deemed Lifetime of Efficient Equipment

The assumed lifetime of the advanced power strip is 7 years.

###### Deemed Measure Cost

For direct install the actual full equipment and installation cost (including labor) and for kits the actual full equipment cost should be used.

###### Loadshape

Loadshape C47 – Standby Losses – Commercial Office

###### Coincidence Factor

N/A due to no savings attributable to standby losses between 1 and 5 PM.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh 	= ((kWwkday * (hrswkday - hrswkday-open)) + (kWwkend * (hrswkend - hrswkend-open))) * weeks/year * ISR

Where:

kWwkday 	= Standby power consumption of connected electronics on weekday off-hours. If unknown, assume 0.0315 kW.

kWwkend 	= Standby power consumption of connected electronics on weekend off-hours. If unknown, assume 0.00617 kW.

hrswkday 	= total hours during the work week (Monday 7:30 AM to Friday 5:30 PM)

= 106

hrswkend 	= total hours during the weekend (Friday 5:30 PM to Monday 7:30 AM)

= 62

hrswkday-open 	= hours the office is open during the work week. If unknown, assume 50 hours.

hrswkend-open 	= hours the office is open during the weekend. If unknown, assume 0 hours.

weeks/year	= number of weeks per year

= 52.2

ISR		= In Service Rate

= Assume 0.969 for commercial Direct Install application

For example, an office open 9 hours per day (45 hours per week) on weekdays and 4 hours on Saturday:

ΔkWh 	= ((0.0315 * (106 - 45)) + (0.00617 * (62 - 4))) * 52.2 * 0.969

= 115 kWh

###### Summer Coincident Peak Demand Savings

N/A due to no savings attributable to standby losses between 1 and 5 PM.

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-APSC-V03-200101

###### Review Deadline: 1/1/2024

### High Efficiency Transformer

###### Description

Distribution transformers are used in commercial and industrial applications to step down power from distribution voltage to be used in HVAC or process loads (220V or 480V) or to serve plug loads (120V).

Distribution transformers that are more efficient than the required minimum federal standard efficiency qualify for this measure. If there is no specific standard efficiency requirement, the transformer does not qualify (because we cannot define a reasonable baseline). For example, although the federal standards increased the minimum required efficiency in 2016, most transformers with a NEMA premium or CEE Tier 2 rating will still achieve energy conservation. Standards are defined for low-voltage dry-type distribution transformers (up to 333kVA single-phase and 1000kVA 3-phase), liquid-immersed distribution transformers (up to 833kVA single-phase and 2500kVA 3-phase), and medium-voltage dry-type distribution transformers (up to 833kVA single-phase and 2500kVA 3-phase).

This measure was developed to be applicable to the following program types:  TOS, NC.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Any transformer that is more efficient than the federal minimum standard. This includes CEE Tier II (single or three phase) and most NEMA premium efficiency rated products.

###### Definition of Baseline Equipment

A transformer that meets the minimum federal efficiency requirement should be used as the baseline to calculate savings. Standards are developed by the Department of Energy and published in the Federal Register 10CFR 431.

(a) Low-Voltage Dry-Type Distribution Transformers.

(2) The efficiency of a low-voltage dry-type distribution transformer manufactured on or after January 1, 2016, shall be no less than that required for their kVA rating in the table below. Low-voltage dry-type distribution transformers with kVA ratings not appearing in the table shall have their minimum efficiency level determined by linear interpolation of the kVA and efficiency values immediately above and below that kVA rating.

| Single-phase |  | Three-phase |  |
| --- | --- | --- | --- |
| kVA | Efficiency (%) | kVA | Efficiency (%) |
| 15 | 97.70 | 15 | 97.89 |
| 25 | 98.00 | 30 | 98.23 |
| 37.5 | 98.20 | 45 | 98.40 |
| 50 | 98.30 | 75 | 98.60 |
| 75 | 98.50 | 112.5 | 98.74 |
| 100 | 98.60 | 150 | 98.83 |
| 167 | 98.70 | 225 | 98.94 |
| 250 | 98.80 | 300 | 99.02 |
| 333 | 98.90 | 500 | 99.14 |
|  |  | 750 | 99.23 |
|  |  | 1000 | 99.28 |

(b) Liquid-Immersed Distribution Transformers.

(2) The efficiency of a liquid-immersed distribution transformer manufactured on or after January 1, 2016, shall be no less than that required for their kVA rating in the table below. Liquid-immersed distribution transformers with kVA ratings not appearing in the table shall have their minimum efficiency level determined by linear interpolation of the kVA and efficiency values immediately above and below that kVA rating.

| Single-phase |  | Three-phase |  |
| --- | --- | --- | --- |
| kVA | Efficiency (%) | kVA | Efficiency (%) |
| 10 | 98.70 | 15 | 98.65 |
| 15 | 98.82 | 30 | 98.83 |
| 25 | 98.95 | 45 | 98.92 |
| 37.5 | 99.05 | 75 | 99.03 |
| 50 | 99.11 | 112.5 | 99.11 |
| 75 | 99.19 | 150 | 99.16 |
| 100 | 99.25 | 225 | 99.23 |
| 167 | 99.33 | 300 | 99.27 |
| 250 | 99.39 | 500 | 99.35 |
| 333 | 99.43 | 750 | 99.40 |
| 500 | 99.49 | 1000 | 99.43 |
| 667 | 99.52 | 1500 | 99.48 |
| 833 | 99.55 | 2000 | 99.51 |
|  |  | 2500 | 99.53 |

(c) Medium-Voltage Dry-Type Distribution Transformers.

(2) The efficiency of a medium- voltage dry-type distribution transformer manufactured on or after January 1, 2016, shall be no less than that required for their kVA and BIL rating in the table below. Medium-voltage dry-type distribution transformers with kVA ratings not appearing in the table shall have their minimum efficiency level determined by linear interpolation of the kVA and efficiency values immediately above and below that kVA rating.

| Single-phase |  |  |  | Three-phase |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| kVA | BIL* |  |  | kVA | BIL |  |  |
|  | 20-45 kV | 46-95 kV | ≥96 kV |  | 20-45 kV | 46-95 kV | ≥96 kV |
|  | Efficiency (%) | Efficiency (%) | Efficiency (%) |  | Efficiency (%) | Efficiency (%) | Efficiency (%) |
| 15 | 98.10 | 97.86 |  | 15 | 97.50 | 97.18 |  |
| 25 | 98.33 | 98.12 |  | 30 | 97.90 | 97.63 |  |
| 37.5 | 98.49 | 98.30 |  | 45 | 98.10 | 97.86 |  |
| 50 | 98.60 | 98.42 |  | 75 | 98.33 | 98.13 |  |
| 75 | 98.73 | 98.57 | 98.53 | 112.5 | 98.52 | 98.36 |  |
| 100 | 98.82 | 98.67 | 98.63 | 150 | 98.65 | 98.51 |  |
| 167 | 98.96 | 98.83 | 98.80 | 225 | 98.82 | 98.69 | 98.57 |
| 250 | 99.07 | 98.95 | 98.91 | 300 | 98.93 | 98.81 | 98.69 |
| 333 | 99.14 | 99.03 | 98.99 | 500 | 99.09 | 98.99 | 98.89 |
| 500 | 99.22 | 99.12 | 99.09 | 750 | 99.21 | 99.12 | 99.02 |
| 667 | 99.27 | 99.18 | 99.15 | 1000 | 99.28 | 99.20 | 99.11 |
| 833 | 99.31 | 99.23 | 99.20 | 1500 | 99.37 | 99.30 | 99.21 |
|  |  |  |  | 2000 | 99.43 | 99.36 | 99.28 |
|  |  |  |  | 2500 | 99.47 | 99.41 | 99.33 |

###### Deemed Lifetime of Efficient Equipment

30 years

###### Deemed Measure Cost

Actual incremental costs should be used.

###### Loadshape

Use custom loadshape based on application; default loadshape is Loadshape C67 (Ameren) or C68 (ComEd), which represent overall utility system loads.

###### Coincidence Factor

Coincidence Factor for distribution transformers is 1.0 by definition. By including the load factor in the demand savings calculation, the load profile is accounted for.

Algorithm

###### Calculation of Energy Savings

Savings are determined by metering equipment

###### Electric Energy Savings

ΔkWh 	= Lossesbase – LossesEE

Where:

Lossesbase =PowerRating* LF*PF* 1EFFbase-1* 8766

LossesEE =PowerRating* LF*PF* 1EFFEE-1* 8766

PowerRating 	= kVA rating of the transformer (in units of kVA)

EFFbase 	= baseline total efficiency rating of federal minimum standard transformer (refer to baseline tables above based on kVA, voltage, and type of transformer)

EFFEE 	= actual total efficiency rating of the transformer as calculated by the appropriate DOE test method.

LF 	= Load Factor for the transformer. Ratio of average transformer load to peak load rating over a period of one year. Use actual load factor for the network segment served based on historical data. If unknown, use 22% for commercial load and 45% for industrial load.

PF 	= Power Factor for the load being served by the transformer. Ratio of real power to apparent power supplied to the transformer. Use actual power factor for the network segment served. If unknown, use 1.0 (unity) by default.

###### Summer Coincident Peak Demand Savings

ΔkW=PowerRating* LF*PF* 1Effbase-1EffEE

Variables as provided above.

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-TRNS-V03-220101

###### Review Deadline: 1/1/2025

### High Frequency Battery Chargers

###### Description

This measure applies to industrial high frequency battery chargers, used for industrial equipment such as fork lifts, replacing existing SCR (silicon controlled rectifier) or ferroresonant charging technology.  High frequency battery chargers have a greater system efficiency.

This measure was developed to be applicable to the following program types: TOS, NC.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

High frequency battery charger systems with minimum Power Conversion Efficiency of 90% and a minimum 8-hour shift operation five days per week.

###### Definition of Baseline Equipment

SCR or ferroresonant battery charger systems with minimum 8-hour shift operation five days per week.

###### Deemed Lifetime of Efficient Equipment

15 years

###### Deemed Measure Cost

The deemed incremental measure cost is $400.

###### Loadshape

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

###### Coincidence Factor

The coincidence factor is assumed to be 0.0 for 1 and 2-shift operation and 1.0 for 3 and 4-shift operation.

Algorithm

###### Electric Energy Savings

∆kWh	= (CAP * DOD) * CHG * (CRB / PCB - CREE / PCEE)

Where:

CAP 	= Capacity of Battery

= Use actual battery capacity, otherwise use a default value of 35 kWh

DOD	= Depth of Discharge

= Use actual depth of discharge, otherwise use a default value of 80%.

CHG 	= Number of Charges per year

= Use actual number of annual charges, if unknown use values below based on the type of operations

| Standard Operations | Number of Charges per year |
| --- | --- |
| 1-shift (8 hrs/day – 5 days/week) | 520 |
| 2-shift (16 hrs/day – 5 days/week) | 1040 |
| 3-shift (24 hrs/day – 5 days/week) | 1560 |
| 4-shift (24 hrs/day – 7 days/week) | 2184 |

CRB 	= Baseline Charge Return Factor

= 1.2485

PCB 	= Baseline Power Conversion Efficiency

= 0.84

CREE 	= Efficient Charge Return Factor

= 1.107

PCEE 	= Efficient Power Conversion Efficiency

= 0.89

Default savings using defaults provided above are provided below:

| Standard Operations | ΔkWh |
| --- | --- |
| 1-shift (8 hrs/day – 5 days/week) | 3,531 |
| 2-shift (16 hrs/day – 5 days/week) | 7,061 |
| 3-shift (24 hrs/day – 5 days/week) | 10,592 |
| 4-shift (24 hrs/day – 7 days/week) | 14,829 |

###### Summer Coincident Peak Demand Savings

∆kW	= (PFB/PCB - PFEE/PCEE) * VoltsDC * AmpsDC / 1000 * CF

Where:

PFB	= Power factor of baseline charger

= 0.9095

PFEE	= Power factor of high frequency charger

= 0.9370

VoltsDC	= Actual DC rated voltage of charger (assumed baseline charger is replaced with same rated high frequency unit)

= Use actual battery DC voltage rating, otherwise use a default value of 48 volts.

AmpsDC	= Actual DC rated amperage of charger (assumed baseline charger is replaced with same rated high frequency unit)

= Use actual battery DC ampere rating, otherwise use a default value of 81 amps.

1,000 	= watt to kilowatt conversion factor

CF 	= Summer Coincident Peak Factor for this measure

= 0.0 (for 1 and 2-shift operation)

= 1.0 (for 3 and 4-shift operation)

Other variables as provided above.

Default savings using defaults provided above are provided below:

| Standard Operations | ∆kW |
| --- | --- |
| 1-shift (8 hrs/day – 5 days/week) | 0 |
| 2-shift (16 hrs/day – 5 days/week) | 0 |
| 3-shift (24 hrs/day – 5 days/week) | 0.1165 |
| 4-shift (24 hrs/day – 7 days/week) | 0.1165 |

###### Natural Gas Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-BACH-V02-210101

###### Review Deadline: 1/1/2025

### Commercial Clothes Dryer Moisture Sensor

###### Description

This measure applies to moisture sensing controllers installed on new or existing commercial natural gas clothes dryers controlled electronically. Moisture controllers detect when the load is dry, which will stop the cycle from consuming additional energy. Some new commercial dryers utilize moisture sensors, but the majority of older dryers, as well as many new models, still do not utilize moisture sensors. In a commercial dyer, when a load is drying, the heat will run completely on in the early stages. Then, it begins to cycle on and off more frequently as the load becomes drier. Traditional moisture sensors use a conductivity strip in the dryer drum. The wet load will contact the strip that completes the circuit. When the load is dry, the circuit is shorted that completes the drying cycle. Instead, this technology is a “plug and play” retrofit controller that uses patent-pending software to determine when the load is dry. When the load is dry, it overrides the existing controls to end the cycle, which shuts the drying cycle. This measure does not apply to mechanical timer dryers or to dryers with modulating valves installed.

Natural gas energy savings will be achieved by reduced drying times and correspondingly reduced natural gas consumption. Electric savings will also be achieved by reduced operating times.

This measure was developed to be applicable to following facility types:

- Hotel/Motel

- Miscellaneous - Fitness and Recreational Sports Centers

- Hospital

- Assisted Living Facilities

- Miscellaneous - Dry cleaning

- Multifamily

Moisture sensing controller retrofits could create significant energy savings opportunities at other larger facility types with on-premise laundry operations (such as correctional facilities, universities, and staff laundries); however, the results included in this analysis are based heavily on past project data for the applicable facility types listed above and may not apply to facilities outside of this list due to variances in number of loads and average pound (lbs.) capacity per project site. Projects at these facilities should continue to be evaluated through custom programs and the applicable facility types and the resulting analysis should be updated based on new information.

This measure was developed to be applicable to the following program types: RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

A retrofit moisture controlling technology is added to new or existing commercial natural gas clothes dryers. Existing facilities must be able to confirm that they do not have moisture sensors (conductive strip type) or modulating gas valves installed on clothes dryers already before proceeding with the installation of this technology.

###### Definition of Baseline Equipment

The baseline equipment is a conventional natural gas clothes dryer without a moisture sensor or a modulating gas valve installed.

###### Deemed Lifetime of Efficient Equipment

The equipment effective useful life (EUL) is 14 years based on manufacturer claims, assumed to be equal to that of a commercial dryer.

###### Deemed Measure Cost

The full retrofit cost is assumed to be $600, including the material cost for the basic moisture control retrofit ($500) and the associated labor for installation ($100).

###### Loadshape

Loadshape C55; Commercial Clothes Washer

###### Coincidence Factor

The coincidence factor for this measure is dependent on the application:

| Application | Coincidence Factor |
| --- | --- |
| Multi-family Dryers | 0.15 |
| On-Premise Laundromats | 0.52 |

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Electric energy savings are per retrofitted dryer.

ΔkWh		= NCycles * SF

Where:

NCycles 	= Number of dryer cycles per year. Refer to the table below if this value is not directly available from the facility.

| Application | Cycles per Dryer Per Year |
| --- | --- |
| Multi-family Dryers | 1,074 |
| On-Premise Laundromats | 3,607 |

SF		= Savings factor

= 0.16 kWh/cycle

If using default cycles the savings are as follows:

| Application | ΔkWh per Dryer |
| --- | --- |
| Multi-family Dryers | 171.8 |
| On-Premise Laundromats | 577.1 |

###### Summer Coincident Peak Demand Savings

ΔkW		= ΔkWh/ Hours * CF

Where:

Hours		= Assumed Run hours of Clothes Dryer

| Application | Hours |
| --- | --- |
| Multi-family Dryers | 806 |
| On-Premise Laundromats | 2,705 |

CF 		= Summer Peak Coincidence Factor for measure.

| Application | Coincidence Factor |
| --- | --- |
| Multi-family Dryers | 0.15 |
| On-Premise Laundromats | 0.52 |

If using default cycles the savings are as follows:

| Application | ΔkW per Dryer |
| --- | --- |
| Multi-family Dryers | 0.0320 |
| On-Premise Laundromats | 0.1109 |

###### Natural Gas Savings

Natural gas savings are per retrofitted dryer.

ΔTherms	= NCycles * SF

Where:

SF	= Savings factor

= 0.15 therms/cycle

If using default cycles the savings are as follows:

| Application | ΔTherms per Dryer |
| --- | --- |
| Multi-family Dryers | 161 |
| On-Premise Laundromats | 541 |

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-CDMS-V01-190101

###### Review Deadline: 1/1/2023

### Efficient Thermal Oxidizers

###### Description

Thermal Oxidizers are used to destroy volatile organic compounds (VOCs) from process exhausts, before emitting the treated air to the environment. VOC emissions are precursors to the formation of ground-level ozone pollution, and its control is mandated by the U.S. EPA.  Some VOC constituents are individually toxic and require efficient destruction. Some waste streams have high enough concentrations to present an explosion hazard. Other waste streams merely present nuisance odors that need to be mitigated.

A facility may be required to utilize a Thermal Oxidizer by a state regulatory agency air quality permit. Some permits may require a VOC destruction efficiency that must be demonstrated with periodic emissions testing. Other permits merely require maintaining an oxidizer chamber temperature. A facility may also choose to utilize a Thermal Oxidizer for other purposes (nuisance odors), without a regulatory requirement.

The Efficient Thermal Oxidizer measure seeks to evaluate natural gas savings from utilizing more efficient means for VOC destruction with the use of a recuperative or regenerative thermal oxidizer. The heat recovery (either Recuperative or Regenerative) is used to pre-heat the inlet process air stream. This primary heat recovery is used within the thermal oxidizer process and the only heat recovery that is covered in this measure protocol. Natural gas savings will result from reduced burner firing. There is a “secondary” form of heat recovery that recovers heat from the combustion exhaust stack for other purposes like space heating, DHW heating, etc.

###### Definition of Efficient Equipment

Two Thermal Oxidizer technologies can be considered as efficient equipment: Recuperative and Regenerative.

Recuperative Thermal Oxidizer

In a Recuperative Thermal Oxidizer, the exhaust air stream is sent through a heat exchanger to indirectly pre-heat the inlet air stream coming from the process. The heat exchanger efficiency for a recuperator is typically 50-70%. The chamber temperature is typically 1400 oF to 1500 oF.

Regenerative Thermal Oxidizer

A Regenerative Thermal Oxidizer utilizes a two-chamber ceramic bed as its heat exchanger system. The exhaust air passes through one bed, imparting its heat onto the ceramic media, while the intake air passes through the other bed, capturing the waste heat from the previous cycle. The flow reverses every few minutes so that the intake bed becomes the exhausted bed and vice versa. The heat exchanger efficiency of a regenerative system is much higher than a recuperative system. These efficiencies can reach 85% to 97%. However, the ceramic media needs to be periodically cleaned or replaced. The chamber temperatures in Regenerative Thermal Oxidizers are typically 1,500 oF to 1,600 oF (depending on VOC requirements).

###### Definition of Baseline Equipment

Depending on the facility process, there may be two baseline selection options: incinerator or recuperator.

The baseline Thermal Oxidizer with no heat recovery is referred to as an Incinerator. This baseline is recommended for selection if it currently exists on site or in new construction when there is a specific process that cannot practically utilize a recuperator due to VOCs coating or clogging the heat exchanger.  This system employs a burner to provide direct fire to a process exhaust air stream. Typical operative temperatures are 1400 oF to 2200 oF. The advantage of an afterburner is a quick startup and shutdown time that is ready on demand. The equipment cost is lower than the efficient equipment, but the fuel consumption is much higher.

In all other cases, (existing equipment is recuperative or new construction/ expansion of manufacturing process), a recuperative thermal oxidizer is recommended as the appropriate baseline.

###### Deemed Lifetime of Efficient Equipment

The expected useful life of any thermal oxidizer system is assumed to 20 years.

###### Deemed Measure Cost

The cost of any thermal oxidizer is dependent on various variables such as air flow capacity, destruction efficiency, heat exchanger efficiency, etc. Shown below is an example of a system for 20,000 CFM.

Recuperative Thermal Oxidizer costs, based on their heat recovery efficiency, is detailed in the table below.

| Heat Recovery Efficiency | Equipment Cost |
| --- | --- |
| 0% | $106,042 |
| 35% | $174,193 |
| 50% | $203,801 |
| 70% | $253,801 |
| Average | $184,317 |

Regenerative Thermal Oxidizer, at 95% heat recovery, have a deemed cost of $546,000.

Incinerator cost is treated as 0% heat recovery in the Recuperative Cost summary table above, and has a deemed cost of $106,042.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

Energy savings from thermally efficient equipment are entirely natural gas related. There are no electricity savings nor peak demand savings, as the blower fans and valve actuators are assumed to operate the same in all conditions.

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

ΔTherms = ((Baseline QT Air Pollution Control Device - Proposed QT Air Pollution Control Device) x Hours) / LHV

Where:

LHV 	=  Latent Heat of Vaporization

= If the post is regenerative thermal oxidizer, LHV = 0.953.

= If the post is recuperative thermal oxidizer, LHV = 1.

Regenerative or Recuperative: A baseline or proposed Regenerative or Recuperative Air Pollution Control Device can each be modeled in the following heat balance equation:

QT (BTU/hr) = QI + QCC + QRL – QVOC

Incinerator: A baseline incinerator Air Pollution Control Device can be modeled as the following heat balance equation:

QT (BTU/hr) = QI + QCC + QRL

Where:

QT = Total Energy Input

QI = Energy used to raise the temperature of process air (FI) in BTU/hr

QCC = Heat used to raise the temperature of combustion air (FCC)

QRL = Radiation heat loss from RTO (BTU/hr)

QVOC = Heat release provided by VOC combustion

Hours = Annual hours per year that Oxidizer is used

Where:

QI = FI X 1.08 x (TO – TI)

TO = Average stack outlet temperature (°F) (actual trended average or use efficiency equation below to solve for TO under assumed conditions)

TO = TC - (N X (TC - TI) X FI / (FI + FCC)

TC = Combustion chamber temperature (°F), trended or design value provided by the manufacturer

N = Thermal Efficiency of Heat Exchanger

| Thermal Oxidizer | Efficiency |
| --- | --- |
| Regenerative | 97% |
| Recuperative | 70% |
| Incinerator | 0% |

TI = Inlet air temperature (°F), this is the temperature of the air coming from the process

FI = Process air (CFM), actual loading or use maximum design value

1.08 = Conversion Factor

= 60 (min/hr) x 0.07489 (lb/ft3, density air at standard conditions) x 0.2404 Btu/°F-lb, (specific heat of air), where 0.2404 is average heat capacity of intake air

Where:

QCC = FCC X 1.08 X (TO – TA)

FCC = Additional combustion air CFM at provided FI value

= If unknown, assume 3% of design value

TO = Average outlet temperature (°F) (same as above)

TA = Combustion intake air temperature (°F)

= Indoor: Actual, or assume 70 °F year-round

= Outdoor: Actual annual average found near the facility, or assume TMY3 annual averages:

| Region / Area | Average Outdoor Air Temperature |
| --- | --- |
| Chicago O'Hare | 50.0 °F |
| Chicago Midway | 52.5 °F |
| Rockford Airport | 47.6 °F |

Where:

QRL = SA x BTU/hr radiant loss

SA = Surface Area (provided by the manufacturer or rough measurements taken)

BTU/hr radiant loss = Assume 240 BTU/hr if installed outdoors, otherwise, 0 BTU/hr for indoor installation since the waste heat provides space heating and offset gas-fired space heating equipment

Where:

QVOC = VOC X HC X (% Dest / 100)

VOC = Average lbs/hr from process to oxidizer

HC = Btu/lb, weighted average for the heat of combustion of VOCS

= Site-specific, lookup table

% Destruction = Destruction efficiency of VOCs provided by the manufacturer, or use:

Hours = Annual hours of operation of the air pollution control device, assume customer production schedule or hours of occupancy

LHV = Lower heating value of natural gas

= 983 BTU/CF

HHV = High heating value of natural gas

= 1,031 BTU/CF

0.953 = LHV / HHV conversion factor

To calculate the natural gas savings by upgrading from an incinerator to an Efficient Thermal Oxidizer system, the new temperatures must be considered. The addition of heat recovery (either Recuperative or Regenerative) will increase the inlet temperature, TI, above that found in the facility.

The calculation should consider changes in the inlet temperature. First, the key temperature required for 99.99% destruction efficiency of various VOC compounds must be determined. The U.S. EPA’s Innovative Strategies and Economics Group produced some guidance on the key temperatures for the following compounds:

| VOC Compound | Key Destruction Temperature (°F) |
| --- | --- |
| Acrylonitrile | 1,344 |
| Allyl chloride | 1,276 |
| Benzene | 1,350 |
| Chlorobenzene | 1,407 |
| 1,2 – dichloromethane | 1,368 |
| Methyl chloride | 1,596 |
| Toluene | 1,341 |
| Vinyl chloride | 1,369 |

For VOC compounds not listed above, the Key Destruction Temperature should be determined through product literature, equipment vendors, Material Data Safety Sheets (MSDS), or some other source.

When employing heat recovery, either Recuperative or Regenerative, the increased outlet temperature is limited to the heat exchanger efficiency. This efficiency, or in other words how much heat can be recovered, is limited to the auto-ignition temperatures of the VOCs in the air stream. Regenerative Thermal Oxidizers offer the advantage of recovering more heat as the combustion can occur within the heat exchanger, whereas with Recuperative Thermal Oxidizers, the heat exchanger efficiency is much lower to prevent premature combustion in the stack of the recuperator.

While the VOCs in the waste air stream have some heating value that contributes to reaching the required chamber temperature, such contributions do not have as high of an impact in the overall energy consumption calculation when compared to the heat exchanger efficiency.

###### Water and Other Non-Energy Impact Descriptions and Calculation

Thermal oxidizer operations will have no impact on water or other resources. There may be some safety issues with potential burning hazards from deploying this equipment at high temperatures. There may also be some potential issues with installing outdoor natural gas piping to the location of the Thermal Oxidizers. In terms of physical sizing, regenerative thermal oxidizers are much larger, thus requiring larger physical space at the site of installation.

###### Deemed O&M Cost Adjustment Calculation

The ceramic media in the regenerative thermal oxidizer requires regular servicing and may need to be considered as a regular part of facility O&M.

###### Measure Code: CI-MSC-ETOX-V01-190101

###### Review Deadline: 1/1/2023

### Spring-Loaded Garage Door Hinge

###### Description

Existing overhead doors often close loosely at the perimeter weather strips and between panels. Conditioned air escapes through these gaps, leading to energy loss. Spring-loaded hinges create tension and reduce gaps at the perimeter and between panels. The product is applicable for small-commercial and residential sectors, but the savings estimated by this measure apply only to small-commercial applications. This measure applies to sites where the inside area of the garage is conditioned during the heating season by natural gas.

This measure was developed to be applicable to the following program types: NC, RF.  If applied to other program types, the measure savings should be verified as a custom measure.

###### Definition of Efficient Equipment

The efficient equipment consists of a heavy-duty spring-loaded hinge installed in place of a standard hinge on a garage overhead door. The number of hinges per project may vary depending on the door type, size, and number of panels. The efficient condition is an air sealed garage door with no gaps around the perimeter or between panels.

###### Definition of Baseline Equipment

The baseline equipment is a garage door with a 1/8-inch gap between the door and the weather-stripping around the perimeter of the door. The bottom of the door is assumed sealed.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 20 years.

###### Deemed Measure Cost

Incremental costs equal installed cost and will vary based on the number of hinges required per door. Based on information provided by the manufacturer to Nicor Gas, average material cost is $126 per garage door and installation cost is $63 per garage door for a total installed cost of $189 per garage door. The typical garage door is assumed  to have 4 panels and 9 total hinges.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

Savings are calculated based on a reduction in airflow rate associated with decreased infiltration across the leakage area. The algorithm below for change in cubic feet per minute, ∆CFM, is modeled after equation 48 in Chapter 16: Ventilation and infiltration of the 2017 ASHRAE Handbook—Fundamentals.

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

∆CFM= Al*Cs*∆T+Cw*Ws20.5

∆HeatLoad= ∆CFM*Convmin* Densityair*SpecificHeatair*∆T

∆thermsHr= ∆HeatLoad/Effheat/ConvBTU

∆thermsAnn= ∆thermsHr* Hours

Where:

Al 	= Leakage area, estimated at 51 (in2), of air gap before retrofit.

Cs 	= Stack coefficient, 0.0299 (cfm 2/in4*°F), adjustment based on airflow at average building height.

Cw 	= Wind coefficient, 0.0086 (cfm 2/in4*mph2), adjustment based on airflow at average building height and wind shelter classification.

∆T 	= Average temperature difference between outside air temperature (OAT) during the heating season  and assumed indoor heating temperature setpoint 70°F; see table below.

Ws 	= Average wind speed (mph) during heating season, see table below.

| Climate Zone | Average OAT, Heating (°F) | Average Delta T, Heating (°F) | Average heating Season Wind Speed (mph) |
| --- | --- | --- | --- |
| 1 (Rockford) | 32 | 38 | 10 |
| 2 (Chicago) | 34 | 36 | 10 |
| 3 (Springfield) | 35 | 35 | 10 |
| 4 (Belleville) | 36 | 34 | 9 |
| 5 (Marion) | 39 | 31 | 7 |

Convmin 	= Conversion from minutes to hours, 60 minutes/hour.

Densityair	= The density of air, 0.08 (lb/ft3) at 1 atmosphere pressure and approximately 30-40°F.

SpecificHeatair		= Specific heat of air, 0.24 (BTU/lb) at 1 atmosphere pressure and 32°F.

Effheat		= Efficiency of the heating system, assume 0.78 for planning purposes.

ConvBTU 	= Conversion from BTUs to therms, 100,000 BTU/therm.

EFLHH 	=Equivalent Full Load Heating Hours in Existing Buildings or New Construction are listed in section 4.4 HVAC End Use, but a subset of the building types most likely to use this measure are repeated here for easy reference.

| EFLH Existing Buildings |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 1,481 | 1,368 | 1,214 | 871 | 973 |
| Garage | 958 | 969 | 852 | 680 | 1,047 |
| High School | 1,845 | 1,857 | 1,666 | 1,187 | 1,388 |
| Manufacturing | 1,048 | 1,013 | 939 | 567 | 634 |
| Office - Low Rise | 1,428 | 1,425 | 1,132 | 692 | 793 |
| Retail - Strip Mall | 1,347 | 1,325 | 1,183 | 1,064 | 1,096 |
| Warehouse | 1,285 | 1,286 | 1,180 | 1,147 | 1,224 |

| EFLH New Construction |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 1,481 | 1,368 | 1,214 | 871 | 973 |
| Garage | 958 | 969 | 852 | 680 | 1,047 |
| High School | 1,807 | 1,642 | 2,093 | 2,292 | 1,830 |
| Manufacturing | 1,048 | 1,013 | 939 | 567 | 634 |
| Office - Low Rise | 947 | 989 | 1,090 | 1,302 | 1,076 |
| Retail - Strip Mall | 722 | 789 | 667 | 834 | 911 |
| Warehouse | 389 | 522 | 408 | 527 | 567 |

Savings for all climate zones and selected building types are presented in the following table.

| Annual Therm Savings Existing Buildings |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 59.89 | 51.62 | 44.19 | 29.20 | 26.38 |
| Garage | 38.74 | 36.56 | 31.01 | 22.79 | 28.39 |
| High School | 74.61 | 70.07 | 60.64 | 39.79 | 37.63 |
| Manufacturing | 42.38 | 38.22 | 34.18 | 19.01 | 17.19 |
| Office - Low Rise | 57.75 | 53.77 | 41.21 | 23.20 | 21.50 |
| Retail - Strip Mall | 54.47 | 50.00 | 43.06 | 35.67 | 29.72 |
| Warehouse | 51.97 | 48.53 | 42.95 | 38.45 | 33.19 |

| Annual Therm Savings New Construction |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 59.89 | 51.62 | 44.19 | 29.20 | 26.38 |
| Garage | 38.74 | 36.56 | 31.01 | 22.79 | 28.39 |
| High School | 73.08 | 61.96 | 76.19 | 76.83 | 49.62 |
| Manufacturing | 42.38 | 38.22 | 34.18 | 19.01 | 17.19 |
| Office - Low Rise | 38.30 | 37.32 | 39.68 | 43.64 | 29.17 |
| Retail - Strip Mall | 29.20 | 29.77 | 24.28 | 27.96 | 24.70 |
| Warehouse | 15.73 | 19.70 | 14.85 | 17.67 | 15.37 |

Savings for all climate zones and selected building types per linear foot are presented in the following table.

| Annual Therm Savings per Linear Foot Existing Buildings |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 1.76 | 1.52 | 1.30 | 0.86 | 0.78 |
| Garage | 1.14 | 1.08 | 0.91 | 0.67 | 0.83 |
| High School | 2.19 | 2.06 | 1.78 | 1.17 | 1.11 |
| Manufacturing | 1.25 | 1.12 | 1.01 | 0.56 | 0.51 |
| Office - Low Rise | 1.70 | 1.58 | 1.21 | 0.68 | 0.63 |
| Retail - Strip Mall | 1.60 | 1.47 | 1.27 | 1.05 | 0.87 |
| Warehouse | 1.53 | 1.43 | 1.26 | 1.13 | 0.98 |

| Annual Therm Savings per Linear Foot New Construction |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 1.76 | 1.52 | 1.30 | 0.86 | 0.78 |
| Garage | 1.14 | 1.08 | 0.91 | 0.67 | 0.83 |
| High School | 2.15 | 1.82 | 2.24 | 2.26 | 1.46 |
| Manufacturing | 1.25 | 1.12 | 1.01 | 0.56 | 0.51 |
| Office - Low Rise | 1.13 | 1.10 | 1.17 | 1.28 | 0.86 |
| Retail - Strip Mall | 0.86 | 0.88 | 0.71 | 0.82 | 0.73 |
| Warehouse | 0.46 | 0.58 | 0.44 | 0.52 | 0.45 |

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-SLDH-V01-200101

###### Review Deadline: 1/1/2023

### Variable Speed Drives for Process Fans

###### Description

This measure is applied to variable speed drives (VSD) which are installed on non-HVAC fans for process loads. There are separate measures for HVAC pumps and cooling tower fans (4.4.17) and HVAC supply and return fans (4.4.26). VSD process pump applications require custom analysis by the program administrator. The VSD will modulate the speed of the motor when it does not need to run at full load. Since the power of the motor is proportional to the cube of the speed for these types of applications, significant energy savings will result.

This measure was developed to be applicable to the following program types: TOS, RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The VSD is applied to a motor which does not have a VSD. The application must have a variable load and installation is to include the necessary controls.  Savings are based on application of VSDs to a range of baseline load conditions including no control, inlet guide vanes, outlet guide vanes and throttling valves.

###### Definition of Baseline Equipment

The time of sale baseline is a new motor installed without a VSD or other methods of control.  Retrofit baseline is an existing motor operating without a method of variable control.  This information shall be collected from the customer.

Installations of new equipment with VSDs which are required by IECC 2012 or 2015 as adopted by the State of Illinois are not eligible for incentives.

Note IECC 2018 became effective July 1, 2019 and is the baseline for all New Construction permits from that date.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is 15 years.

###### Deemed Measure Cost

The costs vary based on the motor horsepower and application. Actual costs should be used.

###### Loadshape

Time-based schedule considerations are required to perform energy savings calculations and should be concurrently used to establish the savings loadshape that is in alignment with relevant loadshape components and definitions.

###### Coincidence Factor

The demand savings factor (DSF) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

| kWhBase = | 0.746×HP×LFηmotor×RHRS×0%100%%FF×PLRBase |
| --- | --- |
| kWhRetrofit = | 0.746×HP×LFηmotor×RHRS ×0%100%%FF×PLRRetrofit |
| ESF = | (kWhBase-kWhRetrofit)/kWhBase |
| ∆kWhtotal = | kWhBase× ESF |

Where:

kWhBase 	= Baseline annual energy consumption (kWh/yr)

kWhRetrofit 	= Retrofit annual energy consumption (kWh/yr)

ESF 	= Energy savings factor; If ESF is greater than 67%, cap the ESF at 67% for process fan VSD improvements.

∆kWhtotal 	= Total project annual energy savings

0.746 		= Conversion factor for HP to kWh

HP		= Nominal horsepower of controlled motor

LF 		= Load Factor; Motor Load at Fan Design CFM (Default = 65%)

ηmotor		= Installed nominal/nameplate motor efficiency

Default motor is a NEMA Premium Efficiency, ODP, 4-pole/1800 RPM fan motor

NEMA Premium Efficiency Motors Default Efficiencies

| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | # of Poles |  |  | # of Poles |  |  |
|  | 6 | 4 | 2 | 6 | 4 | 2 |
|  | Speed (RPM) |  |  | Speed (RPM) |  |  |
|  | 1200 | 1800 Default | 3600 | 1200 | 1800 | 3600 |
| 1 | 0.825 | 0.855 | 0.770 | 0.825 | 0.855 | 0.770 |
| 1.5 | 0.865 | 0.865 | 0.840 | 0.875 | 0.865 | 0.840 |
| 2 | 0.875 | 0.865 | 0.855 | 0.885 | 0.865 | 0.855 |
| 3 | 0.885 | 0.895 | 0.855 | 0.895 | 0.895 | 0.865 |
| 5 | 0.895 | 0.895 | 0.865 | 0.895 | 0.895 | 0.885 |
| 7.5 | 0.902 | 0.910 | 0.885 | 0.910 | 0.917 | 0.895 |
| 10 | 0.917 | 0.917 | 0.895 | 0.910 | 0.917 | 0.902 |
| 15 | 0.917 | 0.930 | 0.902 | 0.917 | 0.924 | 0.910 |
| 20 | 0.924 | 0.930 | 0.910 | 0.917 | 0.930 | 0.910 |
| 25 | 0.930 | 0.936 | 0.917 | 0.930 | 0.936 | 0.917 |
| 30 | 0.936 | 0.941 | 0.917 | 0.930 | 0.936 | 0.917 |
| 40 | 0.941 | 0.941 | 0.924 | 0.941 | 0.941 | 0.924 |
| 50 | 0.941 | 0.945 | 0.930 | 0.941 | 0.945 | 0.930 |
| 60 | 0.945 | 0.950 | 0.936 | 0.945 | 0.950 | 0.936 |
| 75 | 0.945 | 0.950 | 0.936 | 0.945 | 0.954 | 0.936 |
| 100 | 0.950 | 0.954 | 0.936 | 0.950 | 0.954 | 0.941 |
| 125 | 0.950 | 0.954 | 0.941 | 0.950 | 0.954 | 0.950 |
| 150 | 0.954 | 0.958 | 0.941 | 0.958 | 0.958 | 0.950 |
| 200 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.954 |
| 250 | 0.954 | 0.958 | 0.950 | 0.958 | 0.962 | 0.958 |
| 300 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 350 | 0.954 | 0.958 | 0.954 | 0.958 | 0.962 | 0.958 |
| 400 | 0.958 | 0.958 | 0.958 | 0.958 | 0.962 | 0.958 |
| 450 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |
| 500 | 0.962 | 0.962 | 0.958 | 0.958 | 0.962 | 0.958 |

RHRS	= Annual operating hours of process fan. Actual hours should be used.

%FF		= Percentage of run-time spent within a given flow fraction range.

Fans used in process applications operate under site-specific conditions. The percentage of run-time spent within each of the given ranges in the table below should be field collected.

| Flow Fraction (% of design cfm) | Percent of Time at Flow Fraction |
| --- | --- |
| 0% to 10% | Field Collected for each bin. |
| >10% to 20% |  |
| >20% to 30% |  |
| >30% to 40% |  |
| >40% to 50% |  |
| >50% to 60% |  |
| >60% to 70% |  |
| >70% to 80% |  |
| >80% to 90% |  |
| >90% to 100% |  |

PLRBase	= Part load ratio for a given flow fraction range based on the baseline flow control type

PLRRetrofit	= Part load ratio for a given flow fraction range based on the retrofit flow control type

| Control Type | Flow Fraction |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0-10% | >10% to 20% | >20% to 30% | >30% to 40% | >40% to 50% | >50% to 60% | >60% to 70% | >70% to 80% | >80% to 90% | >90% to 100% |
| No Control or Bypass Damper | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Discharge Dampers | 0.46 | 0.55 | 0.63 | 0.70 | 0.77 | 0.83 | 0.88 | 0.93 | 0.97 | 1.00 |
| Outlet Damper, BI & Airfoil Fans | 0.53 | 0.53 | 0.57 | 0.64 | 0.72 | 0.80 | 0.89 | 0.96 | 1.02 | 1.05 |
| Inlet Damper Box | 0.56 | 0.60 | 0.62 | 0.64 | 0.66 | 0.69 | 0.74 | 0.81 | 0.92 | 1.07 |
| Inlet Guide Vane, BI & Airfoil Fans | 0.53 | 0.56 | 0.57 | 0.59 | 0.60 | 0.62 | 0.67 | 0.74 | 0.85 | 1.00 |
| Inlet Vane Dampers | 0.38 | 0.40 | 0.42 | 0.44 | 0.48 | 0.53 | 0.60 | 0.70 | 0.83 | 0.99 |
| Outlet Damper, FC Fans | 0.22 | 0.26 | 0.30 | 0.37 | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06 |
| Eddy Current Drives | 0.17 | 0.20 | 0.25 | 0.32 | 0.41 | 0.51 | 0.63 | 0.76 | 0.90 | 1.04 |
| Inlet Guide Vane, FC Fans | 0.21 | 0.22 | 0.23 | 0.26 | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04 |
| VFD with duct static pressure controls | 0.09 | 0.10 | 0.11 | 0.15 | 0.20 | 0.29 | 0.41 | 0.57 | 0.76 | 1.01 |
| VFD with low/no duct static pressure | 0.05 | 0.06 | 0.09 | 0.12 | 0.18 | 0.27 | 0.39 | 0.55 | 0.75 | 1.00 |

0%100%%FF×PLR	= The sum of the product of the percentage of run-time spent within a given flow fraction range (%FF) and the part load ratio for a given flow fraction range based on the retrofit flow control type.

Example: A process fan with discharge damper controls operates 85% of the time at 75% flow fraction, 5% of the time at 80% flow fraction, and 10% of the time at 95% flow fraction:

0%100%%FF×PLR 	=  (0.85 x 0.93) + (0.05 x 0.97) + (0.10 x 1.00)

= 0.939%

###### Summer Coincident Peak Demand Savings

| kWBase = | 0.746×HP×LFηmotor×PLRBase, FFpeak |
| --- | --- |
| kWRetrofit = | 0.746×HP×LFηmotor× PLRRetrofit, FFpeak |
| ∆kWfan = | kWBase-kWRetrofit |

Where:

kWBase 		= Baseline summer coincident peak demand (kW)

kWRetrofit 		= Retrofit summer coincident peak demand (kW)

∆kWfan 		= Fan-only summer coincident peak demand impact

∆kWtotal 		= Total project summer coincident peak demand impact

PLRBase,FFpeak	= The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the baseline flow control type (default average flow fraction during peak period = 90%)

PLRRetrofit,FFpeak	= The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the retrofit flow control type (default average flow fraction during peak period = 90%)

###### Fossil Fuel Impact Descriptions and Calculation

There are no expected fossil fuel impacts for this measure.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-VSDP-V01-200101

###### Review Deadline: 1/1/2023

### Low Flow Toilets and Urinals

###### Description

Toilets and urinals are found in bathrooms located in commercial, and industrial facilities. The first federal standards dealing with water consumption for toilets and urinals was the Energy Policy Act of 1992. It specified a gallon per flush (gpf) standard for both fixtures. These standards are used to define the baseline equipment for this measure. The Subsequent U.S. EPA WaterSense program in 2009 set even tighter standards for plumbing fixtures, including toilets and urinals. These standards are used to define the efficient equipment for this measure.

###### Definition of Efficient Equipment

The high efficiency equipment is either a U.S. EPA WaterSense certified commercial toilet fixture or commercial urinal.

###### Definition of Baseline Equipment

The baseline equipment is a toilet or urinal that has a maximum gallons per flush outlined by the Energy Policy Act of 1992.

###### Deemed Lifetime of Efficient Equipment

The estimated useful life for this measure is assumed to be 25 years for both toilets and urinals.

###### Deemed Measure Cost

The incremental costs for both toilets and urinals are $0.

Loadshape

Loadshape C02 - Commercial Electric DHW

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

The following savings should be included in the total savings for this measure but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWh	 = 	ΔWater / 1,000,000 * Ewater total

Ewater	= IL Total Water Energy Factor (kWh/Million Gallons)

= 5,010

Toilet Calculation:

For example, a low flow toilet is installed in a commercial location.

ΔkWh = 491 gal/year / 1,000,000 * 5,010 kWh/million gallons

= 2.5 kWh/year

Urinal Calculation:

For example, a low flow urinal is installed in a commercial location.

ΔkWh = 2,340 gal/year / 1,000,000 * 5,010 kWh/million gallons

= 11.7 kWh/year

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

N/A

###### Water Impact Descriptions and Calculation

ΔWater	= (GPFBase - GPFEff) * NFPD * ADPY

Where:

GPFBase		= Baseline equipment gallons per flush

= 1.6 for toilets

= 1.0 for urinals

GPFEff		= Efficient equipment gallons per flush

= Actual, if unknown assume 1.28 for toilets

= Actual, if unknown assume 0.5 for urinals

NFPD		= Number of flushes per day

= 5.9 for toilets

= 18 for urinals,

ADPY		= Annual days per year

= 260 for commercial and industrial

Toilet Calculation:

For example, a low flow toilet is installed in a commercial location.

ΔWater =[(1.6 – 1.28 ) gal/flush x 5.9 flush/day x 260 days/year

= 491 gal/year

Urinal Calculation:

For example, a low flow urinal is installed in a commercial location.

ΔWater = (1.0 – 0.5) gal/flush x 18 flush/day x 260 days/year

= 2,340 gal/year

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-LFTU-V02-210101

###### Review Deadline: 1/1/2023

### Smart Irrigation Controls

###### Description

Irrigation systems are commonly found on commercial properties, educational institutions, public parks, golf courses, and other facilities with landscaped grounds. They are typically operated on timers, applying the irrigation water in the early morning or after dusk.  The timing and duration of irrigation application are determined by the user, along with the location and density of sprinklers. The irrigation water gets applied according to the control schedule, regardless of whether the landscape actually needs the irrigation water at that time.

The new measure involves the installation of a control system technology that reduces or eliminates irrigation during times of precipitation or when there is already sufficient soil moisture. This measure applies to landscape irrigation systems for commercial, institutional, and public properties only. It does not apply to agricultural irrigation systems for crops or residential landscape irrigation systems.

This measure was developed to be applicable to the following program types: TOS, RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Smart Irrigation Controls utilize sensors, gauges, or local weather forecasts to regulate the application of irrigation water to lawn or landscape vegetation. There are two main technologies used for this purpose: 1) Precipitation based smart irrigation controllers, and 2) Soil-moisture based smart irrigation controllers.

Precipitation Based Smart Irrigation Controllers

This type of system utilizes either an on-site rain gauge or a local weather service to determine if there is sufficient precipitation to allow shut-off of the irrigation water.

Soil Moisture Based Smart Irrigation Controllers

This type of system utilizes soil moisture sensors, buried in the root zone, to determine if irrigation water is needed. A “suspended cycle irrigation system” uses the soil moisture sensors to determine whether a regularly scheduled irrigation application is necessary. If there is sufficient soil moisture, then the next scheduled irrigation cycle gets interrupted. A “water-on-demand irrigation system” applies irrigation water when the moisture sensor reaches its lower limit and shuts off when the moisture sensor reaches its upper limit. There is no regularly scheduled irrigation with the water on demand system.

For the purposes of this measure characterization, the assumed rolling 24-hour threshold for shutting off the irrigation is 6 mm (0.24”). The Savings Factor is based on the percentage of time that the rolling 24-hour average of precipitation meets or exceed the 6 mm threshold.

###### Definition of Baseline Equipment

The baseline irrigation system applies irrigation water to the lawn or landscape on a regularly scheduled timer. The timing and duration of irrigation application are determined by the user, along with the location and density of sprinklers. The irrigation water gets applied according to the control schedule, regardless of whether the landscape actually needs the irrigation water at that time.

Sprinkler head nozzles have a variety of configurations that affect the distribution of the irrigation water. The water can come in the form of a spray, a rotating plume, a bubbler, or a drip.

Typical baseline irrigation systems provide 1 inch of irrigation to the entire lawn. This is equivalent to 0.623 gallons per square foot of lawn per week.

###### Deemed Lifetime of Efficient Equipment

The expected useful life for Irrigation Control Measures is assumed to be 15 years.

###### Deemed Measure Cost

The measure cost for a multi-zone smart irrigation control system is $500.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

Energy savings from Irrigation Control Measures are the result of reduced water consumption. There are indirect electric energy savings from reduced potable water treatment.

###### Electric Energy Savings

The electric energy savings are based indirectly on the reduced electricity usage used to provide the potable water and treat the wastewater. By applying an “Energy Factor”, the water savings (in gallons/year) can be converted to electricity savings (in kWh/year). This “Energy Factor” considers the electric energy requirements of potable water treatment plants and potable water distribution. Since the “wasted” irrigation water in the baseline case will likely be absorbed into the soil or will runoff into surface water bodies, electricity savings from a reduction in wastewater treatment load would not apply.

The methodology for quantifying the water savings involves a direct comparison of the baseline equipment to the efficient equipment. In order to calculate the baseline water usage of an irrigation system, the number of sprinklers and their sizing need to be determined. The static pressure and sizing of the water service, along with the sprinkler head orifice sizing will ultimately determine the flow rate of water.

The electricity savings for this measure can be calculated by applying an energy factor to the calculated water savings.

ΔkWhwater = ΔWater / 1,000,000 * Ewater

Where:

Ewater	 	= Illinois Total Water Energy Factor (kWh/Million Gallons)

=2,571

The total water savings for this measure can be calculated as follows:

ΔWater = BSFL – ESFL

Where:

ΔWater 	= Total Water Savings (gallon/season)

The baseline volumetric flow rate for the entire system can be calculated as follows:

BSFL = NOS x SFL x DOI x NAY

Where:

BSFL 		= Baseline System Flow Rate (gallon/year)

NOS 		= Number of Sprinklers, the total number of sprinklers at the property

= Actual

SFL   		= Sprinkler Flow Rate (gallon/minute)

= Actual, site-specific irrigation system specifications should be consulted to determine the property’s sprinkler flow rate

DOI  		= Duration of Irrigation (minutes/application)

= Actual, the baseline scheduling controls should be used to determine the irrigation season

NAY 		= Number of Applications per Year (application/year)

= Actual

The efficient volumetric flow rate can be calculated as follows:

ESFL = BSFL x (1 – SF)

Where:

ESFL 		= Efficient System Flow Rate (gallon/season)

BSFL 		= Baseline System Flow Rate (gallon/season)

SF 		= Savings Factor

The volumetric flow rate for the entire efficient system is based on applying a Savings Factor (SF) to the BSFL. The SF is determined by calculating the number of weeks in the irrigation season (April 25 through October 13) when there is sufficient precipitation to allow the shutoff of the irrigation system. Typical Meteorological Year (TMY-3) data gives precipitation depth in millimeters for each hour of the typical year. By consulting the TMY-3 data for the closest applicable weather station, the SF can be determined.

One source recommends a rain sensor shut-off threshold of 6 mm of precipitation for twice or thrice weekly irrigation schedule or 13 mm of precipitation for once weekly irrigation schedule. For the purposes of this workpaper, we will use a rolling 24-hour threshold of 6 mm.

The State Climatologist Office for Illinois produced a map of the Illinois Growing Season days per year for different parts of the state. Using a growing season average of 170 days, the “irrigation season” begins on April 25 and end on October 13.

By analyzing the TMY-3 precipitation data, the number of weeks during the “irrigation season” that the rolling 24-hour precipitation levels greater than 6 mm can be determined, along with the Savings Factors:

Chicago: 		SF = 0.265

Midway:			SF = 0.241

Rockford:		SF = 0.268

Peoria:			SF = 0.227

Springfield:		SF = 0.186

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

The water savings inherent in the efficient irrigation control technology will help preserve water supplies and extend the life of water treatment and wastewater treatment equipment. By reducing irrigation during periods of precipitation, unnecessary storm runoff and puddling can be avoided. For more details on calculating water savings, please see the ‘Algorithm’ section of this characterization.

###### Deemed O&M Cost Adjustment Calculation

Maintaining an Efficient Irrigation Control system will require periodic cleaning and calibration of the sensors. Any wiring or wireless communication devices will also need to be maintained. Costs for these activities is $196.

###### Measure Code: CI-MSC-SIRC-V02-220101

###### Review Deadline: 1/1/2025

### Commercial Weather Stripping

###### Description

Entrance/exit doors installed for a commercial or industrial buildings often leave clearance gaps to allow for proper operation. The gaps around the doors allow unconditioned air to infiltrate the building due to wind force, internal building stack affect, and other temperature differentials, thus adding to the cooling and heating loads of an HVAC system. Sweeps and other weather stripping applications are designed to close these gaps, while still allowing proper operation. They are installed along the bottom, head, and jambs of exterior doors to prevent air infiltration from adding to the HVAC load.

This measure was developed to be applicable to the following program types: RF, DI. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

There are a variety of types of materials used as door sweeps and weather stripping, including nylon bristles, felt, vinyl, open or closed-cell foam, and EPDM rubber. Their effectiveness is assumed to be the same when properly installed.

###### Definition of Baseline Equipment

This measure shall apply to the exterior doors on commercial buildings that are not sealed from the outside environment (i.e., interior vestibule doors would be ineligible) with visible gaps of at least 1/8 inches and up to 3/4 inches along any outside edge of the door. The space on the interior of the door must be conditioned and/or heated, and the calculation methodology will use standard efficiencies of 1.0 kW/ton for cooling and 80% for heating. Electric resistance heating and electric heat pump systems will use coefficients of performance (COPs) of 1.0 and 3.3, respectively.

###### Deemed Lifetime of Efficient Equipment

The estimated useful life (EUL) is 10 years.

###### Deemed Measure Cost

Costs for this measure should be determined by actual quotes obtained from manufacturers and estimated labor. If not available, it is estimated based on brush weather strips cost of $5.50/LF with labor and other direct costs of installation costing $2.50/LF with the total coming to $8.00/LF.

###### Loadshape

Loadshape C03 - Commercial Cooling

Loadshape C04 - Commercial Electric Heating

Loadshape C05 - Commercial Electric Heating and Cooling

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh	= ΔkWhweatherstrip  * Length

Where:

ΔkWhweatherstrip                    = Annual kWh savings from installation of door sweep per linear foot

| Climate Zone (City based upon) | ΔkWhweatherstrip per linear ft |  |
| --- | --- | --- |
|  | Electric Resistance | Heat Pump |
| 1 (Rockford) | 89.4 | 44.7 |
| 2 (Chicago) | 78.6 | 39.3 |
| 3 (Springfield) | 69.2 | 34.6 |
| 4 (Belleville) | 59.9 | 29.9 |
| 5 (Marion) | 48.0 | 24.0 |

Length                  = Linear feet of door weatherstipping installed

###### Summer Coincident Peak Demand Savings

Cooling savings have not been quantified for this measure.

###### Natural Gas Savings

ΔTherms              = ΔThermsweatherstrip * Length

Where:

ΔThermsweatherstrip                     = Annual therm savings from installation of door sweep per linear foot

| Climate Zone (City based upon) | ΔThermsweatherstrip per linear ft |
| --- | --- |
| 1 (Rockford) | 3.91 |
| 2 (Chicago) | 3.44 |
| 3 (Springfield) | 3.03 |
| 4 (Belleville) | 2.62 |
| 5 (Marion) | 2.1 |

Length                  = Linear feet of door weatherstripping installed

###### Water and Other Non-Energy Impact Descriptions and Calculation

NA

###### Deemed O&M Cost Adjustment Calculation

NA

###### Measure Code: CI-MSC-WTST-V01-200101

###### Review Deadline: 1/1/2023

### Switch Peripheral Equipment Consolidation

###### Description

This measure will allow for projects with small scopes of equipment replacement to be cost effectively brought into the telecommunication optimization incentive program.  Consolidating telecommunication line and trunk equipment eliminate underutilized equipment which reduces power draw from the rectifier. This avoided heat load also results in cooling savings.

This measure was developed to be applicable to the following program types: Telecommunication Optimization.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The measure requires no new equipment and only consolidates partially loaded equipment. There are a myriad of different types of line and trunk equipment, but consolidation eliminates underutilized equipment which will result in energy savings.

###### Definition of Baseline Equipment

Baseline telecommunications equipment is partially loaded line and trunk equipment that is no longer needed due to line loss on the telecommunications network. Lines are consolidated to like equipment and the underutilized equipment is removed. This applies to all line and trunk equipment and does not exclude participation from any particular type of line and trunk equipment. All line and trunk equipment are considered eligible but only up to and including 40 pieces of equipment. Above that amount, projects will require on-site amp reduction verification.

Baseline cooling equipment is assumed to be an Air-Cooled Chiller without an economizer with a capacity >240 MBtu. If cooling equipment can be verified, the chiller efficiency can be replaced with the appropriate value using Table 3.

ASHRAE 90.1 2016: Table 6.8.1-11

| Equipment Type | Net Sensible Cooling Capacity | Downflow units | Upflow - Ducted | Upflow - Unducted | Horizontal Flow |
| --- | --- | --- | --- | --- | --- |
|  |  | COP | COP | COP | COP |
| Air Cooled | < 65 MBtuh | 2.30 | 2.10 | 2.09 | 2.45 |
|  | > 65 MBtuh and < 240 MBtuh | 2.20 | 2.05 | 1.99 | 2.35 |
|  | > 240 MBtuh | 2.00 | 1.85 | 1.79 | 2.15 |
| Water Cooled | < 65 MBtuh | 2.50 | 2.30 | 2.25 | 2.70 |
|  | > 65 MBtuh and < 240 MBtuh | 2.40 | 2.20 | 2.15 | 2.60 |
|  | > 240 MBtuh | 2.25 | 2.10 | 2.05 | 2.45 |
| Water Cooled with Fluid Economizer | < 65 MBtuh | 2.45 | 2.25 | 2.20 | 2.60 |
|  | > 65 MBtuh and < 240 MBtuh | 2.35 | 2.15 | 2.10 | 2.55 |
|  | > 240 MBtuh | 2.20 | 2.05 | 2.00 | 2.40 |
| Glycol Cooled | < 65 MBtuh | 2.30 | 2.10 | 2.00 | 2.40 |
|  | > 65 MBtuh and < 240 MBtuh | 2.05 | 1.85 | 1.85 | 2.15 |
|  | > 240 MBtuh | 1.95 | 1.80 | 1.75 | 2.10 |
| Glycol Cooled with Fluid Economizer | < 65 MBtuh | 2.25 | 2.10 | 2.00 | 2.35 |
|  | > 65 MBtuh and < 240 MBtuh | 1.95 | 1.80 | 1.75 | 2.10 |
|  | > 240 MBtuh | 1.90 | 1.80 | 1.70 | 2.10 |

Converted ASHRAE 90.1 2016: Table 6.8.1-11 Cooling Efficiency Table

| Equipment Type | Net Sensible Cooling Capacity | Downflow units | Upflow - Ducted | Upflow - Unducted | Horizontal Flow |
| --- | --- | --- | --- | --- | --- |
|  |  | kW/Ton | kW/Ton | kW/Ton | kW/Ton |
| Air Cooled | < 65 MBtuh | 1.53 | 1.67 | 1.68 | 1.44 |
|  | > 65 MBtuh and < 240 MBtuh | 1.60 | 1.72 | 1.77 | 1.50 |
|  | > 240 MBtuh | 1.76 | 1.90* | 1.96 | 1.64 |
| Water Cooled | < 65 MBtuh | 1.41 | 1.53 | 1.56 | 1.30 |
|  | > 65 MBtuh and < 240 MBtuh | 1.47 | 1.60 | 1.64 | 1.35 |
|  | > 240 MBtuh | 1.56 | 1.67 | 1.72 | 1.44 |
| Water Cooled with Fluid Economizer | < 65 MBtuh | 1.44 | 1.56 | 1.60 | 1.35 |
|  | > 65 MBtuh and < 240 MBtuh | 1.50 | 1.64 | 1.67 | 1.38 |
|  | > 240 MBtuh | 1.60 | 1.72 | 1.76 | 1.47 |
| Glycol Cooled | < 65 MBtuh | 1.53 | 1.67 | 1.76 | 1.47 |
|  | > 65 MBtuh and < 240 MBtuh | 1.72 | 1.90 | 1.90 | 1.64 |
|  | > 240 MBtuh | 1.80 | 1.95 | 2.01 | 1.67 |
| Glycol Cooled with Fluid Economizer | < 65 MBtuh | 1.56 | 1.67 | 1.76 | 1.50 |
|  | > 65 MBtuh and < 240 MBtuh | 1.80 | 1.95 | 2.01 | 1.67 |
|  | > 240 MBtuh | 1.85 | 1.95 | 2.07 | 1.67 |

*Default value based on previous program data; in all but one project, this was the cooling efficiency value used

###### Deemed Lifetime of Efficient Equipment

10 years.

###### Deemed Measure Cost

There is no equipment cost to implement this measure. The only associated cost is the required internal labor to move lines from the to-be-removed piece of equipment to the chosen like piece of equipment. The default labor cost is $742/piece of equipment removed.

###### Loadshape

Loadshape is determined by the constant power draw by the line and trunk equipment; default loadshape is: Loadshape C53 – Flat.

###### Coincidence Factor

Coincidence Factor is determined by the constant power draw by the line and trunk equipment; the summer peak coincidence factor for the line and trunk equipment is assumed to be 100%. The cooling coincident factor is assumed to be slightly less due to compressor cycling; the summer peak coincidence factor for the cooling system is assumed to be 82%.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

kWh Savings=p*kWTrunk1+LCF*CE*t

Where:

p 		= Number of pieces of redundant equipment removed

kWTrunk		= Average line and trunk equipment power draw, 0.233 kW

LCF		= Load Conversion Factor kW to Ton, 0.284

CE		= Cooling Efficiency, default value = 1.90 kW/ton

t		= time, 8,760 hours

###### Summer Coincident Peak Demand Savings

kW Savings=p*kWTrunkCFTrunk+LCF*CE*CFCooling

Where:

p 		= Number of pieces of redundant equipment removed

kWTrunk		= Average line and trunk equipment power draw, 0.233 kW

LCF		= Load Conversion Factor kW to Ton, 0.284

CE		= Cooling Efficiency, default value = 1.90 kW/ton based on previous program data

CFTrunk		= Line and Trunk Equipment Coincidence Factor, 1.0

CFCool		= Cooling System Coincidence Factor, 0.82

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-SPEC-V01-210101

###### Review Deadline: 1/1/2023

### ENERGY STAR Uninterruptible Power Supply

###### Description

This measure is for replacing an inefficient uninterruptable power supply (UPS) with an efficient ENERGY STAR rated UPS in telecommunications, or similar facility that operates continuously. Note for data centers and other facilities that are not operated similarly to telecommunication applications, a custom calculation based on M&V analysis and that accounts for ramp-up of loads on the UPS should be performed. UPS units provide backup power in data centers and draw power constantly to keep their batteries charged. Uninterruptible power supplies (UPS) are utilized in many organizations to protect themselves from downtime with power distribution and avoid data processing errors due to downtimes.  UPS systems are connected between the public power distribution system and mission critical loads.

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient condition is a new ENERGY STAR UPS in a telecommunication or similar application. For single-normal mode UPSs, the installed system must meet or exceed the average loading-adjusted efficiency values required by the ENERGY STAR program.

###### Definition of Baseline Equipment

The baseline condition is an existing non-ENERGY STAR UPS in a telecommunication or similar application.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 15 years.

###### Deemed Measure Cost

The incremental cost is estimated at $59per UPS unit.

###### Loadshape

Loadshape is determined by the constant power draw by the UPS; default loadshape is Loadshape C53 – Flat.

###### Coincidence Factor

The coincidence factor for the UPS or rectifier is assumed to be 1.0 due to equipment operating during peak period.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

∆kWh	= Size * (1/EffAVGbase – 1/EffAVGee) * EFLH

Where:

Size		= Size of UPS in rated output power, kW

EffAVGbase		= Efficiency of existing UPS

= Actual or use table below

| UPS Product Class | Rated Output Power | Minimum Efficiency |
| --- | --- | --- |
| Voltage and Frequency Dependent (VFD) | P ≤ 300 W | -1.09×10-6 × P² + 6.50×10-4 × P + 0.876 |
|  | 300 W < P ≤ 700 W | -5.63×10-8 × P² + 7.61×10-5 × P + 0.955 |
|  | P > 700 W | -6.22×10-9 × P² + 3.91×10-6 × P + 0.981 |
| Voltage Independent (VI) | P ≤ 300 W | -6.45×10-7 × P² + 3.80×10-4 × P + 0.929 |
|  | 300 W < P ≤ 700 W | -3.94×10-8 × P² + 4.87×10-5 × P + 0.974 |
|  | P > 700 W | -2.28×10-9 × P² + 7.40×10-7 × P + 0.990 |
| Voltage and Frequency Independent (VFI) | P ≤ 300 W | -3.13×10-6 × P² + 1.960×10-3 × P + 0.544 |
|  | 300 W < P ≤ 700 W | -2.60×10-7 × P² + 3.65×10-4 × P + 0.765 |
|  | P > 700 W | -1.70×10-8 × P² + 3.85×10-5 × P + 0.877 |

EffAVGee		= Efficiency of new ENERGY STAR UPS

= Actual or ENERGY STAR minimum value from table below

| Rated Output Power | UPS Product Class |  |  |
| --- | --- | --- | --- |
|  | VFD | VI | VFI |
| P ≤ 350 W | 5.71 × 10-5 × P + 0.962 | 5.71 × 10-5 × P + 0.962 | 0.011 × ln(P) + 0.824 |
| 350 W < P ≤ 1.5 kW | 0.982 | 0.984 | 0.011 × ln(P) + 0.824 |
| 1.5 kW < P ≤ 10 kW | 0.981 - EMOD | 0.981 - EMOD | 0.0145 × ln(P) + 0.8 - EMOD |
| P > 10 kW | 0.97 | 0.94 | 0.0058 × ln(P) + 0.886 |

EMOD = an allowance of 0.004 for Modular UPSs applicable in the commercial 1500 – 10,000 W range

EFLH		= Equivalent Full Load Hours, per equation below and values provided in table

= t0.25×0.25+t0.5×0.5+t0.75×0.75+t1.0×1.0×8760 hours

| Rated Output Power (P) in watts | UPS Product Class | Time spent at specified proportion of reference test load (t) |  |  |  | EFLH |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 25% | 50% | 75% | 100% |  |
| P ≤ 1.5 kW | VFD | 0.2 | 0.2 | 0.3 | 0.3 | 5913 |
|  | VI or VFI | 0 | 0.3 | 0.4 | 0.3 | 6570 |
| 1.5 kW < P ≤ 10 kW | VFD, VI, or VFI | 0 | 0.3 | 0.4 | 0.3 | 6570 |
| P > 10 kW | VFD, VI, or VFI | 0.25 | 0.5 | 0.25 | 0 | 4380 |

Default Energy Savings are provided below:

| Output Power Range | Single-Normal Mode UPS Systems |  |  | Multiple-Normal Mode UPS Systems |  |
| --- | --- | --- | --- | --- | --- |
|  | VFD | VI | VFI | VFD25%/VI75% | VFD25%/VFI75% |
| P ≤ 350 W | 416.7 | 133.3 | 996.6 | 212.4 | 777.2 |
| 350 W < P ≤ 1.5 kW | 162.5 | 246.2 | -407.4* | 229.7 | -219.0* |
| 1.5 kW < P ≤ 10 kW | 131.7 | 105.8 | -609.2* | 115.9 | -383.8* |
| 10 kW < P < 16 kW | 65.2 | -63.4* | 255.1 | -21.9* | 210.9 |
| 16 kW ≤ P ≤ 80 kW | 65.2 | 31.4 | 62.6 | 48.6 | 72.3 |
| P > 80 kW | 65.2 | 31.4 | 102.7 | 48.6 | 72.3 |

‘*’ negative savings, i.e. an increase in consumption and so these are not recommended

###### Summer Coincident Peak Demand Savings

∆kW	= Size * (1/EffAVGbase – 1/EffAVGee) * CF

Where:

CFIT		= Coincidence factor of UPS

= 1.0

Default Summer Peak Demand Savings are provided below based on defaults above:

| Output Power Range | Single-Normal Mode UPS Systems |  |  | Multiple-Normal Mode UPS Systems |  |
| --- | --- | --- | --- | --- | --- |
|  | VFD | VI | VFI | VFD25%/VI75% | VFD25%/VFI75% |
| P ≤ 350 W | 0.0705 | 0.0203 | 0.1517 | 0.0323 | 0.1183 |
| 350 W < P ≤ 1.5 kW | 0.0275 | 0.0375 | -0.0620* | 0.0350 | -0.0333* |
| 1.5 kW < P ≤ 10 kW | 0.0223 | 0.0161 | -0.0927* | 0.01764 | -0.05842* |
| 10 kW < P < 16 kW | 0.0149 | -0.0096* | 0.0388 | -0.00333* | 0.03210 |
| 16 kW ≤ P ≤ 80 kW | 0.0149 | 0.0048 | 0.0095 | 0.00740 | 0.01101 |
| P > 80 kW | 0.0149 | 0.0048 | 0.0156 | 0.00740 | 0.01101 |

###### Natural Gas Savings

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-UPSE-V02-220101

###### Review Deadline: 1/1/2023

### Energy Efficient Rectifier

###### Description

This measure is for replacing an inefficient rectifier with an efficient unit in a data center, telecommunications, or similar facility that operates continuously. A rectifier converts alternating current (AC) to direct current (DC).

This measure was developed to be applicable to the following program types: TOS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient condition is a new rectifier whose efficiency in normal mode (not in energy saver mode) is at least 94%.

###### Definition of Baseline Equipment

The baseline condition is an existing rectifier whose efficiency in normal mode (not in energy saver mode) is less than 90%.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 15 years.

###### Deemed Measure Cost

The incremental cost is estimated at $59 per kW of IT Load.

###### Loadshape

Loadshape is determined by the constant power draw by the Rectifier; default loadshape is Loadshape C53 – Flat.

###### Coincidence Factor

The coincidence factor for the rectifier is assumed to be 1.0 due to equipment operating during peak period.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

∆kWh	= kWhbase - kWhEE

kWhbase	= ((Load * HIT)/Effbase) + ((Load * (1/ Effbase – 1) * HCool * kW/TonCool * 3412/12000)

kWhEE	= ((Load * HIT)/EffEE) + ((Load * (1/ EffEE – 1) * HCool * kW/TonCool * 3412/12000)

Where:

Load		= Average IT load (output kW)

= Actual, typically at 20% of equipment rated load

HIT		= Annual hours of operation of rectifier

= 8760

Hcool		= Annual cooling system hours of operation

= Actual or defaults below:

| System Size | Cooling Hours (Hcool) |
| --- | --- |
| Small IT (≤ 50 kW) without air-side economizer | 8760 hours |
| Small IT (> 50 kW) with air-side economizer | 4380 hours |

Effbase		= Efficiency of existing rectifier

= Actual. If unknown assume 90%

EffEE		= Efficiency of new rectifier

= Actual. If unknown assume 94%

kW/Toncool	= Cooling system efficiency (kW/Ton)

| Cooling Equipment Type | Efficiency Calculation (kW/Toncool) |
| --- | --- |
| Air-Cooled Chiller | kW/TonChiller + kWchilled water pump /Tons |
| Water-Cooled Chiller | kW/TonCompressor + (kWchilled water pump + kWcondensor water pump +kWcooling tower fans)/Tons |
| Direct Expansion System | 12/EER |

###### Summer Coincident Peak Demand Savings

∆kW	= kWbase - kWEE

kWbase	= ((Load * CFIT)/Effbase) + ((Load * CFcool * (1/ Effbase – 1) * kW/TonCool * 3412/12000)

kWhEE	= ((Load * CFIT)/EffEE) + ((Load * CFcool * (1/ EffEE – 1) * kW/TonCool * 3412/12000)

Where:

CFIT		= Coincidence factor of rectifier

= 1.0

CFcool		= Coincidence factor of cooling system

= 0.82

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-RECT-V02-220101

###### Review Deadline: 1/1/2023

### Energy Efficient Hydraulic Oils - Provisional Measure

###### Description

Industrial hydraulic systems use hydraulic oil to transfer input energy to output power. Hydraulic oils also protect critical components from premature wear. Energy efficient hydraulic oil lubricants meet these requirements and provide reduced energy consumption. Energy efficient hydraulic oils have a lower coefficient of friction which reduces the friction between two moving parts (rotating pump equipment and hydraulic oil). This lower coefficient of friction reduces the energy required to yield output power. Second, these oils have a high viscosity index which reduces the effect temperature has on the viscosity of the hydraulic oil. The high viscosity index allows constant viscosity over a range of operating temperatures which optimizes volumetric and mechanical efficiency at the pumps rated output. Additionally, energy efficient hydraulic oils reduce the operating temperature of the hydraulic system.

Manufacturers who use electric-motor-driven hydraulic systems have been found to reduce energy consumption by between 3 and 7%.

This measure was developed to be applicable to the following program types: NC, TOS and RF. If applied to other program types, the measure should be verified as a custom measure.

###### Definition of Efficient Equipment

This is applicable for small, medium, and large manufacturers in all climate zones using electric motors to power their hydraulic system both inside and/or outside conditioned areas; or for all hydraulic systems on mobile equipment in all climate zones on Illinois.

###### Definition of Baseline Equipment

The baseline equipment is defined as hydraulic systems using non-energy efficient industrial hydraulic oils which provides no energy efficiency benefits. In the formula below, the baseline equipment is where, Ei = zero.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

The ability to reduce energy consumption (energy efficiency) is an inherent characteristic in the oil which does not deplete over time. As long as the energy efficient oil is in use, it will provide energy efficiency.

###### Deemed Measure Cost

The actual incremental costs between an energy-efficient hydraulic oil and a standard hydraulic oil should be used.

###### Loadshape

Loadshape C14: Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15: Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16: Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17: Indust. 4-shift (24/7) (e.g., comp. air, lights)

###### Coincidence Factor

No coincidence factor though it is noted that reduced consumption for equipment will reduce the overall baseload power demand, especially if a construction operation or manufacturing operation demand more utility power in summer weather (e.g., construction ground work, rubber manufacturing, etc).

Algorithm

###### Calculation of Energy Savings

Savings are calculated based on a reduced coefficient of friction and the shear-stable high viscosity index value associated with energy-efficient hydraulic oils in hydraulic systems. The algorithm below for Energy Savings, is modeled after the Focus on Energy Emerging Technology Program M&V study.

###### Electric Energy Savings

ΔkWh 	= MotorHP * (0.746 kW/HP) * (%MotorLoading / µMotor) * HOURS * Ei

Where:

MotorHP	= Rated horsepower of electric motor, summed when pumps are in series.

= Actual

%MotorLoading	= Is dependent upon many factors including the part being manufactured, the polymer, the machine’s specifications, and cycle time.

= Actual, calculated as (Average load / Full rated load)

= Estimated as 75%.

µMotor		= Motor efficiency

= Actual. If unknown, estimated as 92% for motors in size range typically used.

HOURS		= Hours of operation per year

= Actual

Ei		= Efficiency improvement due to use of energy efficient hydraulic oils

= Actual. If not measured, assume 3.3%.

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

O&M savings from the necessary standard oil replacement over the lifetime of the energy efficient hydraulic oil (including oil cost, disposal costs, labor and avoided downtime) should be calculated. If additional savings for improved pump and valve lifetime can be demonstrated, these can also be included.

An example O&M cost calculation is provided below, relating to the standard hydraulic oil requiring 1 change out per year:

| O&M Component | Cost |
| --- | --- |
| Oil cost | $800 |
| Oil disposal cost | $80 |
| Labor (4 hours per change at $40/hr) | $160 |
| Downtime Production cost (2 hours at $500 lost production cost per year) | $1000 |
| Total annual O&M benefit (1 change per year) | $2040 |

###### Measure Code: CI-MSC-EEHO-V01-210101

###### Review Deadline: 1/1/2023

### Energy Efficient Gear Lubricants - Provisional Measure

###### Description

Industrial gear reduction systems use gear oil to transfer input energy to output power. Gear oils also protect critical components from premature wear. Energy efficient gear oil lubricants meet these requirements and provide reduced energy consumption. Energy efficient gear oils have a lower coefficient of friction which reduces the friction between two moving parts (rotating pump equipment and hydraulic oil). This lower coefficient of friction reduces the energy required to yield output power. Second, these oils have a high viscosity index which reduces the effect temperature has on the viscosity of the hydraulic oil. The high viscosity index allows constant viscosity over a range of operating temperatures which optimizes volumetric and mechanical efficiency at the pumps rated output. Additionally, energy efficient gear oils reduce the operating temperature of the gear-reduction gearbox.

Manufacturers who use electric-motor-driven gear-reduction gearboxes can reduce energy consumption by up to 1% per gear-mesh (e.g., 3% efficiency for a 3-reduction gearbox).

This measure was developed to be applicable to the following program types: NC, TOS and RF. If applied to other program types, the measure should be verified as a custom measure.

###### Definition of Efficient Equipment

This is applicable for small, medium, and large manufacturers in all climate zones using electric motors to power their gear reduction system both inside and/or outside conditioned areas; or for all gear reduction systems on mobile equipment in all climate zones on Illinois.

###### Definition of Baseline Equipment

The baseline equipment is defined as a gearbox using non-energy efficient industrial gear lubricants which provides no energy efficiency benefits. In the formula below, the baseline equipment is where, Ei = zero.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 10 years.

The ability to reduce energy consumption (energy efficiency) is an inherent characteristic in the oil which does not deplete over time. As long as the energy efficient oil is in use, it will provide energy efficiency.

###### Deemed Measure Cost

The actual incremental costs between an energy-efficient and a standard gear lubricant should be used.

###### Loadshape

Loadshape C14: Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15: Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16: Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17: Indust. 4-shift (24/7) (e.g., comp. air, lights)

###### Coincidence Factor

No coincidence factor though it is noted that reduced consumption for equipment will reduce the overall baseload power demand, especially if a construction operation or manufacturing operation demand more utility power in summer weather (e.g., construction ground work, rubber manufacturing, etc).

Algorithm

###### Calculation of Energy Savings

Savings are calculated based on a reduced coefficient of friction and the shear-stable high viscosity index value associated with energy-efficient gear oils in gear-reduction systems. The algorithm below for Energy Savings is modeled after the Focus on Energy Emerging Technology Program M&V study.

###### Electric Energy Savings

ΔkWh 	= MotorHP * (0.746 kW/HP) * (%MotorLoading / µMotor) * HOURS * Ei

Where:

MotorHP	= Rated horsepower of electric motor, summed when pumps are in series.

= Actual

%MotorLoading	= Is dependent upon many factors including the part being manufactured, the polymer, the machine’s specifications, and cycle time.

= Actual, calculated as (Average load / Full rated load)

= Estimated as 75%.

µMotor		= Motor efficiency

= Actual. If unknown, estimated as 92% for motors in size range typically used.

HOURS		= Hours of operation per year

= Actual

Ei		= Efficiency improvement due to use of energy efficient hydraulic oils

= Actual. If not measured, assume 1% per gear mesh.

###### Summer Coincident Peak Demand Savings

N/A

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

O&M savings from the necessary standard oil replacement over the lifetime of the energy efficient gear oil (including oil cost, disposal costs, labor and avoided downtime) should be calculated. If additional savings for improved gear box lifetime can be demonstrated, these can also be included.

###### Measure Code: CI-MSC-EEGL-V01-210101

###### Review Deadline: 1/1/2023

### Smart Sockets

###### Description

Smart sockets achieve savings through the reduction of the standby load of the controlled appliance, as well as eliminating the operation of an appliance during unoccupied hours.  The standby power consumption of home appliances and office equipment can be significantly reduced.

In a commercial office space, significant opportunity exists for savings from the reduction of plug loads, with power strips and timers being a key energy saving measure. Savings from smart sockets generally occurs during off-hours, when connected equipment continues to consume electricity while in standby mode or when off.  Savings may also be achieved through the more precise scheduling of the appliance, so that it is not operating during unoccupied hours, though those savings have not been attempted to be quantified within this summary.

Smart sockets are ideal for all types of plugged-in devices such as small appliances (coffee maker, office heater, etc.), in-wall AC units, large office equipment, outlet lights, digital signs, decorative lighting, televisions, etc, though they provide the greatest energy savings when installed on equipment with higher wattage and standby power consumption. In a commercial office space, the shared photocopier is often the largest stand-alone user of electricity, with the highest standby power draw, so an ideal candidate for use with a smart socket.  Note that a dedicated power supply is critical for your office photocopier.  Also, note that the electrical amperage rating of the smart socket should be verified to suit the connected equipment.  Desktop computers with peripheral equipment may be better served by an advanced power strip.

This measure was developed to be applicable to the following program types: DI, KITS.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient case is the use of a smart plug with a standby power wattage of 2W or less.  Should be UL listed.  (Simply Conserve Smart Socket SS-15A1-WiFi has a standby power of less than or equal to 0.7).

###### Definition of Baseline Equipment

The assumed baseline is an appliance or piece of office equipment plugged into an outlet (without a power strip) or into a standard power strip with surge protection that does not control connected loads.  Note many ENERGY STAR appliances require power saving settings which will partially offset the savings potential of this measure. Where possible non-ENERGY STAR equipment should be plugged in to the socket to ensure savings are realized.

###### Deemed Lifetime of Efficient Equipment

The assumed lifetime of the smart socket is 7 years.

###### Deemed Measure Cost

For direct install, the actual full equipment and installation cost (including labor) and for kits the actual full equipment cost should be used.  If unknown for kits, use $9.00/each.

###### Loadshape

Loadshape C47 – Standby Losses – Commercial Office

###### Coincidence Factor

N/A due to no savings attributable to standby losses between 1 and 5 PM.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh 	= ((((WBase * OnAdj) – WEff) * (hrswkday - hrswkday-open)) + (((WBase * OnAdj)– WEff) * (hrswkend - hrswkend-open)))/1000 * weeks/year * ISR

Where:

WBase 	= Standby power or On power consumption of connected appliance.

Use actual if known, or refer to tables below. If unknown, e.g. via kits, assume 9.4W

Appliances assumed to be in standby mode:

| Controlled Equipment | Standby Power (W) CF |
| --- | --- |
| Coffee Maker | 1.14 |
| Television, CRT | 3.06 |
| Television, Rear Projection | 6.97 |
| Television, LCD | 8.00 |
| Set-top Box, DVR | 36.68 |
| Set-top Box, Digital Cable | 17.83 |
| Set-top Box, Satellite | 15.66 |
| Television/VCR | 5.99 |
| VCR | 4.68 |
| Computer, Desktop | 2.84 |
| Computer Notebook | 8.90 |
| Multifunction Device, Inkjet | 5.26 |
| Multifunction Device, Laser | 3.12 |
| Scanner, Flatbed | 2.48 |

Appliances assumed to be in on mode:

| Controlled Equipment | On Power (W) CF |
| --- | --- |
| Light | 10.4 |
| Fan | 70 |
| Space Heater | 450 |
| Water Cooler | 100 |

OnAdj	= Adjustment for wattages of appliances that are powered on during out of hours

= 50% for appliances in on mode

=100% for appliances in standby mode and for unknown

WEff 	= Standby power consumption of smart socket. If unknown, assume 0.7W.

hrswkday 	= total hours during the work week (Monday 7:30 AM to Friday 5:30 PM)

= 106

hrswkend 	= total hours during the weekend (Friday 5:30 PM to Monday 7:30 AM)

= 62

hrswkday-open 	= hours the office is open during the work week. If unknown, assume 48 hours.

hrswkend-open 	= hours the office is open during the weekend. If unknown, assume 10 hours.

weeks/year	= number of weeks per year

= 52.2

ISR		= In Service Rate

= Assume 0.969 for commercial Direct Install application

= Assume 0.28 for kits that include two smart sockets

= Assume 0.36 for kits that include one smart socket

For example, a smart socket is direct installed with a LCD Television in an office open 9.6 hours per day (48 hours per week) on weekdays and 10 hours on weekends:

ΔkWh 	= ((((8 * 1) – 0.7) * (106 - 48)) + (((8 * 1) – 0.7) * (62 - 10)))/1000 * 52.2 * 0.969

= 40.6 kWh

###### Summer Coincident Peak Demand Savings

N/A due to no savings attributable to standby losses between 1 and 5 PM.

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-SSOC-V02-220101

###### Review Deadline: 1/1/2025

### Lithium Ion Forklift Batteries

###### Description

This measure applies to electric forklifts used in commercial, industrial, and warehouse environments. Electric forklifts with lithium ion battery systems are more efficient than electric forklfits with traditional lead acid battery systems because the lithium ion batteries have lower internal resistance. This allows the batteries to transfer power faster, reduces waste heat, and reduces standby losses.

Electric forklifts can be purchased with lithium ion battery systems or an existing electric forklift can be retrofitted to use a lithium ion battery system. An electric forklift can be converted to a lithium ion battery system by removing the lead acid battery and installing a battery case that includes a series of lithium ion batteries and the appropriate ballast to meet weight and balance specifications for the forklift. The lithium ion battery case is a one-for-one equivalent replacement of the lead acid battery in respect to capacity, shape, and weight. The forklift may require a new charger to work with the new lithium ion battery system.

This measure was developed to be applicable to the following program types: TOS and RF.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Class I, Class II, or Class III forklifts that are powered by lithium ion batteries with minimum 8-hour shift operation five days per week.

###### Definition of Baseline Equipment

Class I, Class II, or Class III forklifts that are powered by lead acid batteries with minimum 8-hour shift operation five days per week.

###### Deemed Lifetime of Efficient Equipment

15 years.

###### Deemed Measure Cost

Costs will vary significantly based on the capacity and class of the forklift. Costs for this measure should be determined by actual quotes obtained from manufacturers and estimated labor. If not available, it is estimated that converting a lead acid battery forklift to a lithium ion battery system would cost $17,000.

###### Loadshape

Loadshape C14 - Indust. 1-shift (8/5) (e.g., comp. air, lights)

Loadshape C15 - Indust. 2-shift (16/5) (e.g., comp. air, lights)

Loadshape C16 - Indust. 3-shift (24/5) (e.g., comp. air, lights)

Loadshape C17 - Indust. 4-shift (24/7) (e.g., comp. air, lights)

###### Coincidence Factor

It is assumed that lead acid battery forklifts are charged overnight. Therefore, the coincidence factor is assumed to be 0.0 for 1-shift and 2-shift operations and 1.0 for 3-shift and 4-shift operations.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = (CAP * DOD) * CHG * (EELIB - EELAB) / EELAB

Where:

CAP	= Capacity of Battery

= Use actual battery capacity, otherwise use a default value of 35 kWh

DOD	= Depth of Discharge

= Use actual depth of discharge, otherwise use a default value of 80%.

CHG	= Number of Charges per year

= Use actual number of annual charges, if unknown use values below based on the type of operation

| Standard Operations | Number of Charges per year |
| --- | --- |
| 1-shift (8 hrs/day – 5 days/week) | 520 |
| 2-shift (16 hrs/day – 5 days/week) | 1,040 |
| 3-shift (24 hrs/day – 5 days/week) | 1,560 |
| 4-shift (24 hrs/day – 7 days/week) | 2,184 |

EELAB	= Energy Efficiency of Lead Acid Battery

= Use actual efficiency of battery for retrofit, for new or unknown use 46%

EELIB	= Energy Efficiency of Lithium Ion Battery

= Use actual efficiency of battery, if unknown use 73%7

Savings for each shift operation using defaults provided above are provided below:

| Standard Operations | Savings (kWh/yr) |
| --- | --- |
| 1-shift (8 hrs/day – 5 days/week) | 8,546 |
| 2-shift (16 hrs/day – 5 days/week) | 17,092 |
| 3-shift (24 hrs/day – 5 days/week) | 25,638 |
| 4-shift (24 hrs/day – 7 days/week) | 35,894 |

###### Summer Coincident Peak Demand Savings

###### It is assumed there is zero peak demand savings.

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

Lithium ion batteries offer several O&M advantages over lead acid batteries. These benefits include, but are not limited to:

- Lithium ion batteries charge must faster, which results in less downtime.

- There is no requirement for changing out batteries at the end of a shift or having multiple spare batteries in stock.8 A 3-shift operation would require a facility to have three separate lead acid batteries for each forklift, so they could swap out batteries at the end of each shift. A lithium ion battery is charged while still in the forklift and can use opportunity charging during employee breaktime.

- Fewer maintenance issues and no requirement for battery watering8

- Longer operating life. Lithium ion batteries can last nearly four times as long as lead acid batteries.

These benefits should be considered and evaluated on a project-by-project basis. It is estimated that lithium ion forklift adoption saves a facility 65 labor hours per truck on an annual basis.

###### Measure Code: CI-MSC-LION-V01-220101

###### Review Deadline: 1/1/2025

### Building Operator Certification

###### Description

Building Operator Certification (BOC) is a training and certification program for commercial and public sector building operators. The curriculum teaches participants how to improve building comfort and efficiency by optimizing the building’s systems. BOC curriculums provide participants with knowledge about system operations, proper maintenance practices, occupant communication, and occupant comfort. Participants realize energy savings by utilizing the knowledge gained to improve their building operations through O&M and capital measures.

Evaluators in Illinois used differing levels of engagement with participants to estimate savings from the BOC training. While deeming savings does not fully capture the individual and varied actions that participants made as a result of their BOC training, it is a reasonable approach to better align the expected level of impacts and program expenditures with evaluation expenditures. Deemed savings for this measure represent a weighted average of analyses’ results from several Illinois BOC program evaluations. The evaluations estimated net savings and were developed per square foot of building area to account for the diversity of building sizes across Illinois.  All savings estimating algorithms presented in this work paper are for net savings. Participants are required to complete a rigorous BOC course, and can only claim savings for the facilities for which the individual taking the course are responsible.

The AIC and ComEd evaluators will conduct interviews with 2020 participants to determine the actions and corresponding savings achieved since participating in the training, the results of which will be provided in the final 2021 evaluations (produced by April 30, 2022) and used to measure savings for 2021. The 2021 evaluation results will also be used to update this measure for use in 2023. The 2022 IL-TRM v10.0 will be used to verify savings for 2021 and 2022 participants, and these results will be included in the final 2022 BOC evaluations (produced by April 30, 2023). This will include 2 years’ worth of participants due to the annualization of savings for 2022 participants and the transition year of 2021 to the deemed approach. In addition, Nicor evaluators will conduct interviews with past BOC participants to determine the actions and corresponding savings achieved since participating in the training, the results of which will inform updates to this measure for use in 2023.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient case is facilities operated by participants who complete a BOC training program. Participants must complete either the BOC Level I or Level II course and obtain a certificate of completion to be eligible for savings. Eligible BOC programs must cover the following subject areas:

| BOC Level I | BOC Level II |
| --- | --- |
| - Efficient Operation of HVAC Systems - Measuring and Benchmarking Energy - Efficient Lighting Fundamentals - HVAC Controls Fundamentals - Indoor Environmental Quality - Common Opportunities for Low-Cost Operational Improvement | - Building Scoping and Operational Improvements - Optimizing HVAC Controls for Energy Efficiency - Introduction to Building Commissioning - Water Efficiency for Building Operators - Project Peer Exchange |

The BOC course must include formal instruction (i.e., lectures), individual projects and group exercises, bringing the total course time to at least 61 hours. Participants must obtain a training certificate of completion to be eligible for savings. Individuals who participate are not eligible for savings more than twice over the measure life, once for BOC Level I and another for BOC Level II.  The entire floor area for any given building can only be used once over the measure life, and evaluators will verify attendees’ participation year-over-year.

The savings factors for this measure were developed based on an examination of savings using a weighted average approach from several similar BOC programs. The table below outlines the referenced evaluation studies, and key parameters which were inputs to this measure characterization. It is important to note that the savings information referenced is net. Therefore, this measure does not require the additional application of a net-to-gross ratio.

No previous custom study of customer participation in BOC shall inform eligibility for this measure.

| Utility or Program Administrator | Year | Participants | Average Building Area | MWh/ Participant | kW/ Participant | Therm/ Participant | Incremental Measure Costs ($/Participant) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Ameren Illinois | 2020 | 10 | 140,137 | 60 | 0.83 | 987 | $253.94 |
| Ameren Illinois | 2019 | 12 | 408,309 | 64 | 12.8 | 3,615 | $114.93 |
| ComEd | 2020 | 33 | 319,068 | 133 | 14.7 | 0 | $8,878.79 |
| Weighted Average |  |  | 306,006 | 105 | 12.0 | 968 | $5,398.52 |

###### Definition of Baseline Equipment

The baseline is building operations as they existed before the participant completed the BOC training course.

###### Deemed Lifetime of Efficient Equipment

The measure life for BOC savings is 13 years.  Based on analyzed research, assume 42% of BOC savings are derived from O&M measures that have a 4-year measure life. This should be handled similar to other midlife adjustments, where after 4 years, a midlife adjustment factor of 58% is applied for the remaining nine years of the measure life.

###### Deemed Measure Cost

The deemed training measure cost is $1,400. In addition, the incremental cost of capital and O&M measures should also be included. If unknown, use an incremental measure cost of $0.018/ft2.

###### Loadshape

C23 – Commercial Ventilation

###### Coincidence Factor

The demand savings factor (Cd) is already based upon coincident savings, and thus there is no additional coincidence factor for this characterization.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = Ce * Area

Where

Area 	= Building area operated by the participant. The maximum eligible area per participant is 500,000 ft2. In the event there are multiple participants who operate the same building (i.e. service address), or group of buildings, the program administrator can only claim savings on building square footage once (i.e., they cannot claim savings based on the same square footage for multiple participants), unless the managed square footage exceeds 500,000 ft2; in which case, the program administrator can continue to claim savings up to the 500,000 ft2 per participant cap until the total square footage has been accounted for.

Ce 	= unit area kWh savings constant per participant, 0.342 kWh/ft2/participant

###### Summer Coincident Peak Demand Savings

kW = Cd * Area / 1000

Where

Cd 	= Unit demand savings constant, 0.0384 W/ft2 (capped)/participant

1000 	= unit conversion from W to kW

###### Natural Gas Savings

Therms = Cg * Area

Where

Cg 	= Unit gas savings constant, 0.00316 therms/ft2 (capped)/participant

###### Water and Other Non-Energy Impact Descriptions and Calculation

###### N/A. Water and other non-energy impacts could be added in future updates.

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-BOC-V01-220101

###### Review Deadline: 1/1/2023

### Warm-Mix Asphalt Chemical Additives

###### Description

Warm-Mix Asphalt (WMA) is the name for a variety of technologies that allow for production and placement of asphalt at temperatures lower than traditional Hot-Mix Asphalt (HMA). The production temperature of WMA is typically 25°F to 90°F below that of HMA, resulting in reduced energy consumption. The actual temperature reduction depends upon the warm mix technology used. Currently, there are three categories of WMA technologies: asphalt foaming technologies, organic additives, and chemical additives.

The asphalt foaming technologies include a variety of processes to foam asphalt, including water-injecting systems, damp aggregate, or the addition of a hydrophilic material such as a zeolite. In the asphalt plant, the water turns to steam, disperses throughout the asphalt, and expands the binder, providing a corresponding temporary increase in volume and fluids content, similar in effect to increasing the binder content. Chemical additives often include surfactants that aid in coating and lubrication of the asphalt binder in the mixture. Lastly, organic additives are typically special types of waxes that cause a decrease in binder viscosity above the melting point of the wax.

In additional to energy savings, using WMA in place of HMA reduces greenhouse gas emissions and provides multiple non-energy benefits, such as beter compaction, cool-weather paving, longer haul distances, and improved working conditions for the paving crew (reduction of fumes and odors). Warm-mix chemical additives allow for the mixing and placement of asphalt at temperatures lower than traditional HMA while maintaining similar strength, durability, and performance characteristics.

This measure is applicable to the industrial market with the end user in the transporation sector. WMA can be used in any climate, as the lower mix temperature allows WMA to be used in cooler ambient conditions than traditional HMA.

This measure was developed to be applicable to the following program types: TOS. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient case is WMA. WMA is generally produced at temperatures ranging from 25°F to 90°F lower than HMA.

General WMA technologies can be categorized as chemical additives, organic additives, and water-based foaming methods. Chemical additives reduce the internal friction between aggregate particles and thin films of binders when subjected to high shear rates during mixing and high shear stress during compaction. In contrast, the other two WMA methods rely on reduction of binder viscosity.

###### Definition of Baseline Equipment

The baseline case is traditional HMA. HMA is traditionally mixed between 280°F and 320°F.

###### Deemed Lifetime of Efficient Equipment

The measure life is 1 year. Savings occur during production, and last only as long as the production runs. Since savings and costs scale to tons of asphalt production, a 1-year measure life appropriately tracks lifecycle savings.

###### Deemed Measure Cost

The costs of WMA depend primarily on the type of WMA technology that is used. Of the WMA technology options, water-injection asphalt foaming typically have the lowest cost per ton. Water injection WMA technologies have a lower incremental cost at around $0.08 per ton.

Compared to other WMA technologies, additive based WMA technologies increase the mix costs by $2.50 per ton due to the cost of chemicals and freight costs.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

Energy savings are dependent on multiple factors that primarily affect the production of WMA. The following factors have been identified as the primary contributors to energy consumption:

- Mixing drum temperature

- Additive type

###### Electric Energy Savings

N/A.

###### Summer Coincident Peak Demand Savings

N/A.

###### Natural Gas Savings

Average temperature reduction achieved by plants that reduce mix production temperature when using WMA must be determined to estimate reductions in energy consumption. In practice, WMA production temperatures when using water-injection foaming technologies are typically about 25°F lower than those for hot mix asphalt (HMA) using the same mix design. WMA produced with additives tends to have substantially lower mixing temperatures. For the purpose of estimating energy savings, a temperature difference of 50°F is assumed for additive-type WMA compared to HMA using the same mix design.

thermssavings=tons×SF

Where:

tons	=	Tons of asphalt produced

SF	=	WMA production savings factor (therms/ton)

=              1100 Btu/Δ°F/ton

=              0.011 therms/Δ°F/ton (1100 Btu/Δ°F/ton/100,000 – Conversion factor from Btu to therm)

= 	See Table 2 for SF for Water Injection Foaming and Additives

Table 2 Energy Savings by mixing temperature reduction

| WMA Production Technology | [A] Energy Savings (therms/Δ°F/ton) | [B] Temperature Reduction (°F) | [C] = [A]*[B] SF (therms/ton) |
| --- | --- | --- | --- |
| Water Injection Foaming | 0.011 | 25 | 0.275 |
| Additives | 0.011 | 50 | 0.605 |
| Custom Documented | 0.011 | Custom | Calculated |

Example:

A plant producing 1,000 ton ashphalt everyday now decides to adopt additives for energy savings and non energy benefits. The savings for that plant will be computed:

Savings = 1,000 tons * 0.605 (therms/ton) from table # 2. = 605 therms saved.

###### Water and Other Non-Energy Impact Descriptions and Calculation

In addition to reduced energy consumption, reduction in production temperatures results in reduced greenhouse gas emissions from the combustion process and any emissions from the mixed asphalt.  The reduction of emissions, fumes, and odors results in a healthier work environment for production operators, truck drivers, and application workers. The lower temperature mix also allows for an extended paving season, night paving, and longer hauling distances for the WMA in comparison to HMA with faster application times.

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-WMIX-V01-220101

###### Review Deadline: 1/1/2025

### Energy Efficient Hand Dryers

###### Description

###### This measure consists of installing efficient hand dryers that save energy by drying with air movement, using motion sensors, and reducing drying time.  Energy efficient hand dryers use less energy per dry than standard hand dryers.  Hand dryers are applicable in retail, commercial, and industrial settings.

###### This measure was developed to be applicable to the following program types: TOS, ERET.  If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

To qualify for this measure, a hand dryer must use 5 Wh or less per use.

###### Definition of Baseline Equipment

The baseline equipment for this measure is hand dryer with 5 or more Wh per use.  Usually, these hand dryers are push-button activated.

###### Deemed Lifetime of Efficient Equipment

The measure life for a new energy efficient hand dryer is 10 years.

###### Deemed Measure Cost

Incremental cost is $483. Baseline cost for a hand dryer is $368. Efficient cost for an efficient hand dryer is $851.

###### Loadshape

Loadshape C02 - Commercial Electric DHW

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

∆kWh=UPD*DPY*(ΔWh)1000

Where:

UPD		= Number of uses per day.

= If not known, use assumption from the table below.

DPY	 	= Number of days the facility operates per year.

= If not known, use assumption from the table below.

| Usage | Uses per Day |  | Days per Year (DPY) |  | Building Type |  |
| --- | --- | --- | --- | --- | --- | --- |
| Low | 50 |  | 250 |  | Office / Warehouse |  |
| Medium/Moderate | 250 | 365 | Restaurant / Small Grocery/Retail |
| High | 500 |  | 200 |  | School/University / Theater / Conference Center |  |
| High - Grocery | 500 | 365 | Large Grocery/Retail |
| Heavy Duty/Extreme | 2,500 |  | 365 |  | Transportation Center / Stadium / Airport |  |

ΔWh		= Change in Watt-hours from baseline to efficient.

ΔWh =Power*Cycle TimeBaseline-Power*Cycle TimeEfficient3600sechr

Where:

Power		= Unit wattage.

= If not known, use assumption from the table below.

Cycle Time	= Runtime seconds per use.

= If not known, use assumption from the table below.

| Assumptions | Power (watts) | Cycle Time (seconds) |
| --- | --- | --- |
| Baseline | 2,036 | 37 |
| Efficient | 1,066 | 12 |

###### For example, a new efficient hand dryer replacing a baseline hand dryer at a large grocery store, with unknown uses per day and unknown days per year:

ΔkWh	= 	(500 * 365 * (((2036*37) - (1066*12)) /3600)) /1000

=	3,170.4 kWh

###### Summer Coincident Peak Demand Savings

ΔkW = ΔkWhHOU*CF

Where:

HOU		= Use building hours, if known.

= If hours not known, hours are selected from the fixture hours column of the lighting reference

table in section 4.5 for each building type.

CF 		= Coincident Factor, use 1.0.

###### For example, a new efficient hand dryer replacing a baseline hand dryer at a large grocery store, with unknown uses per day and unknown days per year:

ΔkW	=	3,170.4 / 5,468 * 1.0

=	0.58 kW

###### Natural Gas Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-MSC-EEHD-V01-220101

###### Review Deadline: 1/1/2026

Equipment life is expected to be longer, but measure life is more conservative to account for possible attrition in use over time.

Based on bulk pricing reported by EnSave, which administers the rebate in Vermont

Efficiency Vermont (EVT) Technical Reference Manual (TRM), Measure Savings Algorithms and Cost Assumptions, March 16, 2015. Based on field study conducted by Efficiency Vermont on 352 sites in Vermont and Minnesota.

The number of days in the use season in which the temperature drops below 25°F in the state of Illinois. The data is sourced as an average from TMY3 weather data for five different weather zones within the state.

EVT TRM, March 16, 2015. Based on field study conducted by EVT on 352 sites in Vermont and Minnesota.

Ibid. The hours per day saved is sourced as the difference between the baseline run hours per day without the timer, 10.66 hours, and the efficient run hours per day with the timer, 2.90 hours.

Ibid. Based on an average sized engine block heater, which typically ranges in connected load from 0.20 kW and 2 kW, as sourced from Efficiency Vermont program data.

Ibid.

Act on Energy Commercial Technical Reference Manual No. 2010-4

Ibid.

Ibid.

Ibid.

Ibid.

Act on Energy Commercial Technical Reference Manual No. 2010-4

Ibid.

Ibid.

Ibid.

Ibid.

Act on Energy Commercial Technical Reference Manual No. 2010-4

Ibid.

Ibid.

Ibid.

Focus on Energy Evaluation Business Programs Measure Life Study: Final Report August 25, 2009, Public Service Commission of Wisconsin.

The measure incremental cost is sourced from the 2019 Michigan Energy Measures Database (MEMD).

The default fan horsepower is based on a review of single- and three-phase fans listed on BESS Labs performance tested exhaust fans between 36” and 47”. The Bioenvironmental and Structural Systems (BESS) Laboratory is a research and agriculture fan product-testing lab at the University of Illinois. For more detail on the derivation of fan horsepower from BESS Lab’s fan performance archive, please see “BESS Bin Data.xlsx”.

The baseline run time assumes equipment continuous operation from May 1st through October 31st. Efficient run time is based on regional TMY3 weather data and is the count of hours in which outdoor air temperature exceeds 70°F.

Table 1 with efficiency classes 60034-30 (2008), 4 Pole High Efficiency Motor, Technical note, IEC 600034-30 standard on efficiency classes for low voltage AC motors, TM)25 EN RevC 01-2-12, ABB.

Measure life is sourced from DEER 2008 for permanent, solid-set low pressure sprinkler nozzles.

The incremental cost is sourced from SCE Workpaper, SCE13WP007, Low pressure Sprinkler Nozzles, January 2013.

Iowa Energy Efficiency Statewide TRM, Version 3.0, effective January 1, 2019

For additional detail on the derivation of Illinois-specific savings values and how the original source material was modified and normalized into single deemed values, please see the Illinois Workpaper for this measure, “Illinois_Statewide_TRM_Workpaper_Low Pressure Sprinkler Nozzles_2019 4.1.7.docx”.

It is less stressful (metabolically) for cows to drink warmed water, and research has shown that cows will drink more water if it is warmer, leading to increased milk production. “Massachusetts Farm Energy Best Management Practices for Dairy Farms”, United States Department of Agriculture (USDA), Natural Resource Conservation Service (NRCS), 2012.

PA Consulting Group for the State of Wisconsin Public Service Commission, Focus on Energy Evaluation. Business Programs: Measure Life Study. Page 45 of pdf file. August 25, 2009.

The equipment and labor costs are sourced from the PG&E Workpaper – Milk Pre Cooler (PGE3PAGR114), February 2013.

Efficiency Vermont (EVT) Technical Reference Manual (TRM), Measure Savings Algorithms and Cost Assumptions, March 16, 2015

The efficacy of a milk plate cooler is sourced from Sanford, Scott (University of Wisconsin–Madison). “Energy Efficiency for Dairy Enterprises.” Presentation to Agricultural and Life Sciences Program staff. December 2014. It was assumed that there is a 25°F of milk temperature difference for a single pass plate cooler and a 35°F of temperature difference for a double/multi-pass plate cooler. For the purposes of this measure, a straight average of 30°F between the two types was used. A plate cooler reduces the overall load on the refrigeration compressors and the revised ΔT when accounting for a milk pre-cooler is 30°F less

“Ag Heat Recovery Tank Supplemental Data.” WI Dairy Statistics tab shows USDA reported annual data from: U.S. Department of Agriculture. “Milk Production per Cow, Wisconsin.”

The default value for the average number of milking cows per farm is sourced from the 2017 U.S. Census of Agriculture, Illinois State Summary Highlights, Full Report, Volume 1, Chapter 2, U.S. State Level. Average number of cows per farm = 93,341 cows / 924 farms.

Specific heat of whole milk, Table 3: Unfrozen Composition Data, Initial Freezing Point, and Specific Heat of Foods, 2014 ASHRAE Handbook - Refrigeration. Page 19.5.

Average efficiency of an existing compressor on a dairy farm, as sourced from, Massachusetts Farm Energy: Best Management Practices for Dairy Farms, USDA NRCS, 2012 (page 19).

Raw milk for pasturing must be cooled with 4 hours. Assuming 2 milking per day. Dairy Farm Energy Management Guide: California, Ludington, Johnson, Kowalski, & Mage, Southern California Edison, 2004.

Focus on Energy Evaluation Business Programs Measure Life Study: Final Report August 25, 2009, Public Service Comission of Wisconsin.

The equipment and labor costs are sourced from the PG&E Workpaper – Milk Vacuum Pump VSD, Dairy Farm Equipment (PGE3PAGR116), February 2013.

Average efficiency of an existing compressor on a dairy farm, as sourced from, Massachusetts Farm Energy: Best Management Practices for Dairy Farms, USDA NRCS, 2012 (page 19)

Specific heat of whole milk, Table 3: Unfrozen Composition Data, Initial Freezing Point, and Specific Heat of Foods, 2014 ASHRAE Handbook - Refrigeration. Page 19.5.

Sanford, Scott (University of Wisconsin–Madison). “Well Water Precoolers.” Publication A37843. October 2003. It was determined that a plate cooler alone can reduce milk temperature to 68 ˚F and a plate cooler paired with a milk transfer pump VSD can reduce milk temperature to 56.3˚F. The additional benefits of the milk transfer pump VSD over the plate cooler is 11.7˚F.

“Ag Heat Recovery Tank Supplemental Data.” WI Dairy Statistics tab shows USDA reported annual data from: U.S. Department of Agriculture. “Milk Production per Cow, Wisconsin.”

The default value for the average number of milking cows per farm is sourced from the 2017 U.S. Census of Agriculture, Illinois State Summary Highlights, Full Report, Volume 1, Chapter 2, U.S. State Level. Average number of cows per farm = 93,341 cows / 924 farms.

Focus on Energy Evaluation Business Programs Measure Life Study: Final Report August 25, 2009, Public Service Comission of Wisconsin.

The incremental cost is sourced from the PG&E Workpaper – Scroll Compressor (PGE3PAGR113), February 2013. The incremental cost is based on the difference in material and labor cost between a reciprocating compressor, $2,538, and a scroll compressor, $2,985.

Efficiency Vermont (EVT) Technical Reference Manual (TRM), Measure Savings Algorithms and Cost Assumptions, March 16, 2015

Average efficiency of a reciprocating compressor, as sourced from Wisconsin Focus on Energy TRM – Plate Heat Exchanger and Well Water Pre-Cooler, 2017

Average efficiency of a scroll compressor, as sourced from Massachusetts Farm Energy: Best Management Practices for Dairy Farms, USDA NRCS, 2012 (page 33)

Specific heat of whole milk, Table 3: Unfrozen Composition Data, Initial Freezing Point, and Specific Heat of Foods, 2014 ASHRAE Handbook - Refrigeration. Page 19.5.

Safe Handling of Milk & Dairy Products. March 8th, 2017 and Sanford, Scott (University of Wisconsin–Madison). “Well Water Precoolers.” Publication A37843. October 2003. The temperature of the milk exiting the cow is considered to be 98°F and the final, cooled temperature of the milk is assumed to be 38°F.

The efficacy of a milk plate cooler is sourced from Sanford, Scott (University of Wisconsin–Madison). “Energy Efficiency for Dairy Enterprises.” Presentation to Agricultural and Life Sciences Program staff. December 2014. It was assumed that there is a 25°F of milk temperature difference for a single pass plate cooler and a 35°F of temperature difference for a double/multi-pass plate cooler. For the purposes of this measure, a straight average of 30°F between the two types was used. A plate cooler reduces the overall load on the refrigeration compressors and the revised ΔT when accounting for a milk pre-cooler is 30°F less.

“Ag Heat Recovery Tank Supplemental Data.” WI Dairy Statistics tab shows USDA reported annual data from: U.S. Department of Agriculture. “Milk Production per Cow, Wisconsin.”

The default value for the average number of milking cows per farm is sourced from the 2017 U.S. Census of Agriculture, Illinois State Summary Highlights, Full Report, Volume 1, Chapter 2, U.S. State Level. Average number of cows per farm = 93,341 cows / 924 farms.

Raw milk for pasturing must be cooled with 4 hours. Assuming 2 milking per day. Dairy Farm Energy Management Guide: California, Ludington, Johnson, Kowalski, & Mage, Southern California Edison, 2004.

U.S. Department of Agriculture, Natural Resources Conservation Service. “Energy Self-Assessment: Refrigeration Heat Recovery.” Accessed December 8, 2015.

PA Consulting Group Inc. “State of Wisconsin Public Service Commission of Wisconsin Focus on Energy Evaluation Business Programs: Measure Life Study Final Report.” August 25, 2009.

The incremental cost is sourced from Efficiency Vermont custom project data based on actual equipment installs between 2010 and 2017.

Wisconsin Milk Marketing Board. “Did You Know? Website: Milking Every Day.” Accessed December 21, 2015

Talbot, Jacob (American Council for an Energy-Efficient Economy). ACEEE Report A121: Market Transformation Efforts for Water Heating Efficiency. January 2012.

“Ag Heat Recovery Tank Supplemental Data.” WI Dairy Statistics tab shows USDA reported annual data from: U.S. Department of Agriculture. “Milk Production per Cow, Wisconsin.”

The default value for the average number of milking cows per farm is sourced from the 2017 U.S. Census of Agriculture, Illinois State Summary Highlights, Full Report, Volume 1, Chapter 2, U.S. State Level. Average number of cows per farm = 93,341 cows / 924 farms.

Specific heat of whole milk, Table 3: Unfrozen Composition Data, Initial Freezing Point, and Specific Heat of Foods, 2014 ASHRAE Handbook - Refrigeration. Page 19.5.

The efficacy of a milk plate cooler is sourced from Sanford, Scott (University of Wisconsin–Madison). “Energy Efficiency for Dairy Enterprises.” Presentation to Agricultural and Life Sciences Program staff. December 2014. It was assumed that there is a 25°F of milk temperature difference for a single pass plate cooler and a 35°F of temperature difference for a double/multi-pass plate cooler. For the purposes of this measure, a straight average of 30°F between the two types was used. A plate cooler reduces the overall load on the refrigeration compressors and the revised ΔT when accounting for a milk pre-cooler is 30°F less.

Sanford, Scott (University of Wisconsin–Madison). “Well Water Precoolers.” Publication A37843. October 2003

DeLaval. “Dairy Farm Energy Efficiency.” April 20, 2011. DeLaval estimates the heat recovery potential to be between 20 and 60%. Based on engineering judgement and further corroboration from the Wisconsin Focus on Energy TRM, opted to default to a 55% savings factor.

The hot water use per day is based on the average hot water requirements per wash cycle multiplied by the number of wash cycles per day. The average amount of hot water used per wash cycle, 47.9 gallons, is sourced from the National Resource Conservation Service for Wash Water Requirements for Milking Systems, a calculator developed by University of Wisconsin, August 2005, Milking Center Waste Volume, v12,05, The number of wash cycles per day account for the hot water rinse cycles that are used to flush and clean the milk lines before and after milking. As sourced from the Regional Technical Forum (RTF) as part of the Northwest Power & Conservation Council, Deemed Measures List; Agricultural: Variable Frequency Drives-Dairy, FY2012, v1.2. Pre- and post-power meter data for five sites were used to establish RTF energy savings and the raw data used to generate load profiles showed, on average, two milkings per day. As there will be one more wash cycle than milking, the default average wash cycles per day is three.

Design Light Consortium – Horticultural Lighting, Testing and Reporting Requirements for LED-Based Horticultural Lighting, version 2.1, effective July 1, 2021. To date, all horticultural lamps certified by the DLC specification are LEDs.

Erik Runkle and Bruce Bugbee “Plant Lighting Efficiency and Efficacy: μmols per joule”. Accessed 4/21/2020.

Jesse Remillard and Nick Collins, “Trends and Observations of Energy Use in the Cannabis Industry,” ACEEE, accessed April 17, 2020. Baseline watts per square foot were taken by using typical fixture technology by crop type and dividing by 16 sqft per fixture (a 4’x4’ area is a typical coverage amount for one grow light fixture).

Jesse Remillard and Nick Collins, “Trends and Observations of Energy Use in the Cannabis Industry,” ACEEE, accessed April 17, 2020. Baseline watts per square foot were taken by using typical fixture technology by crop type and dividing by 16 sqft per fixture (a 4’x4’ area is a typical coverage amount for one grow light fixture).

Jacob A. Nelson, Bruce Bugbee, “Economic Analysis of Greenhouse Lighting: Light Emitting Diodes vs. High Intensity Discharge Fixtures.” Utah State University. Accessed 5/6/2020.

Microgreens T5 fixture is based on a 6-lamp high output fixture, based on program experience.

Jacob A. Nelson, Bruce Bugbee, “Economic Analysis of Greenhouse Lighting: Light Emitting Diodes vs. High Intensity Discharge Fixtures.” Utah State University. Accessed 5/6/2020.

Propagation T5 fixture is based on a 4-lamp high output fixture, based on program experience.

Jacob A. Nelson, Bruce Bugbee, “Economic Analysis of Greenhouse Lighting: Light Emitting Diodes vs. High Intensity Discharge Fixtures.” Utah State University. Accessed 5/6/2020.

Recreational cannabis baseline PPE requirement is either 36 W/sqft or 2.2 μmol/J and DLC listed. Per HB 1438.

Recreational cannabis baseline wattage was back calculated using 36 W/sqft and 16 sqft coverage area to get 576 W per fixture.

Illinois legislation Public Act 101-0027 the Cannabis Regulation and Tax Act, Article 20: Adult Use Cultivation Centers, (Section

20-15 (a) (23) a commitment to a technology standard for resource efficiency of the cultivation center facility (B) Lighting)

Based on 50,000 hours lifetime and 5,250 hours per year of use (average hours of use per year using flowering and vegetative rooms).

Focus on Energy Evaluation Business Programs: Measure Life Study Final Report: August 25, 2009

Assumes a 4’ x 4’ canopy

Sole-Source Lighting of Plants. Technically Speaking by Erik Runkle. Michigan State University Extension. September 2017. Accessed: 7/29/2019.

Annual hours of operation were found by multiplying hours per day by 350 operating days per year. Assuming 5 crop cycles with 3 days of downtime between each cycle

Waste heat factor for cooling savings calculation can be found in the Indoor Agriculture Loadshapes excel file.

Negative value because this is an increase in heating consumption due to the efficient lighting

Zhang, Q. and H. Xin, “Responses of Piglets to Creep heat Type and Location in Farrowing Crate,” Applied Engineering in Agriculture (2001): Vol. 17(4) 515-519

“Research at Puratone Confirms Effectiveness and Extensive Energy Savings of Heat Pads,” Manitoba Hydro Power Smart

Professional judgement based on Iowa Energy Efficiency Statewide Technical Reference Manual 2018 Volume 3: Nonresidential Measures, Agriculture Equipment: 3.1.9 Heat Mat, Posted July 12th, 2017

Hog Slat. (2019). Heat Pad. Online pricing catalogue for agriculture and livestock equipment.

Coincidence factor is taken from the IL TRM loadshape C04 – Non-residential Electric Loadshape.

While heat mat hours do vary from heat lamps slightly, the savings assumptions match heat lamp hours for consistency. Calculation method from Iowa State University farm manager (Ben Drescher): "At minimum I’d say they are on 24-7 from Oct-March and March-May, and 12 hours a day June-September 8 hours a day. You’d also take off for power washing etc. so if you had a 24 day turn in a farrowing room you’d run them for 21 days and turn the room subtract 3 days from x 15 turns a year - resulting in 5120 hours." Cadmus did not round data and estimated 5,105 hours. Email sent 10/23/15. "FW: Heat lamp bulbs". Itron benchmarked the HOU with their own analysis which resulted in 5,109 hours: 30.42 days/month; 3 months (summer) run 33% of time; 6 months run 50% of time; 3 months (winter) run full time.

Coincidence factor is taken from the IL TRM loadshape C04 – Non-residential Electric Loadshape.

Franklin Energy field experience

The cost of a replacement heat lamp bulb is sourced from an average of available products via online pricing for agriculture equipment and heat lamps. For more information on the cost of a heat lamp and the derivation of O&M cost savings, please see: “Swine Heat Pads_OM.xlsx”.

Utah State University Extension. Variable Frequency Drives for Irrigation Pumps Variable. Frequency Drives for Irrigation Pumps. Published March 2020

DEER 2008.

Average from IPL and MidAmerican VFD reported costs from rebate forms. IPL & MIdA VFD Costs.xls

Douglass, J. (2005). Induction Motor Efficiency Standards. Washington State University and the Northwest Energy Efficiency Alliance, Extension Energy Program, Olympia, WA, October 2005.

Estimated typical VFD efficiency, as sourced from; “Chapter 18: Variable Frequency Drive Evaluation Protocol”, The Uniform Methods Project: Methods for Determining Energy Efficiency Savings for Specific Measures, NREL, December 2014 (pg. 2)

Iowa State University Ag Extension, “Computing a Grain Storage Rental Rate”, October 2013. The useful life of grain storage bins was estimated to be between 15 and 25 years and the drying equipment useful life was estimated to be between 10 and 12 years. Combined with engineering judgement, the estimated measure life for a high efficiency grain dryer is estimated to be 20 years, which is corroborated by the Wisconsin Focus on Energy 2021 Technical Reference Manual, Cadmus, Publich Service Commission of Wisconsin – Energy Efficient Grain Dryer.

Alliant Energy Custom Rebate project data from 2012-2014; original Alliant table was modified, adding a new column of hours per year use and renaming labels.  Annual tier production quantities (bushels/yr) were divided by the maximum nominal tier capacities (bushels/hr @ rated capacity) to obtain Hours per Year @ Rated Capacity.  Arithmetic average hours of use was 336.3 per year.

Wisconsin Focus on Energy project data; 13 recent grain dryer projects in Wisconsin were used as the source of average pre- and post- moisture content (23% and 15%, respectively) and baseline and proposed dryer efficiency.

The National Corn Handbook. “Energy Conservation and Alternative Sources for Corn Drying.” NCH-14, page 3, Table 4. http://corn.agronomy.wisc.edu/Management/NCH.aspx

Wisconsin Focus on Energy project data; 13 recent grain dryer projects in Wisconsin were used as the source of average pre- and post- moisture content (23% and 15%, respectively) and baseline and proposed dryer efficiency.

“Tables for Weights and Measurement: Crops”. Murhpy, William J., , Accessed August 19, 2020.  Table shown was modified from the original by eliminating some redundant rows for similar crops, and by adding a new column that calculates pounds of moisture evaporated per Standard Bushel per 1% moisture reduction by the dryer.

"Reducing Grain Drying Costs". Sanford, Scott., University of Wisconsin Rural Energy Program, 2013. Notes 20-30% savings in bin dryers through the use of stirrers and ambient air low temperatiure drying. Based on this, 71% is used as a conservative value, but Actual values can be used if available. Accessed August 19, 2020.

Alliant Energy Custom Rebate project data from 2012-2014; same comments apply as in prior footnote.

The Standard Dryer Fan Power using the fan brakehorsepower equation.

The same Dryer Fan Power formula as in the above footnote.

University of Wisconsin-Madison Extension. “Low Cost Energy Conservation: Grain Drying (A3784-10).”  Tune-Ups are recommended annually because of the dusty environment components are subject to during the grain drying process. Although farms often defer grain dryer maintenance, the energy savings will not persist over multiple seasons.

From Wisconsin Focus on Energy 2020 Technical Reference Manual, Grain Dryer Tune-Up (pg. 44). Incremental costs are based on trade ally survey.

U.S. Department of Agriculture. “Energy Self-Assessment, Step 2: Informational Section.” Grain Drying Energy Efficiency and Energy Cost graph. Accessed May 2019. See Grain Dryer Tune Up Supporting Document for referenced graph. And University of Wisconsin–Madison, Extension. Wisconsin Energy Efficiency and Renewable Energy “Improving Energy Efficiency in Grain Drying: Fact Sheet.” December 2012.

The National Corn Handbook. “Energy Conservation and Alternative Sources for Corn Drying.” NCH-14, page 3, Table 4.

The National Corn Handbook. “Energy Conservation and Alternative Sources for Corn Drying.” NCH-14, page 3, Table 4.

University of Nebraska-Lincoln, Institute of Agriculture and Natural Resources. “Harvest Soybeans at 13% Moisture”.

University of Minnestota Extension. “Storing, drying, and handling wet soybeans”.

“Tables for Weights and Measurement: Crops”. Murhpy, William J. Table shown was modified from the original by eliminating some redundant rows for similar crops, and by adding a new column that calculates pounds of moisture evaporated per standard bushel per 1% moisture reduction by the dryer.

Conservative estimate – assumptions outlined in the Wisconsin Focus on Energy 2020 Technical Reference Manual, Grain Dryer Tune-Up (pg. 44).

Act on Energy Commercial Technical Reference Manual No. 2010-4, 9.2.2 Gas Boiler Tune-up

Act on Energy Commercial Technical Reference Manual No. 2010-4, 9.2.2 Gas Boiler Tune-up

Work Paper – Tune up for Boilers serving Space Heating and Process Load by Resource Solutions Group, January 2012

Custom site-specific utilization factors for greenhouses can be modeled using the greenhouse configuration and boiler capacity with USDA Virtual Grower software. https://www.ars.usda.gov/midwest-area/wooster-oh/application-technology-research/docs/virtual-grower/

ASHRAE Fundamentals 2017 Chapter 14 Appendix HDD at 65 °F was used to smooth the Virtual Grower software outputs.

Guidehouse evaluation results from tune-up efficiency improvement research for Peoples Gas and North Shore Gas through their C&I and Public Sector Prescriptive Rebate Program, their Small Business Program, and their Multi-Family Programs. The evaluation included project and population data from program year’s 2018 and 2019.

Guidehouse evaluation results from tune-up efficiency improvement research for Peoples Gas and North Shore Gas through their C&I and Public Sector Prescriptive Rebate Program, their Small Business Program, and their Multi-Family Programs. The evaluation included project and population data from program year’s 2018 and 2019.

Sanford, Scott, College of Agricultural and Life Science, University of Wisconsin Cooperative Extension. Using Greenhouse Curtains to Reduce Greenhouse Heating and Cooling Costs.

DEER 2008, http://www.deeresources.com/

‘Greenhouse Thermal Curtains’, Pacific Gas & Electric Company, PGECOAGR101, 2008

Bartok, John, Department of Natural Resources Management and Engineering, University of Connecticut, Natural Resource, Agriculture, and Engineering Service (NRAES) Cooperative Extension, Energy Conservation for Commercial Greenhouses, 2001 Revision, Table 4-1 Heat loss through blanket and roof, average of all material types.

Bartok, Table 1-2 Heat flow u-value for double layer polyethlene film.

Bartok, Table 4-1 Heat loss through blanket and roof, average of all material types.

Bartok, Table 1-2 Heat flow u-value for single layer polyethlene film.

ASHRAE HVAC Applications, Design for Greenhouses, ch. 25.2.1 Table 4, Suggested Design Air Changes for old construction with good maintenance.

Bartok, Chapter 6, page 42.

ASHRAE ch. 25.2.2 Table 10, Suggested Radiant Energy, Duration, and Time of Day for Supplemental Lighting in Greenhouses, average of all W/ft2.

ASHRAE ch. 25.2.2 Table 10, Suggested Radiant Energy, Duration, and Time of Day for Supplemental Lighting in Greenhouses, average of all hours.

Bartok, John, Department of Natural Resources Management and Engineering, University of Connecticut, Natural Resource, Agriculture, and Engineering Service (NRAES) Cooperative Extension, Energy Conservation for Commercial Greenhouses, 2001 Revision, Chapter 1, page 4.

Bartok, Chapter 1, page 5.

Itron, Inc. 2005. 2004-2005 Database for Energy Efficiency Resources (DEER) Update Study – Final Report. Prepared for Southern California Edison.

Itron, Inc. 2014. 2010-2012 WO017 Ex Ante Measure Cost Study Final Report. Prepared for the California Public Utilities Commission.

Bartok, Table 1-2 Heat flow u-value for double layer polyethlene film.

Bartok, Table 1-2 Heat flow u-value for IR-inhibited double layer polyethlene film.

Bartok, Table 1-2 Heat flow u-value for single layer polyethlene film.

ASHRAE HVAC Applications, Design for Greenhouses, ch. 25.2.1 Table 4, Suggested Design Air Changes for old construction with good maintenance.

Bartok, Chapter 6, page 42.

ASHRAE ch. 25.2.2 Table 10, Suggested Radiant Energy, Duration, and Time of Day for Supplemental Lighting in Greenhouses, average of all W/ft2.

ASHRAE ch. 25.2.2 Table 10, Suggested Radiant Energy, Duration, and Time of Day for Supplemental Lighting in Greenhouses, average of all hours.

ENERGY STAR Program Requirements for Product Specification for Residential Water Heaters, v4.0, effective January 5, 2022. ENERGY STAR Program Requirements Product Specification for Commercial Water Heaters, v2.0, effective October 1, 2018.

Minimum performance rating assumes a high usage draw pattern of 84 gallons per day. A typical dairy in Illinois is estimated to use 131.7 gallons of hot water per day. Please see ‘4.1.10 Dairy Refrigeration Heat Recovery’ for the derivation of the hot water heated on an average dairy farm. Note that minimum performance requirements for residential water heaters toggle between EF and UEF depending on size category based on ‘Code of Federal Regulations, federal standards for residential water heaters, 10 CFR 432.32(d)’. Commercial water heaters must meet a minimum Thermal Efficiency (TE) and are subject to maximum standby loss requirements of Q/800 + 110 x √Vr where Q is the input rating in Btu/hr per ‘2019 Building Energy Efficiency Standards; 5.3 Mandatory Requirements for Water Heating’, California Energy Commission.

Additional reference stating >20 years from the US DOE Energy Savers for Tankless or Demand-Type Water Heaters, and 15 years from the ‘New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs’, v8.0, effective January 1, 2021.

From the 2010-2012 WO017 Ex Ante Measure Cost Study Final Report from the California Public Utilities Commission Table 3-12.

Coincidence factor based on the average wattage in peak period divided by the maximum wattage from Itron eShape data for Missouri, calibrated to Illinois loads.

Water heating temperature for dairy farms: The cycle for cleaning needs 170 °F to start and cannot drop below 120°F by the end of the wash cycle. ‘Hot Water for Dairy Farms’, PHCP Pros, Harvey Ramer, May 11, 2017

Expected temperature a refrigeration heat recovery unit can pre-heat well water up to. For more detail, please see: ‘4.1.10 Dairy Refrigeration Heat Recovery.’

Average value assuming 50% of farms have Dairy Refrigeration Heat Recovery system

‘4.1.10 Dairy Refrigeration Heat Recovery’ details average default values for hot water use and number of milking cows if unknown. The 1.30 gallons of hot water per day is calculated from (131.7 GPD/101 cows). This value is corroborated by milking system washing hot water consumption of 5L per cow (1.32 gallons per cow) per Shortall J. et al. and supported by data from NYSERDA Dairy Farm Audit Summary, in which 10 dairy farms averaged of 1.40 gallons of hot water per cow per day based on measured electric water heater energy consumption and assumed 98% efficiency.

Full load hours assumption based on Wh/Max W Ratio from Itron eShape data for Missouri, calibrated to Illinois loads.

Coincidence factor based on Average W in peak period/Max W from Itron eShape data for Missouri, calibrated to Illinois loads.

ENERGY STAR Commercial Ovens Key Product Criteria, version 2.2, effective October 7, 2015

Ibid. Pan capacity is defined as the number of steam table pans the combination oven is able to accommodate as

per the ASTM F-1495-05 standard specification.

The measure life is sourced from the Food Service Technology Center’s energy savings calculator for combination ovens.

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985

Algorithms and assumptions derived from ENERGY STAR Commercial Kitchen Equipment Savings Calculator

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985

Algorithms and assumptions derived from ENERGY STAR Commercial Kitchen Equipment Savings Calculator

2008 Database for Energy-Efficiency Resources (DEER), Version 2008.2.05, “Effective/Remaining Useful Life Values”, California Public Utilities Commission, December 16, 2008.

Incremental costs are based on the Northwest Regional Technical Forum, ENERGY STAR Version 4.0 Analysis. For cost calculation details, see the CostData&Analysis tab within the file Commercial Refrigerators & Freezers_Costs_Nov 2017.xlsm.

The CF for Commercial Refrigeration was calculated based upon the Ameren provided eShapes

Federal standards for equipment manufactured on or after March 27, 2017: 10 CFR §431.66 - Energy Conservation Standards for Commercial Refrigerators, Freezers and Refrigerator-Freezers.

ENERGY STAR Program Requirements for Commercial Refrigerators and Freezers Partner Commitments Version 4.0, effective March 27, 2017

California DEER 2008 which is also used by both the Food Service Technology Center and ENERGY STAR®.

Source for incremental cost for efficient natural gas steamer is RSG Commercial Gas Steamer Workpaper, January 2012.

Source for efficient electric steamer incremental cost is $2,490 per 2009 PG&E Workpaper - PGECOFST104.1 - Commercial Steam Cooker - Electric and Gas as reference by KEMA in the ComEd C & I TRM.

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985.Unknown is an average of other location types

Food Service Technology Center 2011 Savings Calculator

Food Service Technology Center 2011 Savings Calculator

Production capacity per Food Service Technology Center 2011 Savings Calculator of 23.3333 lb/hr per pan for electric baseline steam cookers and 21.6667 lb/hr per pan for natural gas baseline steam cookers.  ENERGY STAR® savings calculator uses 23.3 lb/hr per pan for both electric and natural gas baseline steamers.

ENERGY STAR Commercial Kitchen Equipment Savings Calculator, Steam Cooker Calculations

Reference Food Service Technology Center 2011 Savings Calculator values as used by Consortium for Energy Efficiency, Inc. for baseline electric and natural gas steamer heavy cooking load energy efficiencies.

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985.

Unknown is average of other locations

Reference amount used by both Food Service Technology Center and ENERGY STAR® savings calculator

Reference information from the Food Service Technology Center siting that ENERGY STAR® steamers are not typically operated in constant steam mode, but rather are used in timed mode.  Reference ENERGY STAR Commercial Kitchen Equipment Savings Calculator, Steam Cooker Calculation. Both baseline & efficient steamer mode values should be considered for users in Illinois market.

Food Service Technology Center 2011 Savings Calculator.

Production capacity per Food Service Technology Center 2011 Savings Calculator of 18.3333 lb/hr per pan for gas ENERGY STAR® steam cookers and 16.6667  lb/hr per pan for electric ENERGY STAR® steam cookers.  ENERGY STAR® savings calculator uses 16.7 lb/hr per pan for electric and 20 lb/hr for natural gas ENERGY STAR® steamers.

Reference Food Service Technology Center 2011 Savings Calculator values as used by Consortium for Energy Efficiency, Inc. for Tier 1A and Tier 1B qualified electric and natural gas steamer heavy cooking load energy efficiencies, as sourced from ENERGY STAR Program Requirements Product Specification for Commercial Steam Cookers, version 1.2, effective August 1, 2013.

Reference ENERGY STAR Commercial Kitchen Equipment Savings Calculator, Steam Cooker Calculations

Ibid.

Ohio TRM which references 2002 Food Service Technology Center "Commercial Cooking Appliance Technology Assessment" Chapter 8: Steamers.  This is also used by the ENERGY STAR Commercial Kitchen Equipment Savings Calculator.  11,000 Btu/preheat is from 72,000 Btu/hr * 15 min/hr /60 min/hr for gas steamers and 0.5 kWh/preheat is from 6 kW/preheat * 15 min/hr / 60 min/hr

Reference Food Service Technology Center 2011 Savings Calculator values for Baseline Preheat Energy.

Reference Food Service Technology Center 2011 Savings Calculator values as used by Consortium for Energy Efficiency, Inc. for baseline electric and natural gas steamer heavy cooking load energy efficiencies.

Ibid.

Amount used by both Food Service Technology Center and ENERGY STAR® savings calculator

Reference ENERGY STAR Commercial Kitchen Equipment Savings Calculator, Steam Cooker Calculations.

Ibid.

Ibid.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’. Note that the Commercial Steam Cooker does not discharge its water into the wastewater system so only the water supply factor is used here.

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985.

FSTC (2002). Commercial Cooking Appliance Technology Assessment. Chapter 8: Steamers.

Source Consortium for Energy Efficiency, Inc. September 2010 "Program Design Guidance for Steamers" for Tier 1A and Tier 1B water requirements.  Ohio Technical Reference Manual 2010 for 10 gal/hr water consumption which can be used when Tier level is not known.

Source for 365.25 days/yr is ENERGY STAR® savings calculator which references Food Service Technology research on average use, 2009.

See ‘Arkansas Deemed TRM Table for GasFoodService.xls’ from v3.0 Arkansas Technical Reference Manual.

Ibid.

The Resource Solutions Group Commercial Conveyor Oven – Gas workpaper from January 2012; Commercial Gas Conveyor Oven – Large Gas Savings (therms/unit).

Version 2.2. of the ENERGY STAR specification.

Lifetime from ENERGY STAR Commercial Kitchen Equipment Savings Calculator, Oven Calculations, which cites reference as “FSTC research on available models, 2009”.

Measure cost from ENERGY STAR Commercial Kitchen Equipment Savings Calculator which cites reference as “EPA research on available models using AutoQuotes, 2010”.

Algorithms and assumptions derived from ENERGY STAR Commercial Kitchen Equipment Savings Calculator, Oven Calculations.

Lifetime from ENERGY STAR Commerical Kitchen Equipment Savings Calculator which cites reference as “EPA/FSTC research on available models, 2013”

Measure cost from ENERGY STAR Commercial Kitchen Equipment Savings Calculator which cites reference as “Difference between a similar ENERGY STAR and non-qualifying model EPA research using AutoQuotes, 2016 ( for high/low temp undercounter/single door) and 2012 ( all other types)”.

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985

Algorithms and assumptions derived from ENERGY STAR Commercial Kitchen Equipment Savings Calculator.

Booster water heater energy only applies to high-temperature dishwashers.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985.

Lifetime from ENERGY STAR Commercial Kitchen Equipment Savings Calculator ,which cites reference as “FSTC research on available models, 2009.

Measure cost from ENERGY STAR Commercial Kitchen Equipment Savings Calculator (last updated March 2021) which cites reference as “Difference between a similar ENERGY STAR and non-qualifying model, EPA research using AutoQuotes, October 2020”.

Values taken from Minnesota Technical Reference Manual, (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985.

Algorithms and assumptions derived from ENERGY STAR Commercial Kitchen Equipment Savings Calculator (last updated March 2021).

Algorithms and assumptions derived from ENERGY STAR Commercial Kitchen Equipment Savings Calculator (last updated March 2021).

Lifetime from ENERGY STAR Commercial Kitchen Equipment Calculator, Commercial Griddle Calculations, which cites reference as “FSTC research on available models, 2009”.

Measure cost from ENERGY STAR Commercial Kitchen Equipment Calculator, which cites reference as “EPA research on available models using AutoQuotes, 2010”.

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al.,  May 1985.

Algorithms and assumptions derived from ENERGY STAR Griddle Commercial Kitchen Equipment Savings Calculator.

Duel fuel griddles are usually electric top plates and gas bottom plates, often used by fast food restaurants. As per DOE workpaper "Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances (2015 Update)" these models have a “second heating plate that is lowered on top of the food and used to simultaneously cook both sides." It therefore is reasonable to assume half savings are attributed to gas v electric.

Lifetime from ENERGY STAR Commercial Kitchen Equipment Calculator, Hot Food Holding Cabinet Calculations, which cites reference as “FSTC research on available models, 2009”.

Measure cost from ENERGY STAR Commercial Kitchen Equipment Calculator, which cites reference as “EPA research on available models using AutoQuotes, 2010”.

Values taken from Minnesota Technical Reference Manual (Version 2.2, effective May 2, 2018), ‘Electric Oven and Range’ measure and are based upon “Project on Restaurant Energy Performance-End-Use Monitoring and Analysis”, Appendixes I and II, Claar, et. al., May 1985.

Algorithms and assumptions derived from ENERGY STAR Commercial Kitchen Equipment Savings Calculator.

Based on DOE Technical Support Document, 2014 as recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Incremental costs from ENERGY STAR Commercial Kitchen Equipment Savings Calculator.  Calculator cites EPA research using AutoQuotes, 2016.

Use the appropriate equipment type baseline and ice harvest rate range when calculating the savings for a CEE Tier Advanced ice maker.

Duty cycle varies considerably from one installation to the next. TRM assumptions from Vermont, Wisconsin, and New York vary from 40 to 57%, whereas the ENERGY STAR Commercial Ice Machine Savings Calculator assumes a value of 75%. A field study of eight ice machines in California indicated an average duty cycle of 57% (“A Field Study to Characterize Water and Energy Use of Commercial Ice-Cube Machines and Quantify Saving Potential”, Food Service Technology Center,  December 2007). Furthermore, a report prepared by ACEEE assumed a value of 40% (Nadel, S., Packaged Commercial Refrigeration Equipment: A Briefing Report for Program Planners and Implementers, ACEEE, December 2002). The value of 57% was utilized since it appears to represent a high quality data source.

Unit is assumed to be connected to power 24 hours per day, 365.25 days per year.

AHRI Certification Directory, Automatic Commercial Ice Makers, Accessed on 7/7/10.

Baseline for TOS programs is calculated using the maximum flow rate for each product class in 10 CFR 431.266, Energy Efficiency Program for Certain Commercial and Industrial Equipment weighted by estimated 2018 shipments for each product class from Table 3.6.1: U.S. DOE, “Technical Support Document: Energy Efficiency Program for Consumer Products and Commercial and Industrial Equipment: Commercial Prerinse Spray Valves,” December 2015.

Average flow rate of spray valve replaced through direct install programs from DNV-GL, “Impact Evaluation of National Grid Rhode Island C&I Prescriptive Gas Pre-Rinse Spray Valve Measure – Final Report,” September 30, 2014, page 6-6.

Measure life from U.S. DOE, “Technical Support Document: Energy Efficiency Program for Consumer Products and Commercial and Industrial Equipment: Commercial Prerinse Spray Valves,” December 2015, page 8-13."

Incremental measure cost based on U.S. DOE, “Technical Support Document: Energy Efficiency Program for Consumer Products and Commercial and Industrial Equipment: Commercial Prerinse Spray Valves,” December 2015, page 8-1.

Total installed cost is the manufacturer selling price ($35.40) from Table 8.2.1 multiplied by the retailer markup (1.52) from Table 8.2.2: U.S. DOE, “Technical Support Document: Energy Efficiency Program for Consumer Products and Commercial and Industrial Equipment: Commercial Prerinse Spray Valves,” December 2015.  It is assumed that programs typically install spray valves only when other kitchen equipment is also being installed, and therefore, there are no additional labor costs associated with spray valve installations.

If unknown, assume a 70 degree temperature rise from Tin per Food Service Technology Center calculator assumptions to account for variations in mixing and water heater efficiencies.

Table 4 in Chen, et. al., “Calculating Average Hot Water Mixes of Residential Plumbing Fixtures”, June 2020, reports a value of 50.7°F for inlet water temperature for U.S. Census Division 3.

Electric water heaters have recovery efficiency of 98%, as sourced from available products on the AHRI Certification Directory.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

IECC 2015, Table C404.2, Minimum Performance of Water-Heating Equipment

In order to calculate energy savings, water savings must first be calculated

Baseline for TOS programs is calculated using the maximum flow rate for each product class in 10 CFR 431.266, Energy Efficiency Program for Certain Commercial and Industrial Equipment weighted by estimated 2018 shipments for each product class from Table 3.6.1: U.S. DOE, “Technical Support Document: Energy Efficiency Program for Consumer Products and Commercial and Industrial Equipment: Commercial Prerinse Spray Valves,” December 2015.

Average flow rate of spray valve replaced through direct install programs from DNV-GL, “Impact Evaluation of National Grid Rhode Island C&I Prescriptive Gas Pre-Rinse Spray Valve Measure – Final Report,” September 30, 2014, page 6-6.

A new pre-rinse spray valve is assumed to be 20% more efficient than the federal standard.

Hours primarily based on PG& E savings estimates, algorithms, sources (2005), Food Service Pre-Rinse Spray Valves with review of 2010 Ohio Technical Reference Manual and Act on Energy Business Program Technical Resource Manual Rev05.

Average ISR for pre-rinse spray valves distributed to ComEd Small Business Kit customers in CY2018, CY2019, and CY2020. ISR was calculated based on 262 telephone surveys from restaurant and fire station participants. Please see file “SB Kits Survey Analysis TRMv10 Support.xlsx”

Lifecycle determined from Food Service Technology Center Gas Broiler Life-Cycle Cost Calculator and from FSTC Broiler Technology Assessment.

See ‘Arkansas Deemed TRM Table for GasFoodService.xls’ from v3.0 Arkansas Technical Reference Manual.

Assumptions derived from Food Service Technology Center Gas Broiler Life-Cycle Cost Calculator and from FSTC Broiler Technology Assessment, Section 4: Broilers.

Typical annual operating time from FSTC Broiler Technology Assessment, Table 4.3.

Typical preheat time from FSTC Broiler Technology Assessment.

Duty cycle from FSTC Broiler Technology Assessment, Table 4.3.

Lifecycle determined from Food Service Technology Center Gas Oven Life-Cycle Cost Calculator.

See ‘Arkansas Deemed TRM Table for GasFoodService.xls’ from v3.0 Arkansas Technical Reference Manual.

Median rated energy input for rotisserie ovens from FSTC Oven Technology Assessment, Section 7: Ovens, Table 7.2.

Infrared energy input rate calculated based on efficient energy input rate of 50,000 Btu/hr, baseline cooking efficiency of 25%, and infrared cooking efficiency of 45%. Efficiencies and rates derived from FSTC Gas Rotisserie Oven Test Reports and FSTC Oven Technology Assessment.

Duty cycle from Food Service Technology Center Oven Technical Assessment, Table 7.2.

Typical operating hours based on oven operating schedule of 8 hours per day, 6 days per week, 52 weeks per year, provided in Food Service Technology Center Oven Technical Assessment, Table 7.2.

Lifecycle determined from Food Service Technology Center Gas Broiler Life-Cycle Cost Calculator and from FSTC Broiler Technology Assessment.

See ‘Arkansas Deemed TRM Table for GasFoodService.xls’ from v3.0 Arkansas Technical Reference Manual.

Median rated energy input for salamander broilers from FSTC Broiler Technology Assessment, Section 4: Broilers, Table 4.3.

Calculated energy input rate based on baseline energy input rate of 38,500 Btu/hr, baseline cooking efficiency of 22.5%, and infrared cooking efficiency of 35%.

Duty cycle from Food Service Technology Center Broiler Technical Assessment, Table 4.3.

Typical operating hours based on broiler operating schedule of 8 hours per day, 6 days per week, 52 weeks per year, provided in Food Service Technology Center Broiler Technical Assessment, Table 4.3.

Lifecycle determined from Food Service Technology Center Gas Broiler Life-Cycle Cost Calculator and from FSTC Broiler Technology Assessment.

See ‘Arkansas Deemed TRM Table for GasFoodService.xls’ from v3.0 Arkansas Technical Reference Manual.

Baseline energy input rate calculated based on efficient energy input rate of 90,000 Btu/hr, baseline cooking efficiency of 25%, and infrared cooking efficiency of 40%.

Median rated energy input for upright broilers from FSTC Broiler Technology Assessment, Section 4.0: Broiler, Table 4.3.

Duty cycle from Food Service Technology Center Broiler Technical Assessment, Table 4.3.

Typical operating hours based on broiler operating schedule of 8 hours per day, 6 days per week, 52 weeks per year, provided in Food Service Technology Center Broiler Technical Assessment, Table 4.3.

“Commercial Kitchen Ventilation: An Energy Efficiency Program Administrator’s Guide to Demand Control Ventilation”, CEE, October 2010 (pg. 9). The 20-year measure life estimate is based on interviews with manufacturer and industry experts.

The incremental costs were derived from Southern California Edison (SCE) program data on 72 demand control kitchen ventilation project installations between 2013 and 2017 (see; “SCE13CC008._Exhaust_Hood_DCKV_Exhaust_CFM_and_Cost_Field_Data.xlsx”). For reference, the baseline measure costs were factored out accordingly, being obtained from costs for five kitchen exhaust fans from RSMeans online in 2017. For more detail on the source of these cost estimates, please see the California eTRM – Exhaust Hood Demand Controlled Ventilation, Commercial measure (SWFS012-01), March 4, 2020.

Based on data provided in PGE Workpaper, Commercial Kitchen Demand Ventilation Controls, PGECOFST116, June 1, 2009. See ‘Kitchen DCV.xls’ for details.

Based on data provided in PGE Workpaper, Commercial Kitchen Demand Ventilation Controls, PGECOFST116, June 1, 2009. See ‘Kitchen DCV.xls’ for details.

Based on data provided in PGE Workpaper, Commercial Kitchen Demand Ventilation Controls, PGECOFST116, June 1, 2009. See ‘Kitchen DCV.xls’ for details.

Average of units in PGE Workpaper, Commercial Kitchen Demand Ventilation Controls, PGECOFST116, June 1, 2009.

Food Service Technology Center Outside Air Load Calculator, with inputs of one cfm, and hours from Commercial Kitchen Demand Ventilation Controls (Average 17.8 hours a day 4.45 am to 10.30 pm). Savings for Rockford, Chicago, and Springfield were obtained from the calculator; values for Belleview and Marion were obtained by using the average savings per HDD from the other values.

Work Paper WPRRSGNGRO301 CLEAResult"Boiler Tune-Up" which cites Focus on Energy Evaluation Business Programs: Deemed Savings Manual V1.0, PA Consulting, KEMA, March 22, 2010.

See ‘Arkansas Deemed TRM Table for GasFoodService.xls’ from v3.0 Arkansas Technical Reference Manual.

Ibid.

See ‘Arkansas Deemed TRM Table for GasFoodService.xls’ from v3.0 Arkansas Technical Reference Manual.

Lifecycle determined from Food Service Technology Center Gas Rack Oven Life-Cycle Cost Calculator and from FSTC Oven Technology Assessment.

See ‘Arkansas Deemed TRM Table for GasFoodService.xls’ from v3.0 Arkansas Technical Reference Manual.

Assumptions derived from Food Service Technology Center Gas Rack Oven Life-Cycle Cost Calculator, FSTC Oven Technology Assessment, Section 7: Ovens, and from FSTC Gas Double Rack Oven Test Reports.

Median rated energy input for rack ovens from FSTC Oven Technology Assessment, Section 7: Ovens.

Average baking efficiency of double rack oven from FSTC Gas Double Rack Oven Test Reports.

Duty cycle from FSTC Gas Double Rack Oven Test Reports on various double rack ovens.

Typical operating hours based on oven operating schedule of 12 hours per day, 6 days per week, 52 weeks per year, provided in FSTC Gas Double Rack Oven Test Reports on various double rack ovens.

Food Service Technology Center (FSTC). Default value from life cycle cost calculator for electric ovens.

Based on data from the Regional Technical Forum for the Northwest Council (Commercial Cooking Convection Oven Calculator, UES Measure Workbook) using actual list prices from 2018, see “ComCookingConvectionOven_v4_0.xlsm”.

Minnesota Technical Reference Manual, (version 3.2, effective January 7, 2021), Commercial Food Service - Electric Oven and Range, page 481. Unknown is an average of other location types.

Minnesota Technical Reference Manual, (version 3.2, effective January 7, 2021), Commercial Food Service - Electric Oven and Range, page 481. Unknown is an average of other location types.

Food Service Technology Center (FSTC). Default value from life cycle cost calculator for electric ovens.

Food Service Technology Center (2002).  Commercial Cooking Appliance Technology Assessment.  Prepared by Don Fisher.  Chapter 7: Ovens.

American Society for Testing and Materials.  Industry standard for Commercial Ovens.

Based on data from the Regional Technical Forum for the Northwest Council (Commercial Cooking Convection Oven Calculator, UES Measure Workbook), see “ComCookingConvectionOven_v4_0.xlsm”.

Assumptions derived from ENERGY STAR Commercial Kitchen Equipment Savings Calculator (last updated March 2021).

Based on data from the Regional Technical Forum for the Northwest Council (Commercial Cooking Convection Oven Calculator, UES Measure Workbook), Table 5: Idle rates, Energy Efficiencies, and Preheat rates Data (Data compiled from Caenergywise Qualified Product List, eTRM baseline data, stakeholder outreach, and ENERGY STAR's Qualified Product List).

Ibid.

Pacific Gas & Electric Work Paper PGECOFST101 Commercial Convection Oven-Electric, Revision 6, 8/2016.

Alignment with existing dipper well program measure lives in California. Dipper Well Replacement Field Evaluation

Report, Frontier Energy, November 2017.
  https://fishnick.com/publications/fieldstudies/Dipper_Well_Replacement_Field_Evaluation_ICP.pdf

Google Shopping search for the term “water efficient dipper well”.  Results include the “Conservewell” from KaTom Restaurant Supply for $300.

Google Shopping search for the term “dipper well system”. Results show various baseline models that range from $100 to $200.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

Michael Slater and Amin Delagah, “Dipper Well Replacement Field Evaluation Report”, Frontier Energy Report #50115-R0, November 2017. Prepared for the Metropolitan Water District of Southern California. http://www.bewaterwise.com/pdfs/ICP/2015ICP-DipperWellFrontierEnergy.pdf

Michael Slater and Amin Delagah, “Dipper Well Replacement Field Evaluation Report”, Frontier Energy Report #50115-R0, November 2017. Prepared for the Metropolitan Water District of Southern California. http://www.bewaterwise.com/pdfs/ICP/2015ICP-DipperWellFrontierEnergy.pdf

Design & Engineering Services Customer Service Organization Southern California Edison, October 2012, Vacuum-Sealing and Packaging Machines For Food Service Applications Field Test Et10sce1450, pg 1.

The October 2012 SCE field test (mentioned above) was a study based datalogger information over six weeks of units in 199 stores.

Based on similar equipment types, as there is not a standard for shrink wrappers listed. The Illinois TRM v9’s kitchen equipment measure lives range from 5-20 years.  70% of the kitchen equipment measures have a 12 year measure life, but half of these are gas-only measures.  We used Efficient Dipper Wells’ measure life of 10 years as both measures save energy by replacing continuously running equipment with equipment that only runs when needed. Both On-Demand Package Sealers and Efficient Dipper Wells also may have higher regular maintenance needs than the other Kitchen equipment - to prevent clogging.

Commercial Vacuum Sealer costs – Manual (Baseline) & Automatic. Please see pdf of https://www.webstaurantstore.com/ data sets.

Design & Engineering Services Customer Service Organization Southern California Edison, October 2012, Vacuum-Sealing And Packaging Machines For Food Service Applications Field Test Et10sce1450 – Note: this was a study based datalogger information over six weeks of units in 199 stores.

Ibid

ESF assumes On-Demand Package Sealer is actively heating 10% of the Hours of Use. The ESF source assumption is that the On-Demand sealers will be in use an average of six minutes of every hour.  Currently there is no logged data that captures the total amount of time the efficient machines run, however once we get that data is available from the program, this value will be updated.

All Residential sized Federal Standards are from DOE Standard 10 CFR 430, Residential-Duty and Commercial Federal Standard are from DOE Standard 10 CFR 431.

It is assumed that tanks <75,000Btu/h and >55 gallons will not be eligible measures due to the high baseline.

Definitions provided in 10 CFR 430, Subpart B, Appendix E, Section 5.4.1.

DEER 08, EUL_Summary_10-1-08.xls.

As recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Ohio Technical Reference Manual 8/2/2010 referencing CenterPoint Energy-Triennial CIP/DSM Plan 2010-2012 Report; Additional reference stating >20 years is soured from the US DOE Energy Savers for Tankless or Demand-Type Water Heaters.

Ibid.

Cost information is based upon data from “2010-2012 WA017 Ex Ante Measure Cost Study Draft Report”, Itron, February 28, 2014. See “NR HW Heater_WA017_MCS Results Matrix - Volume I.xls” for more information.

Act on Energy Commercial Technical Reference Manual, Table 9.6.1-4

Act on Energy Technical Reference Manual, Table 9.6.2-3

Minnesota Center for Energy and Environment, Low contractor estimate used to reflect less labor required in new construction of venting.

Costs for <2.6 UEF are based upon averages from the NEEP Phase 3 Incremental Cost Study. The assumption for higher efficiency tanks is based upon averaged from NEEP Phase 4 Incremental Cost Study. See ‘HPWH Cost Estimation.xls’ for more information.

Coincidence factor based on Average W in peak period/Max W from Itron eShape data for Missouri, calibrated to Illinois loads.

Table 4 in Chen, et. al., “Calculating Average Hot Water Mixes of Residential Plumbing Fixtures”, June 2020, reports a value of 50.7°F for inlet water temperature for U.S. Census Division 3.

Methodology based on Cadmus analysis. Annual hot water usage in gallons based on CBECS (2012) and RECS (2009) consumption data of East North Central (removed outliers of 1,000 kBtuh or less) to calculate hot water usage. Annual hot water gallons per tank size gallons based on the tank sizing methodology found in ASHRAE 2011 HVAC Applications. Chapter 50 Service Water Heating. Demand assumptions (gallons per day) for each building type based on ASHRAE Chapter 50 and to LBNL White Paper. LBL-37398 Technology Data Characterizing Water Heating in Commercial Buildings: Application to End Use Forecasting. Assumes hot water heater efficiency of 80%.

According to CBECS 2012 “Lodging” buildings include Dormitories, Hotels, Motel or Inns and other Lodging and “Nursing” buildings include Assisted Living and Nursing Homes.

Methodology based on Cadmus analysis. Annual hot water usage in gallons based on CBECS (2012) and RECS (2009) consumption data of East North Central (removed outliers of 1,000 kBtuh or less) to calculate hot water usage. Annual hot water gallons per tank size gallons based on the tank sizing methodology found in ASHRAE 2011 HVAC Applications. Chapter 50 Service Water Heating. Demand assumptions (gallons per day) for each building type based on ASHRAE Chapter 50 and to LBNL White Paper. LBL-37398 Technology Data Characterizing Water Heating in Commercial Buildings: Application to End Use Forecasting. Assumes hot water heater efficiency of 80%.

According to CBECS 2012 “Lodging” buildings include Dormitories, Hotels, Motel or Inns and other Lodging and “Nursing” buildings include Assisted Living and Nursing Homes.

All Residential sized Federal Standards are from DOE Standard 10 CFR 430, Residential-Duty and Commercial Federal Standard are from DOE Standard 10 CFR 431.

It is assumed that tanks <75,000Btu/h and >55 gallons will not be eligible measures due to the high baseline.

Definitions provided in 10 CFR 430, Subpart B, Appendix E, Section 5.4.1.

This algorithm calculates the heat removed from the air by subtracting the HPWH electric consumption from the total water heating energy delivered. This is then adjusted to account for location of the HP unit and the coincidence of the waste heat with cooling requirements, the efficiency of the central cooling, and latent cooling demands.

Note unconditioned means a space that is not intentionally heated via furnace vents or boiler radiators. The presence of and/or leakage from a heating system in a space doesn’t in itself imply the space is conditioned.

This is estimated based on the percentage of lighting savings that result in reduced cooling loads (lighting is used as a proxy for hot water heating since load shapes suggest their seasonal usage patterns are similar). This is based on the WHFe for unknown non-residential buildings (1.08) and assuming an average cooling COP of 3.08 (1.08 = 1 + 0.246/3.08).

A sensible heat ratio (SHR) of 0.75 corresponds to a latent multiplier of 4/3 or 1.33. SHR of 0.75 for typical split system from page 10 of “Controlling Indoor Humidity Using Variable-Speed Compressors and Blowers” by M. A. Andrade and C. W. Bullard, 1999: www.ideals.illinois.edu/bitstream/handle/2142/11894/TR151.pdf

This is estimated based on the percentage of lighting savings that result in increased heating loads (lighting is used as a proxy for hot water heating since load shapes suggest their seasonal usage patterns are similar). The WHFh for unknown non-residential buildings is 35%.

These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Heat Pumps was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time means that using the minimum standard is appropriate. An 85% distribution efficiency is then applied to account for duct losses for heat pumps.

Full load hours assumption based on Wh/Max W Ratio from Itron eShape data for Missouri, calibrated to Illinois loads.

Coincidence factor based on Average W in peak period/Max W from Itron eShape data for Missouri, calibrated to Illinois loads.

All Residential sized Federal Standards are from DOE Standard 10 CFR 430, Residential-Duty and Commercial Federal Standard are from DOE Standard 10 CFR 431.

Definitions provided in 10 CFR 430, Subpart B, Appendix E, Section 5.4.1.

Water heaters (WH) require annual maintenance. There are different levels of effort for annual maintenance depending if the unit is gas or electric, tanked or tankless. Electric and gas tank water heater manufacturers recommend an annual tank drain to clear sediments. Also recommended are “periodic” inspections by qualified service professionals of operating controls, heating element and wiring for electric WHs and thermostat, burner, relief valve internal flue-way and venting systems for gas WHs. Tankless WH require annual maintenance by licensed professionals to clean control compartments, burners, venting system and heat exchangers. This information is from WH manufacturer product brochures including GE, Rennai, Rheem, Takagi and Kenmore.  References for incremental O&M costs were not found. Therefore the incremental cost of the additional annual maintenance for tankless WH is estimated at $100.

Workpaper WPSCGNRWH150827A, Laminar Flow Restrictors For Hospitals and Health Care Facilities.

As recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Direct-install price per faucet assumes cost of aerator and install time. (2011, Market research average of $3 and assess and install time of $5 (20min @ $15/hr).

Direct install price per faucet assumes cost of LFR ($7.27) and install time ($7) (Southern California Gas Company, Workpaper WPSCGNRWH150827A Revision #0, September, 2015).

This algorithm calculates the amount of energy saved per aerator by determining the fraction of water consumption savings for the upgraded fixture. Due to the distribution of water consumption by fixture type, as well as the different number of fixtures in a building, several variables must be incorporated.

Table HC8.9. Water Heating in U.S. Homes in Midwest Region, Divisions, and States,  2009 (RECS).

DeOreo, B., and P. Mayer. Residential End Uses of Water Study Update. Forthcoming. ©2015 Water Research Foundation. Reprinted With Permission.

Measurement should be based on actual average flow consumed over a period of time rather than a onetime spot measurement for maximum flow. Studies have shown maximum flow rates do not correspond well to average flow rate due to occupant behavior which does not always use maximum flow.

2008, Schultdt, Marc, and Debra Tachibana. Energy related Water Fixture Measurements: Securing the Baseline for Northwest Single Family Homes. 2008 ACEEE Summer Study on Energy Efficiency in Buildings. Page 1-265.

Using measured flow rate assumption from Workpaper WPSCGNRWH150827A, Laminar Flow Restrictors For Hospitals and Health Care Facilities.

Average retrofit flow rate for kitchen and bathroom faucet aerators from sources 2, 4, 5, and 7. This accounts for all throttling and differences from rated flow rates. Assumes all kitchen aerators at 2.2 gpm or less and all bathroom aerators at 1.5 gpm or less. The most comprehensive available studies did not disaggregate kitchen use from bathroom use, but instead looked at total flow and length of use for all faucets. This makes it difficult to reliably separate kitchen water use from bathroom water use. It is possible that programs installing low flow aerators lower than the 2.2 gpm for kitchens and 1.5 gpm for bathrooms will see a lower overall average retrofit flow rate.

Measurement should be based on actual average flow consumed over a period of time rather than a onetime spot measurement for maximum flow. Studies have shown maximum flow rates do not correspond well to average flow rate due to occupant behavior which does not always use maximum flow.

2008, Schultdt, Marc, and Debra Tachibana. Energy related Water Fixture Measurements: Securing the Baseline for Northwest Single Family Homes. 2008 ACEEE Summer Study on Energy Efficiency in Buildings. Page 1-265.

Using measured flow rate assumption from Workpaper WPSCGNRWH150827A, Laminar Flow Restrictors For Hospitals and Health Care Facilities.

Table 2-45 Chapter 49, Service Water Heating, 2007 ASHRAE Handbook, HVAC Applications.

Estimated based on data provided in Appendix E; “Waste Not, Want Not: The Potential for Urban Water Conservation in California”, Pacific Institute, November 2003.

Based on review of the Illinois plumbing code (Employees and students per faucet). Retail, grocery, warehouse and health are estimates. Meals per faucet estimated as 4 bathroom and 3 kitchen faucets and average meals per day of 250 (based on California study above) – 250/7 = 36. Fast food assumption estimated.

Cadmus and Opinion Dynamics Showerhead and Faucet Aerator Meter Study Memorandum dated June 2013, directed to Michigan Evaluation Working Group. If the aerator location is unknown an average of 91% should be used which is based on the assumption that 70% of household water runs through the kitchen faucet and 30% through the bathroom (0.7*93)+(0.3*86)=0.91.

Southern California Gas Company, Workpaper WPSCGNRWH150827A Revision #0, September, 2015.

Table 4 in Chen, et. al., “Calculating Average Hot Water Mixes of Residential Plumbing Fixtures”, June 2020, reports a value of 50.7°F for inlet water temperature for U.S. Census Division 3.

Electric water heaters have recovery efficiency of 98%, as sourced from available products on the AHRI Certification Directory.

ComEd Energy Efficiency/Demand Response Plan: Plan Year 2 (6/1/2009-5/31/2010) Evaluation Report: All Electric Single Family Home Energy Performance Tune-Up Program, December 21, 2010, Table 3-8.

Analysis of CY2018, CY2019, and CY2020 Small Business Kit participant survey installation data. Use if annual survey data is not available or applicable. Please see file “SB Kits Survey Analysis TRMv10 Support.xlsx”

Based on DCEO STEP Program GPY5 evaluation report for showerheads and aerators. Guidehouse, In-Service Rates for a CY2020 Business Remote Assessment Path for Customer Installed Measures, August 21, 2020. Please see file “Business Program Remote Assessment and Install ISR Memo 2020-08-21.docx”

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

44% is the proportion of hot 140F water mixed with 50.7F supply water to give 90°F mixed faucet water.

Calculated as follows: Assumptions for percentage of usage during peak period (1-5pm) were made and then multiplied by 65/365 (65 being the number of days in peak period) and by the number of total annual recovery hours to give an estimate of the number of hours of recovery during peak periods. There are 260 hours in the peak period so the probability you will see savings during the peak period is calculated as the number of hours of recovery during peak divided by 260. See ‘C&I Faucet Aerator.xls’ for details.

Table HC8.9. Water Heating in U.S. Homes in Midwest Region, Divisions, and States,  2009 (RECS).

Review of AHRI Directory suggests range of recovery efficiency ratings for new Gas DHW units of 70-87%. Average of existing units is estimated at 75%.  Commercial properties are more similar to MF homes than SF homes.  MF hot water is often provided by a larger commercial boiler.  This suggests that the average recovery efficiency is somewhere between a typical central boiler efficiency of .59 and the .75 for single family home.  An average is used for this analysis by default.

Table C-6, Measure Life Report, Residential and Commercial/Industrial Lighting and HVAC Measures, GDS Associates, June 2007.  Evaluations indicate that consumer dissatisfaction may lead to reductions in persistence, particularly in Multi-Family.

Direct-install price per showerhead assumes cost of showerhead (Market research average of $7 and assess and install time of $5 (20min @ $15/hr).

Calculated as follows: Assume 11% showers take place during peak hours (as sourced from “Analysis of Water Use in New Single Family Homes, Aquacraft Water Engineering and Management, January 2011). There are 65 days in the summer peak period, so the percentage of total annual aerator use in peak period is 0.11*65/365 = 1.96%. The number of hours of recovery during peak periods is therefore assumed to be 1.96% * 369 = 7.23 hours of recovery during peak period. There are 260 hours in the peak period, so the probability you will see savings during the peak period is 7,23/260 = 0.0278.

Based on excel spreadsheet 120911.xls …on IL-TRM SharePoint.

Table HC8.9. Water Heating in U.S. Homes in Midwest Region, Divisions, and States,  2009 (RECS).

Based on measured data from Ameren IL EM&V of Direct-Install program. Program targets showers that are rated 2.5 GPM or above.

Note that actual values may be either a) program-specific minimum flow rate, or b) program-specific evaluation-based value of actual effective flow-rate due to increased duration or temperatures. The latter increases in likelihood as the rated flow drops and may become significant at or below rated flows of 1.5 GPM. The impact can be viewed as the inverse of the throttling described in the footnote for baseline flowrate.

Representative value from sources 1, 2, 3, 4, 5, and 6 (See Source Table at end of measure section).

Set equal to L_base.

Cadmus and Opinion Dynamics Showerhead and Faucet Aerator Meter Study Memorandum dated June 2013, directed to Michigan Evaluation Working Group.

Table 4 in Chen, et. al., “Calculating Average Hot Water Mixes of Residential Plumbing Fixtures”, June 2020, reports a value of 50.7°F for inlet water temperature for U.S. Census Division 3.

Electric water heaters have recovery efficiency of 98%, as sourced from available products on the AHRI Certification Directory.

Deemed values are from ComEd Energy Efficiency/ Demand Response Plan: Plan Year 2 (6/1/2009-5/31/2010) Evaluation Report: All Electric Single Family Home Energy Performance Tune-Up Program Table 3-8. Alternative ISRs may be developed for program delivery methods based on evaluation results.

Based on DCEO STEP Program GPY5 evaluation report for showerheads and aerators. Guidehouse, In-Service Rates for a CY2020 Business Remote Assessment Path for Customer Installed Measures, August 21, 2020.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

60.8% is the proportion of hot 140F water mixed with 50.7°F supply water to give 105°F shower water.

Calculated as follows: Assume 11% showers take place during peak hours (as sourced from “Analysis of Water Use in New Single Family Homes, Aquacraft Water Engineering and Management, January 2011). There are 65 days in the summer peak period, so the percentage of total annual aerator use in peak period is 0.11*65/365.25 = 1.96%. The number of hours of recovery during peak periods is therefore assumed to be 1.96% * 369 = 7.23 hours of recovery during peak period where 369 equals the average annual electric DHW recovery hours for showerhead use including SF and MF homes with Direct Install and Retrofit/TOS measures. There are 260 hours in the peak period so the probability you will see savings during the peak period is 7.23/260 = 0.0278.

Default assumption for unknown fuel is based on EIA Residential Energy Consumption Survey (RECS) 2009 for Midwest Region, data for the state of IL. If utilities have specific evaluation results providing a more appropriate assumption for homes in a particular market or geographical area then that should be used.

Review of AHRI Directory suggests range of recovery efficiency ratings for new Gas DHW units of 70-87%. Average of existing units is estimated at 75%.  Commercial properties are more similar to MF homes than SF homes.  MF hot water is often provided by a larger commercial boiler.  This suggests that the average recovery efficiency is somewhere between a typical central boiler efficiency of .59 and the .75 for single family home.  An average is used for this analysis by default.

The effective useful life of a pool cover is typically one year longer than its warranty period. SolaPool Covers. Pool Covers Website, FAQ- "How long will my SolaPool cover blanket last?". Pool covers are typically offered with 3 and 5 year warranties with at least one company offering a 6 year warranty. Conversation with Trade Ally. Knorr Systems.

Pool Cover Costs: Lincoln Commercial Pool Equipment online catalog.  Accessed 8/26/11.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’. Note since the water loss associated with this measure is due to evaporation and does not discharge into the wastewater system, only the water supply factor is used here.

Full method and supporting information found in reference document: IL TRM - Business Pool Covers WorkPaper.docx. Note that the savings estimates are based upon Chicago weather data.

Business Pool Covers.xlsx

Ibid.

Aligned with other national energy efficiency programs and confirmed with national vendors

Average cost per unit of capacity for laundromats was generated using data collected from previous Peoples Gas and North Shore Gas custom projects

Average costs per unit of capacity were generated using data collected from existing ozone laundry projects that received incentives under the Non-Residential Retrofit Demand Reduction program (NRR-DR), as well as from the Nicor Custom Incentive Program, and the Nicor Emerging Technology Program (ETP). See referenced document Table 2 and RSMeans Mechanical Cost Data, 31st Annual Edition (2008)

Washer savings were reviewed but were considered negligible and not included in the algorithm (0.00082 kWh / lbs-capacity, determined through site analysis through Nicor Emerging Technology Program (ETP) and confirmed with national vendors). Note that washer savings from Nicor’s site analysis are smaller than those reported in a WI Focus on Energy case study (0.23kWh/100lbs, Hampton Inn Brookfield, November 2010). Electric impact of operating ozone generator (0.0021 kWh / lbs-capacity same source as washer savings) was also considered negligible and not included in calculations. Values should continue to be studied and monitored through additional studies due to limited data points used for this determination.

Assumed average horsepower for boilers connected to applicable washer.

Engineered estimate provided by CLEAResult review of Nicor custom projects. Machines spent approximately 7 minutes per hour filling with water and were in operation approximately 20 hours per day. Total pump time therefore estimated as 7/60 * 20 * 365 = 852 hours, and rounded down conservatively to 800 hours.

Page 7, Laundries and Dry-Cleaning Operations, Watersmart Guidebook EBMUD_WaterSmart_Guide_Laundries_Dry-Cleaning_Operations.pdf.

Average water reduction factors were generated using data collected from existing ozone laundry projects that received incentives under the Non-Residential Retrofit Demand Reduction program (NRR-DR). Table 6 summarizes data gathered from several NRR-DR projects, Nicor Custom projects, and Nicor ETP projects. Nicor Savings Numbers are associated with ACEE_AWE_Ozone Laundry / From Gas Savings Calculations.

Average lbs-capacity per project site was generated using data collected from existing ozone laundry projects that received incentives under the Non-Residential Retrofit Demand Reduction program (NRR-DR), as well as from the Nicor Custom Incentive Program, and the Nicor Emerging Technology Program (ETP). See referenced document Table 2.

See the “Water Impact Descriptions and Calculation” section of this measure for more information.

See the “Water Impact Descriptions and Calculation” section of this measure for more information.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

Assuming boiler efficiency is the regulated minimum efficiency (80%), per Title 20 Appliance Standard of the California Energy Regulations (October 2007). The incoming municipal water temperature is assumed to be 55 °F with an average hot water supply temperature of 140°F, based on default test procedures on clothes washers set by the Department of Energy’s Office of Energy Efficiency and Renewable Energy (Federal Register, Vol. 52, No. 166). Enthalpies for these temperatures (107 btu/lbs at 140F, 23.07 btu/lbs at 55F) were obtained from ASHRAE Fundamentals.

DOE Technical Support Document Chapter 6, 2010 https://www.regulations.gov/contentStreamer?documentId=EERE-2006-STD-0127-0118&attachmentNumber=8&disposition=attachment&contentType=pdf

Average utilization factors were generated using data collected from existing ozone laundry projects that received incentives under the NRR-DR program. Table 3 summarizes data gathered from several NRR-DR projects, Nicor Custom projects, and Nicor ETP projects.

Calculated as WUsage * Average % Hot water (estimated at 59% from Custom laundromat data); 1.09*0.59 = 0.64 gal / lbs laundry.

Average hot water usage factors were generated using data collected from existing ozone laundry projects that received incentives under the NRR-DR program. Summarizes data gathered from several NRR-DR projects.

Average hot water reduction factors were generated using data collected from existing ozone laundry projects that received incentives under the Non-Residential Retrofit Demand Reduction program (NRR-DR). Table 5  summarizes data gathered from several NRR-DR projects, Nicor Custom projects, and Nicor ETP projects. Nicor Savings Numbers are associated with ACEE_AWE_Ozone Laundry / From Gas Savings Calculations.

Based on Peoples Gas custom project data.

Average water usage factors were generated using data collected from existing ozone laundry projects that received incentives under the NRR-DR program.  summarizes data gathered from several NRR-DR projects.

DOE Technical Support Document Chapter 6, 2010 https://www.regulations.gov/contentStreamer?documentId=EERE-2006-STD-0127-0118&attachmentNumber=8&disposition=attachment&contentType=pdf

Average utilization factors were generated using data collected from existing ozone laundry projects that received incentives under the NRR-DR program. Table 3 summarizes data gathered from several NRR-DR projects, Nicor Custom projects, and Nicor ETP projects.

Page 7, Laundries and Dry-Cleaning Operations, Watersmart Guidebook EBMUD_WaterSmart_Guide_Laundries_Dry-Cleaning_Operations.pdf.

Average water reduction factors were generated using data collected from existing ozone laundry projects that received incentives under the Non-Residential Retrofit Demand Reduction program (NRR-DR). Table 6 summarizes data gathered from several NRR-DR projects, Nicor Custom projects, and Nicor ETP projects. Nicor Savings Numbers are associated with ACEE_AWE_Ozone Laundry / From Gas Savings Calculations.

Confirmed through communications with national vendors and available references, via an online forum (The Ozone Laundry Blog – The Importance of Maintenance).

International Energy Conservation Code (IECC) 2012/2015/2018, Table C404.2, Minimum Performance of Water-Heating Equipment.

Nicor Gas Energy Efficiency Plan 2011-2014. Revised Plan Filed Pursuant to Order Docket 10-0562, May 27, 2011.

Baseline install costs are based on data from the “2010-2012 WO017 Ex Ante Measure Cost Study”, Itron, California Public Utilities Commission. The data is provided in a file named “MCS Results Matrix – Volume I”.

The two equations are provided to show how savings are determined during the initial phase of the measure (existing to efficient) and the remaining phase (new baseline to efficient). In practice, the screening tools used may either require a First Year savings (using the first equation) and then a “number of years to adjustment” and “savings adjustment” input which would be the (new base to efficient savings)/(existing to efficient savings).

Navigant, ComEd PY3 Multi-Family Home Energy Savings Program Evaluation Report Final, May 16, 2012.

Deoreo, B., and P. Mayer. Residential End Uses of Water Study Update. Forthcoming. ©2015 Water Research Foundation. Reprinted With Permission.

Table 4 in Chen, et. al., “Calculating Average Hot Water Mixes of Residential Plumbing Fixtures”, June 2020, reports a value of 50.7°F for inlet water temperature for U.S. Census Division 3.

IECC 2015, Table C404.2, Minimum Performance of Water-Heating Equipment

Based upon DCEO data provided 10/2014; average age adjusted efficiency of existing units replaced through the program. Efficiency age adjustment of 0.5% per year based upon NREL “Building America Performance Analysis Procedures for Existing Homes”.

Stand-by loss is provided in IECC 2012/2015/2018, Table C404.2, Minimum Performance of Water-Heating Equipment.

Benningfield Group. (2009). PY 2009 Monitoring Report: Demand Control for Multifamily Central Domestic Hot Water. Folsom, CA: Prepared for Southern California Gas Company, October 30, 2009.

The incremental costs were averaged based on the following multi-family, dormitory and hospitality building studies-

- Gas Technology Institute. (2014). 1003: Demand-based domestic hot water recirculation Public project report. Des Plaines, IL: Prepared for Nicor Gas, January 7, 2014.

- Studies performed in multiple dormitory buildings in the California region for Southern California Gas’ PREPS Program, 2012.

- Evaluation of New DHW System Controls in Hospitality and Commercial Buildings. Prepared for: Minnesota Department of Commerce, Division of Energy Resources, 2018.

This value is the average kWh saved per pump based on results from Multi-Family buildings studied in Nicor Gas Emerging Technology Program study, Southern California Gas’ study in multiple dormitory buildings, and Minnesota’s Evaluation of New DHW System Controls in Hospitality and Commercial Buildings . Note this value does not reflect savings from electric units but electrical savings from gas-fired units. See ‘CDHW Controls Summary Calculations.xlsx’ for more information.

See ‘CDHW Controls Summary Calculations.xlsx’ for more information.

This is an average number based on Residential Energy Consumption Survey (2009) data and Commercial Building Energy Consumption Survey (2012) data compiled by U.S. Energy Information Administration, for buildings with more than 5 apartments in Illinois and Nursing Home and Assisted Living facilties in Midwest.

This is based on Commercial Building Energy Consumption Survey (2012) data compiled by U.S. Energy Information Administration, for Education facilities in East North Central.

This value is ratioed upon the Btu per Dwelling per Hotel/Motel vs Dormitory building type assuming the same heating capacity requirements based upon the similarity between the building types.

This is based on studies done in multiple university dormitory buildings in the California region, for Southern California Gas’ PREPS Program, 2012. It closely matches the design guidelines outlined in 2007 ASHRAE Handbook, Chapter 49: Service Water Heating, Table 7, and assumes 1 to 2 students per dorm room based on typical dorm room layouts. This source provides the source for dormitory assumptions of Boiler Input Capacity, tlow occ, Rnormal occ and Rlow occ,

This is based on studies done at Multi-Family Buildings for the Nicor Gas Emerging Technology Program by Gas Technology Institute. It closely matches the design guidelines outlined in 2007 ASHRAE Handbook, Chapter 49: Service Water Heating, Table 9, and assumes 2.1 persons per apartment as per ComEd PY3 Multi-Family Home Energy Savings Program Evaluation Report Final, May 16, 2012 by Navigant. This source provides the source for dormitory assumptions of Boiler Input Capacity, tlow occ, Rnormal occ and Rlow occ,

Calculated based upon ASHRAE 2015 ASHRAE HVAC Applications Table 6 and IL TRM assumptions. See ‘CDHW Controls Summary Calculations.xlsx’ for more information.

Based on results of studies performed in multiple university dormitory buildings in the California region, for Southern California Gas’ PREPS Program, 2012.

Based on results of the studies done at Multi-Family Buildings for the Nicor Gas Emerging Technology Program:

- Gas Technology Institute. (2014). 1003: Demand-based domestic hot water recirculation Public project report. Des Plaines, IL: Prepared for Nicor Gas, January 7, 2014.

Calculucated from the Btu per dwelling unit and average annual therm consumption for DHW for all Hospitallity Buildings noted in “Evaluation of New DHW System Controls in Hospitality and Commercial Buildings”, MN Commerce Department Energy Resources, 06/30/2018.

Low occupancy periods for dormitory buildings can be assumed as vacation day or holiday occupancy.

Assumed no low occupancy hours based upon load profile for Guest Room SWH schedule for Other days for Small & Large Hotels, “US Department of Energy Commercial Reference Building Models of National Building Stock”, Deru, Field, Struder, Benne, Griffith and Torellini, National Renewable Energy Laboratory, February 2011.

Average Hospitallity Savings, “Evaluation of New DHW System Controls in Hospitality and Commercial Buildings”, MN Commerce Department Energy Resources, 06/30/2018.

Estimated from low occupancy hours

Savings methodology factors are for a constant speed fan.

Professional judgement, consistent with expected lifetime of kitchen demand ventilation controls and other kitchen equipment.

Minnesota 2012 Technical Reference Manual, Electric Food Service_v03.2.xls

Average dishwashing and faucet water usage taken from Chapter 8, Table 8.3.3 Normalized Annual End Uses of Water in Select Restaurants in Western United States.

Average value based on case studies. Northwinds Sailing, Inc. and North Shore Sustainable Energy, LLC. Angry Trout Café Kitchen Exhaust Heat Recovery. Minnesota Department of Commerce, Division of Energy Resources, 2012.

Commercial Kitchen Loads for listed buildings in U.S. Department of Energy Commercial Reference Building Models of the National Building Stock, NREL

Each filter is 20 X 20 inches.

Exhaust Fan Schedules for listed buildings in U.S. Department of Energy Commercial Reference Building Models of the National Building Stock, NREL.

Minnesota 2012 Technical Reference Manual, Electric Food Service_v03.2.xls.

Act on Energy Commercial Technical Reference Manual No. 2010-4, 9.2.2 Gas Boiler Tune-up.

Act on Energy Commercial Technical Reference Manual No. 2010-4, 9.2.2 Gas Boiler Tune-up.

Work Paper – Tune up for Boilers serving Space Heating and Process Load by Resource Solutions Group, January 2012

US DOE Building America Program, Building America Analysis Spreadsheet (for Chicago, IL), Office of Energy Efficiency & Renewable Energy.

Methodology based on Cadmus analysis. Annual hot water usage in gallons based on CBECS (2012) and RECS (2009) consumption data of East North Central (removed outliers of 1,000 kBtuh or less) to calculate hot water usage. Annual hot water gallons per tank size gallons based on the tank sizing methodology found in ASHRAE 2011 HVAC Applications. Chapter 50 Service Water Heating. Demand assumptions (gallons per day) for each building type based on ASHRAE Chapter 50 and to LBNL White Paper. LBL-37398 Technology Data Characterizing Water Heating in Commercial Buildings: Application to End Use Forecasting. Assumes hot water heater efficiency of 80%.

According to CBECS 2012 “Lodging” buildings include Dormitories, Hotels, Motel or Inns and other Lodging and “Nursing” buildings include Assisted Living and Nursing Homes.

Table 8-18: Average Useful Lifetime of Commercial Washing Equipment, Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, Navigant Consulting, December 21, 2009.

One study found the average cost of tunnel washers to be $1,100,000. Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, Navigant Consulting, December 21, 2009. https://www1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf

Matt Poe. “Efficient, Flexible Tunnel Washers: Tunnel washers have made leaps forward in technology, productivity in the past 10 years”, American Laundry News, 12/11/18. <https://americanlaundrynews.com/articles/efficient-flexible-tunnel-washers>

Ibid.

Theresa Boehl. “Tunnel Washers: The Answer to Rising Labor, Utility Costs?”, American Laundry News, 5/27/14. <https://americanlaundrynews.com/articles/tunnel-washers>

IL TRM Section 4.3.6 “Ozone Laundry”

Joseph Ricci. “Outsourced Hotel Laundries: The Value of Certification”, Lodging, 3/28/17. <https://lodgingmagazine.com/outsourced-hotel-laundries-the-value-of-certification/>

IL TRM Section 4.3.6 footnote for Wutil, which states “Average utilization factors were generated using data collected from existing ozone laundry projects that received incentives under the NRR-DR program.”

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

US DOE Building America Program, Building America Analysis Spreadsheet (for Chicago, IL), Office of Energy Efficiency & Renewable Energy

Annual repair & maintenance costs have been estimated at $19,000 per unit.  Energy Savings Potential and RD&D Opportunities for Commercial Building Appliances, Navigant Consulting, December 21, 2009. https://www1.eere.energy.gov/buildings/publications/pdfs/corporate/commercial_appliances_report_12-09.pdf

3E Plus v4.1 is a heat loss calculation software provided by the NAIMA (North American Insulation Manufacturer Association).

ASHRAE Handbook – Fundamentals 2017 lists requirements for pipe and duct insulation but does not mention tank insulation.

Based on the California Municipal Utilities Association Technical Reference Manual Third Edition measure 14.1.

Based on RS Means Data Line Number 220719101162.

Zimmerman, Cliff, Franklin Energy, “Thermal Regain Factor_4-30-14.docx”, 2014. Based on climate zone 2. Note ‘Location not specified – Commercial’ assumes pipes provide DHW year round. ‘Location not specified – Commercial’ assumes semi-conditioned annual usage.

Minimum efficiency for steam boilers as set in IECC 2018 code C403.3.2.

Tank insulation calc_8-4-20.xlsx including tables obtained from 3E Plus v4.1 software.

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL for the average ambient temperature and wind speed for Aurora, IL. Adjusted to align with ASHRAE 24.4 Terrain Category 1 for Large city centers with densely populated, tall buildings (2017).

A full description of the ComEd model development is found in “ComEd Portfolio Modeling Report. Energy Center of Wisconsin July 30, 2010”.

Based on model with single duct reheat system with a fixed outdoor air volume.

Based on model with single duct reheat system with airside economizer controls, with constant volume zone reheat boxes and single speed fan motors.

Based on model with single duct reheat system with airside economizer controls, zone VAV reheat boxes and VFD fan motors.

3 years is given for “Clean Condenser Coils – Commercial” and “Clean Evaporator Coils”. DEER2014 EUL Table.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

In the context of this measure Energy Efficiency Ratio (EER) refers to field-measured steady-state rate of heat energy removal (e.g., cooling capacity) by the equipment in Btuh divided by the steady-state rate of energy input to the equipment in watts. This ratio is expressed in Btuh per watt (Btuh/watt). The cooling capacity may be derived using either refrigerant or air-side measurements. The measurement is performed at the outdoor and indoor environmental conditions that are present at the time the tune-up is being performed, and should be normalized using a correction function to the AHRI 210/240 Standard test conditions. The correction function should be developed based on manufacturer’s performance data. Care must be taken to ensure the unit is fully loaded and operating at or near steady-state. Generally, this requires that the outside air temperature is at least 60°F, and that the unit runs with all stages of cooling enabled for 10 to 15 minutes prior to making measurements. For more information, please see “IL TRM_Normalizing to AHRI Conditions Method”.

Savings estimates are determined by applying the findings from DNV-GL “Impact Evaluation of 2013-2014 HVAC3 Commercial Quality Maintenance Programs”, April 2016, to simulate the inefficient condition within select eQuest models and across climate zones. The percent savings were consistent enough across building types and climate zones that it was determined appropriate to apply a single set of assumptions for all. See ‘eQuest C&I Tune up Analysis.xlsx’ for more information.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Act on Energy Commercial Technical Reference Manual No. 2010-4, 9.2.2 Gas Boiler Tune-up

Act on Energy Commercial Technical Reference Manual No. 2010-4, 9.2.2 Gas Boiler Tune-up

Work Paper – Tune up for Boilers serving Space Heating and Process Load by Resource Solutions Group, January 2012

Guidehouse evaluation results from tune-up efficiency improvement research for Peoples Gas and North Shore Gas through their C&I and Public Sector Prescriptive Rebate Program, their Small Business Program, and their Multi-Family Programs. The evaluation included project and population data from program year’s 2018 and 2019.

Guidehouse evaluation results from tune-up efficiency improvement research for Peoples Gas and North Shore Gas through their C&I and Public Sector Prescriptive Rebate Program, their Small Business Program, and their Multi-Family Programs. The evaluation included project and population data from program year’s 2018 and 2019.

Act on Energy Commercial Technical Reference Manual No. 2010-4, 9.2.2 Gas Boiler Tune-up

Act on Energy Commercial Technical Reference Manual No. 2010-4, 9.2.2 Gas Boiler Tune-up

Work Paper – Tune up for Boilers serving Space Heating and Process Load by Resource Solutions Group, January 2012

Work Paper – Tune up for Boilers serving Space Heating and Process Load by Resource Solutions Group, January 2012

Guidehouse evaluation results from tune-up efficiency improvement research for Peoples Gas and North Shore Gas through their C&I and Public Sector Prescriptive Rebate Program, their Small Business Program, and their Multi-Family Programs. The evaluation included project and population data from program year’s 2018 and 2019.

Guidehouse evaluation results from tune-up efficiency improvement research for Peoples Gas and North Shore Gas through their C&I and Public Sector Prescriptive Rebate Program, their Small Business Program, and their Multi-Family Programs. The evaluation included project and population data from program year’s 2018 and 2019.

This is intentionally longer than the assumptions found in the early replacement commercial HVAC measures as the application of boiler reset controls will occur in a variety of sites that may not be targeted for early replacement HVAC systems.

Nexant. Questar DSM Market Characterization Report. August 9, 2006.

Savings factor is the estimate of annual gas consumption that is saved due to adding boiler reset controls.  A comparable savings factor, based on boiler tuneup savings is derived from Xcel Energy "DSM Biennial Plan-Technical Assumptions," Colorado.  For further substantiation, Wisconsin Focus on Energy 2020 TRM uses 8%, citing multiple sources. And other prescriptive programs across the country consistently use between 5 and 10% savings factor (Efficiency Vermont - 2020, New York TRM, version 7.0 – 2020 (Cadmus Group, Inc. Home Energy Services Impact Evaluation, August 2012, pg. 20)).

DEER 2008

The incremental capitol cost is based on historic project data from Wisconsin Focus on Energy, spanning 2015 through June 2018. The data is aggregated based on 29 projects that comprised of 100 installed unit heaters. The average installed unit heater cost was $22.64 / kBtu/h of input unit capacity. The baseline unit heater cost was estimated to be $7.08 / kBtu/h of input unit capacity, per review of online pricing of Reznor and Modine models on Supply House’s website. The incremental cost was sourced from the 2020 Wisconsin Focus on Energy TRM, Public Service Commission of Wisconsin, Cadmus – “Unit Heaters, > 90% Thermal Efficiency (pg. 234)

The utilization factor accounts for the fact that unit heaters are typically over-sized. Value as sourced from the 2020 Wisconsin Focus on Energy Technical Reference Manual, Public Service Commission of Wisconsin, Cadmus – Unit Heaters, ≥ 90% Thermal Efficiency (pg. 234)

Baseline combustion efficiency is sourced from IECC 2018 for all capacity warm-air unit heaters, gas-fired.

As recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

(http://deeresources.com/deer0911planning/downloads/EUL_Summary_10-1-08.xls).

Based on Navigant Consulting, NEEP “Incremental Cost Study Phase Two Final Report”, January 2013.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Integrated Part Load Value is a seasonal average efficiency rating calculated in accordance with ARI Standard 550/590. It may be calculated using any measure of efficiency (EER, kW/ton, COP), but for consistency with IECC code requirements, it is expressed in terms of IPLV here.

Can determine IPLV from standard testing or looking at engineering specs for design conditions.  Standard data is available from AHRI online Certification Directory.

Federal Baselines defined by Code of Federal Regulations §430.32(d). ENERGY STAR specification defined by Version 4.0 Room Air Conditioners. CEE specification defined by Room Air Conditioner Specification effective January 31, 2017.

Side louvers that extend from a room air conditioner model in order to position the unit in a window. A model without louvered sides is placed in a built-in wall sleeve and are commonly referred to as "through-the-wall" or "built-in" models.

Casement-only refers to a room air conditioner designed for mounting in a casement window of a specific size.

Casement-slider refers to a room air conditioner with an encased assembly designed for mounting in a sliding or casement window of a specific size. Reverse cycle refers to the heating function found in certain room air conditioner models.

Measure Life Report, Residential and Commercial/Industrial Lighting and HVAC Measures, GDS Associates, June 2007.

CEE Tier 1 cost based on field study conducted by Efficiency Vermont and Tier 2 based on professional judgement.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year

Based on maximum capacity average from the RLW Report: Final Report Coincidence Factor Study Residential Room Air Conditioners, June 23, 2008.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

DEER 2008 value for energy management systems.

This value was extracted from Smart Ideas projects in PY1 and PY2.

For motels, see S. Keates, ADM Associates Workpaper: “Suggested Revisions to Guest Room Energy Management (PTAC & PTHP)”, 11/14/2013 and spreadsheet summarizing the results: ‘GREM Savings Summary_IL TRM_1_22_14.xlsx’. In 2014 the hotel models were also run to compile results, rather than by applying adjustment factors to the motel results as had been done in V3.0 of the TRM. The updated values can be found in ‘GREM Savings Summary (Hotel)_IL TRM_10_16_14.xls’.

Consistent with Residential measure and based on 2016 DOE Rulemaking Technical Support document, as recommended in Guidehouse ‘ComEd Effective Useful Life Research Report’, May 2018.

Assumed to be one third of effective useful life of replaced equipment.

Assume full measure life (16 years) for replacing electric resistance as we would not expect that resistance heat would fail during the lifetime of the efficient measure.

Based on a review of TRM incremental cost assumptions from Vermont, Wisconsin, and California.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

In situ performance based on Opinion Dynamics and Cadmus metering study of Ameren HVAC program participants; See ‘AIC HVAC Metering Study Memo FINAL 2_28_2018’.

In situ performance based on Opinion Dynamics and Cadmus metering study of Ameren HVAC program participants; See ‘AIC HVAC Metering Study Memo FINAL 2_28_2018’.

In situ performance based on Guidehouse review of 201 ASHP installs. While the data indicated an average of 1.006, the range was 0.9 to 1.06 so calculation of this value should be done where possible.

Based on Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder. Note this is appropriate for single speed units only.

Fe is estimated using TRM models for the three most popular building types for programmable thermostats: low-rise office (10.2%), sit-down restaurant (8.6%), and retail – strip mall (4.4%). 7.7% reflects the average Fe of the three building types. See “Fan Energy Factor Example Calculation 2021-06-23.xlsx” for reference.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Code of Federal Regulations, effective January 15, 2021 (10 CFR 432(e)(3)).

Consistent with DOE assumption determined through a literature review in Appendix 8-F of the Department of Energy Commercial Technical Support Document.

Ibid.

Ibid.

Miura Modular Boilers, https://s29958.pcdn.co/wp-content/uploads/2019/03/LXBrochure2016.pdf

Code of Federal Regulations, effective January 15, 2021 (10 CFR 432(e)(3)).

Thermal Efficiency. Code of Federal Regulations, effective March 2, 2012 (10 CFR 431.87).

Combustion Efficiency. Code of Federal Regulations, effective March 2, 2012 (10 CFR 431.87).

Code of Federal Regulations, effective March 2, 2012 (10 CFR 431.87). Includes efficiency requirements for all steam boilers ≥ 300,000 Btu/hr.

As part of the code of federal regulations, energy conservation standards for covered residential furnace fans become effective on July 3, 2019 (10 CFR 430.32(y)). The expectation is the baseline will essentially become an ECM motor.

The Technical Advisory Committee agreed that if the cost of repair is less than 20% of the new baseline replacement cost it can be considered early replacement. Note the non-inflated cost is used as this would be a cost consideration in the program year.

Average of 15-18 year lifetime estimate made by the Consortium for Energy Efficiency in 2010.

Assumed to be one third of effective useful life.

Based on data from Appendix E of the US DOE Appliance Standards Technical Support Documents including equipment cost and installation labor. Where efficiency ratings are not provided, the values are interpolated from those that are.

$2641 inflated using 1.91% rate.

To estimate heating, cooling and shoulder season savings for Illinois, VEIC adapted results from a 2009 Focus on Energy study of BPM blower motor savings in Wisconsin. This study included effects of behavior change based on the efficiency of new motor greatly increasing the amount of people that run the fan continuously. The savings from the Wisconsin study were adjusted to account for different run hour assumptions (average values used) for Illinois. See: FOE to IL Blower Savings.xlsx.

The weighted average value is based on assumption that 75% of buildings installing BPM furnace blower motors have Central AC.

Hours per year are estimated using the eQuest or OpenStudio models as the total number of hours the cooling system is operating for each building type.

Coincidence Factors are estimated using the eQuest models.

The two equations are provided to show how savings are determined during the initial phase of the measure (existing to efficient) and the remaining phase (new baseline to efficient). In practice, the screening tools used may either require a First Year savings (using the first equation) and then a “number of years to adjustment” and “savings adjustment” input which would be the (new base to efficient savings)/(existing to efficient savings).

Average nameplate efficiencies of all Early Replacement qualifying equipment in Ameren PY3-PY4.

Residential sized units as per Code of Federal Regulations, effective November, 2015 (10 CFR 432(e)).

Commercial sized units as per Code of Federal Regulations, effective January 1994 (10 CFR 431(d)).

Commercial sized units as per Code of Federal Regulations, effective January 1, 2023 (10 CFR 431(d)).

Minimum ENERGY STAR efficiency after 2.1.2012.

"AHRI Standard 1330 - 2014 Standard for Performance Rating for Radiant Output of Gas Fired Infrared Heaters". 2014. Air Conditioning, Heating, and Refrigeration Institute. Arlington, VA.

2020 Michigan Energy Measures Database (MEMD). Please see file “mi_master_measure_database_2020-011020_681298_7.xlsx”

2020 Michigan Energy Measures Database (MEMD). Please see file “mi_master_measure_database_2020-011020_681298_7.xlsx”

2016 ASHRAE® HANDBOOK: Heating, Ventilating, and Air-Conditioning SYSTEMS AND EQUIPMENT, Inch-Pound Edition, Chapter 16, pg. 16.1, “Energy Conservation,” 2016, American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Inc. Atlanta, GA.

"Put Your Infra-Red Knowledge to the Test". Contracting Canada, July - August 2002.

Based on 2015 DOE Technical Support Document, as recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Standard assumption of one third of effective useful life.

DEER 2008. This assumes that baseline shift from IECC 2012 to IECC 2015 carries the same incremental costs. Values should be verified during evaluation.

Based on DCEO – IL PHA Efficient Living Program data.

Based on subtracting TOS incremental cost from the DCEO data and incorporating inflation rate of 1.91%.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

There are no heating efficiency improvements for PTACs since although some do provide heating, it is always through electric resistance and therefore the COPbase and COPee would be 1.0.

Efficiency of existing unit is estimated based on the 2012 IECC building energy code standard sized, and assuming a 1 ton unit; PTAC: EER = 13.8 – (0.3 * 12,000/1,000) = 10.2, and PTHP: EER = 14 – (0.3 * 12,000/1,000) = 10.4.

Based on Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder. Note this is appropriate for single speed units only.

Efficiency of existing unit is estimated based on the 2012 IECC building energy code, and assuming a 1 ton unit; COP = 3.2 – (0.026 * 12,000/1,000) = 2.9.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Please see; ‘C&I Pipe Insulation Calculator Access.docx’ for directions on accessing the external calculator. The use of other comparable external calculators are allowed if the functionality mirrors the savings approach detailed in this characterization.

Unconditioned space with heat transfer to conditioned space (e.g. boiler room, ceiling plenum, basement, crawlspace, wall, etc.).

Comprehensive list of building types available in Section 4.4, HVAC End Use of IL TRM.

For insulation thicknesses greater than 4”, savings can be claimed based on 4” insulation thickness.

Equivalent length of elbows and tees is based on methodology described in ANSI/ASME B36.19. Equivalent length of flanges and valves is based on methodology described in ATSM Standard C1129-12.

International Energy Conservation Code, 2018; Section C403.11.3 Piping Insulation (Mandatory), Table C403.11.3, Page C-69.

ASHRAE Handbook—Fundamentals, 23.14; Hart, G., “Saving energy by insulating pipe components on steam and hot water distribution systems”, ASHRAE Journal, October 2011.

Measure Life Report, Residential and Commercial/Industrial Lighting and HVAC Measures, GDS Associates, June 2007.

RS Means 2008. Mechanical Cost Data, pages 106 to 119

RS Means 2010: “for fittings, add 3 linear feet for each fitting plus 4 linear feet for each flange of the fitting”

This value comes from the reference table “Savings Summary by Building Type and System Type.” The formula and the input tables in this section document assumptions used in calculation spreadsheet “Pipe Insulation Savings 2013-11-12.xlsx”.

Average efficiencies of units from the California Energy Commission (CEC).

Ibid.

Katrakis, J. and T.S. Zawacki. “Field-Measured Seasonal Efficiency of Intermediate-sized Low-Pressure Steam Boilers”.  ASHRAE V99, pt. 2, 1993.

Zimmerman, Cliff, Franklin Energy, “Thermal Regain Factor_4-30-14.docx”, 2014. Based on climate zone 2. Note ‘Location not specified – Commercial’ assumes semi-conditioned spaces with 50% pipes providing space heating and 50% providing DHW. ‘Location not specified – Commercial’ assumes semi-conditioned annual usage.

3E Plus is a heat loss calculation software provided by the NAIMA (North American Insulation Manufacturer Association).

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL for the average ambient temperature for Aurora, IL.

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL for the average ambient temperature for Aurora, IL.

Based on the dimensions for diameter, long radius, and short radius given by ANSI/ASME 36.19.

Based on the center to face and diameter dimensions given by ANSI/ASME B36.19.

Based on ComEd Small Business Trade Ally feedback. For units rated at less than 20 ton units, the cost of common repairs is under $2,000, significantly less than the cost of purchasing new equipment. Therefore, if the cost of repair is less than $2,000, it can be considered early replacement because customers would repair instead of replace a failed unit. Repair cost data was not available for units larger than 20 tons.

Measure Life Report: Residential and Commercial/Industrial Lighting and HVAC Measures, GDS Associates, Inc., June 2007.

Assumed to be one third of effective useful life.

CEE Commercial Unitary Air-conditioning and Heat Pumps Specification, which provides high efficiency performance specifications for single-package and split system unitary air conditioners.

NEEP Incremental Cost Study (ICS) Final Report – Phase 3, May 2014.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

The two equations are provided to show how savings are determined during the initial phase of the measure (existing to efficient) and the remaining phase (new baseline to efficient). In practice, the screening tools used may either require a First Year savings (using the first equation) and then a “number of years to adjustment” and “savings adjustment” input which would be the (new base to efficient savings)/(existing to efficient savings).

Based on Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder. Note this is appropriate for single speed units only.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Source paper is the CLEAResult "Steam Traps Revision #1" dated August 2011.   Primary studies used to prepare the source paper include Enbridge Steam Trap Survey, KW Engineering Steam Trap Survey, Enbridge Steam Saver Program 2005, Armstrong Steam Trap Survey, DOE Federal Energy Management Program Steam Trap Performance Assessment, Oak Ridge National Laboratory Steam System Survey Guide, KEMA Evaluation of PG&E's Steam Trap Program, Sept. 2007.  Communication with vendors suggested an inverted bucket steam trap life typically in the range of 5 - 7 years, float and thermostatic traps 4- 6 years, float and thermodynamic disc traps of 1 - 3 years.  Cost does not include installation.

“Venturi Steam Trap – Functional Laboratory Study, GTI on behalf of Illinois utilities, Nicor Gas, Peoples Gas, and North Shore Gas, and on behalf of contributing utilities from other states, March 26, 2019. This report reflects phase 1 of an ongoing field study that will continue data collection to validate useful life and provide information on proper sizing in various end use applications. Additional data expected in 2021.

Ibid. Based on reported age for venturi steam traps currently operating in the field.

Ibid.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’. Note since the water loss associated with this measure is due to evaporation and does not discharge into the wastewater system, only the water supply factor is used here.

See “Derivation of Equation for Subsonic Compressible Flow through an Orifice and Supporting Calculations for Illinois TRM Steam Trap Measure” paper for more information.

Enbridge adjustment factor used as referenced in CLEAResult “Work Paper Steam Traps Revision #2" Revision 3 dated March 2, 2012 and DOE Federal Energy Management Program Steam Trap Performance Assessment.

Medium and high pressure steam trap inlet pressure based on Navigant analysis of source collected during program implementation by Nicor Gas for GPY1 through GPY4. For each steam trap project, the data provided measure savings description, operating pressure, installation Zip code, business building type, program year, and annual operating hours. Dry cleaning steam trap inlet pressure based on C5 Steam Traps – Nicor FINAL 10.27.11.

For applications where inlet pressures and orifice diameters are provided in the table, default values are directly calculated using the equation above. For applications where inlet pressures and orifice diameters are not provided in the table, default values are assumptions based on engineering judgement and will be revisited in future years.

Heat of vaporization of steam at the inlet pressure to the steam trap.  Implicit assumption that the average boiler nominal pressure where the vaporization occurs, is essentially that same pressure.  Referenced in CLEAResult “Work Paper Steam Traps Revision #2" Revision 3 dated March 2, 2012.

US DOE Building America Program. Building America Analysis Spreadsheet.  For Chicago, IL.

Ibid.

Katrakis, J. and T.S. Zawacki. “Field-Measured Seasonal Efficiency of Intermediate-sized Low-Pressure Steam Boilers”.  ASHRAE V99, pt. 2, 1993.

Medium and high-pressure steam trap annual operating hours based on Navigant analysis of source collected during program implementation by Nicor Gas for GPY1 through GPY4. For each steam trap project, the data provided measure savings description, operating pressure, installation Zip code, business building type, program year, and annual operating hours.

Dry cleaners survey data as referenced in CLEAResult “Work Paper Steam Traps Revision #2" Revision 3 dated March 2, 2012.

Efficiency Vermont TRM 10/26/11 for HVAC VSD motors.

DEER 2008.

Ohio TRM 8/6/2010 varies by motor/fan size based on equipment costs from Granger 2008 Catalog pp 286-289, average across available voltages and models. Labor costs from RS Means Data 2008. Ohio average cost adjustment applied.

Del Balso, Ryan J. “Investigation into the Reliability of Energy Efficiency/Demand Side Management Savings Estimates for Variable Frequency Drives in Commercial Applications”, University of Colorado, Department of Civil, Environmental and Architectural Engineering, 2013.

Ohio TRM 8/6/2010 pp207-209, Com Ed TRM June 1, 2010.

Hours per year are estimated using the eQuest or OpenStudio models as the total number of hours the heating or cooling system is operating for each building type. “Heating and Cooling Run Hours” are estimated as the total number of hours fans are operating for heating, cooling and ventilation for each building type. This may overclaim certain applications (e.g. pumps) and so where possible actual hours should be used for these applications.

Based on OpenStudio Large Office model, finding difference in energy use for each VSD application. See ‘VSD ESF Calculation.xls’.

Based on OpenStudio Large Office model, finding difference in maximum demand for each VSD application. See ‘VSD ESF Calculation.xls’.

During the course of conversations with vendors and Building Automation System (BAS) contractors, it was determined that sensors have to be functional for up to 10 years.  It is recommended that they are part of a normal preventive maintenance program in which calibration is an important part of extending useful life.  Although they are not subject to mechanical failure, they do fall out of tolerance over time.

Discussion with vendors.

California Utilities Statewide Codes and Standards Team. 2011. "2013 California Building Energy Efficiency Standards”, Garage Exhaust, Section 4.2 Page 14.

The electric energy savings was calculated using TMY3 weather data and methodology consistent with ASHRAE standards. Savings are calculated on an annual basis for each given temperature zone in Illinois. Energy savings for DCV were developed utilizing standards, inputs and approaches as set forth by ASHRAE 90.1 -2010 (code level up until Dec 31, 2015). Building input parameters like square footage, equipment efficiencies and occupancy match those used in the EFLH calculations. Reference calculation found in Demand Control Ventilation 12-30-13.xls.

Savings are estimated based on a study done by California Utilities Statewide Codes and Standards Team, “2013 California Building Energy Efficiency Standards”, 2013, Section 2.4, Table 1. The savings are primarily fan savings, and are not dependent on climate zone.

The natural gas energy savings was calculated using TMY3 weather data and methodology consistent with ASHRAE standards. Savings are calculated on an annual basis for each given temperature zone in Illinois. Energy savings for DCV were developed utilizing standards, inputs and approaches as set forth by ASHRAE 62.1 and 90.1, respectively. Building input parameters like square footage, equipment efficiencies and occupancy match those used in the EFLH calculations. Reference calculation found in Demand Control Ventilation 12-30-13.xls.

The standard turndown ratio for boilers is 6:1. Understanding Fuel Savings in the Boiler Room, ASHRAE Journal, David Eoff, December, 2008 p 38.

Focus on Energy Evaluation, Business Programs: Deemed Savings Manual V1.0, March 22, 2010. This factor implies that boilers are 30% oversized on average.

FES Analysis of bin hours based upon a 30% oversizing factor.

“Burner,” Obtained from a nation-wide survey conducted by ASHRAE TC 1.8 (Akalin 1978). Data changed by TC 1.8 in 1986.

FES review of PY2/PY3 costs for custom People’s and North Shore high turndown burner projects. See High Turndown Costs.xlsx for details.

Release 3.0 Operations & Maintenance Best Practices A Guide to Achieving Operational Efficiency, August 2010, Federal Energy Management Program, US Department of Energy. The equation was determined by plotting the values in Table 9.2.1 – Boiler Cycling Energy Loss.

PA Consulting, KEMA, Focus on Energy Evaluation, Business Programs: Deemed Savings Manual V1.0, March 22, 2010, Page 4-12.

Ibid.

10:1 ratio used to qualify for efficient equipment.

Ontario Energy Board, “Final Report: Custom Measure Life”, Michaels Energy, May 10, 2018, burner modification measure life is estimated at 20 years.

Codes and Standards Enhancement Initiative (CASE) – Commercial Boilers; 2013 California Building Energy Efficiency Standards, California Utilities Statewide Codes and Standards Team, October 2011 (pg. 19). The estimated incremental costs were provided by boiler control representatives and did not vary with boiler capacity. The $8,500 estimated incremental cost represents the mid-point of the estimated price range.

Available and Emerging Technologies for Reducing Greenhouse Gas Emissions from Industrial, Commercial, and Institutional Boilers, Prepared by the Sector Policies and Programs Division Office of Air Quality Planning and Standards U.S. Environmental Protection Agency Research Triangle Park, North Carolina 27711, October 2010, Table 1. ICI Boilers – Summary of Greenhouse Gas Emission Reduction Measures, pg. 8.

Department of Energy (DOE). January 2012, Steam Tip Sheet #4, Improve Your Boiler’s Combustion Efficiency. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. This value was determined as an appropriate average over the stack temperatures and excess air levels indicated.

Ontario Energy Board, “Final Report: Custom Measure Life”, Michaels Energy, May 10, 2018, burner modification measure life is estimated at 20 years.

CODES AND STANDARDS ENHANCEMENT INITIATIVE (CASE) PROCESS BOILERS, 2013 California Building Energy Efficiency Standards, California Utilities Statewide Codes and Standards Team, October 2011, pg. 22.

Department of Energy (DOE). 2009. Energy Matters newsletter. Fall 2009- Vol. 1, Iss. 1. Washington, DC: U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy, Industrial Technologies Program.

Ibid.

Department of Energy (DOE), January 2012, Steam Tip Sheet #4, Improving Your Boiler’s Combustion Efficiency. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. This value was determined as an appropriate average over the stack temperatures and excess air levels indicated.

CODES AND STANDARDS ENHANCEMENT INITIATIVE (CASE) PROCESS BOILERS, 2013 California Building Energy Efficiency Standards, California Utilities Statewide Codes and Standards Team, October 2011, pg. 22.

State of Wisconsin Public Service Commission of Wisconsin Focus on Energy Evaluation Business Programs: Measure Life Study Final Report: August 25, 2009, Table 1-2. Recommended Measure Life by WISeerts Group Description, pg. 1-4.

CODES AND STANDARDS ENHANCEMENT INITIATIVE (CASE) PROCESS BOILERS, 2013 California Building Energy Efficiency Standards, California Utilities Statewide Codes and Standards Team, October 2011, pg. 22.

Based on internet review of savings potential;

“Up to 4%”:  Use of Automatic Vent Dampers for New and Existing Boilers and Furnaces, Energy Innovators Initiative Technical Fact Sheet, Office of Energy Efficiency, Canada, 2002

“Up to 1%”: Page 9, The Carbon Trust, “Steam and high temperature hot water boilers”, March 2012,

“1 - 2%”: Page 2, Sustainable Energy Authority of Ireland “Steam Systems Technical Guide”.

CODES AND STANDARDS ENHANCEMENT INITIATIVE (CASE) PROCESS BOILERS, 2013 California Building Energy Efficiency Standards, California Utilities Statewide Codes and Standards Team, October 2011, pg. 22.

Measure Life Report, Residential and Commercial/Industrial Lighting and HVAC Measures, GDS Associates, June 2007.

A market survey was performed to determine these costs.

This value comes from the reference table “Savings Summary by Building Type and System Type.” The formula and the input tables in this section document assumptions used in calculation spreadsheet “Pipe Insulation Savings 2013-11-12.xlsx”.

Average efficiencies of units from the California Energy Commission (CEC).

Ibid.

Katrakis, J. and T.S. Zawacki. “Field-Measured Seasonal Efficiency of Intermediate-sized Low-Pressure Steam Boilers”.  ASHRAE V99, pt. 2, 1993.

Zimmerman, Cliff, Franklin Energy, “Thermal Regain Factor_4-30-14.docx”, 2014. Based on climate zone 2. Note ‘Location not specified – Commercial’ assumes semi-conditioned spaces with 50% pipes providing space heating and 50% providing DHW. ‘Location not specified – Commercial’ assumes semi-conditioned annual usage.

Efficiency Vermont TRM 10/26/11 for HVAC VSD motors.

NEEP Incremental Cost Study Phase Two Final Report.

Methodology developed and tested in Del Balso, Ryan Joseph. “Investigation into the Reliability of Energy Efficiency/Demand Side Management Savings Estimates for Variable Frequency Drives in Commercial Applications”. A project report submitted to the Faculty of the Graduate School of the University of Colorado, 2013.

Lawrence Berkeley National Laboratory, and Resource Dynamics Corporation. (2008). “Improving Motor and Drive System Performance; A Sourcebook for Industry”. U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy. Golden, CO: National Renewable Energy Laboratory.

Douglass, J. (2005). Induction Motor Efficiency Standards. Washington State University and the Northwest Energy Efficiency Alliance, Extension Energy Program, Olympia, WA, October 2005.

Hours per year are estimated using the eQuest or OpenStudio models as the total number of hours the fans are operating for heating, cooling and ventilation for each building type.

Assumed service life limited by controls -" Demand Control Ventilation Using CO2 Sensors", pg. 19, by US Department of Energy Efficiency and Renewable Energy.

“National Cost-Effectiveness of ASHRAE Standard 90.1-2010 Compared to ASHRAE Standard 90.1-2007”, PNNL, November 2007 (page 4-16).

Energy savings modeled using IL TRM energy models with added energy recovery wheels or enthalpy plates. Energy recovery device specifications based on product data from the AHRI Certification Directory (https://www.ahridirectory.org/Search/SearchHome?ReturnUrl=%2f). See reference “ERV Effectiveness AHRI Directory Survey.”

Demand savings modeled using IL TRM energy models with added energy recovery wheels or enthalpy plates. Energy recovery device specifications based on  product data from the AHRI Certification Directory (https://www.ahridirectory.org/Search/SearchHome?ReturnUrl=%2f). Coincident demand measured according to TRM guidelines, though in 1-hour increments as established by the eQUEST simulation.

Weather Station Data, 99.6% Heating DB - 2013 Fundamentals, ASHRAE Handbook

Energy Recovery Fact Sheet - Center Point Energy, MN

PA Consulting, Focus on Energy Evaluation, Business Programs: Measure Life Study, August 25, 2009.

Cleaver Brooks. March 2012, Boiler Efficiency Guide, Pg. 7, Figure 1.

The minimum stack temperature for a non-condensing economizer is 250°F from Department of Energy (DOE). January 2012, Steam Tip Sheet #26A, Consider Installing a Condensing Economizer. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. The average temperature drop is assumed to be ½ way between the existing and efficient temperature minimum, ( 425°F + 250°F ) / 2 = 338°F.

The minimum stack temperature for a non-condensing economizer is 250°F from Department of Energy (DOE). January 2012, Steam Tip Sheet #26A, Consider Installing a Condensing Economizer. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. The average temperature drop is assumed to be ½ way between the existing and efficient temperature minimum, ( 480°F + 250°F ) / 2 = 365°F.

The minimum stack temperature for a condensing economizer is 250°F from Department of Energy (DOE). January 2012, Steam Tip Sheet #26A, Consider Installing a Condensing Economizer. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. The average temperature drop is assumed to be ½ way between the existing and efficient temperature minimum, ( 425°F + 135°F ) / 2 = 280°F.

The minimum stack temperature for a condensing economizer is 250°F from Department of Energy (DOE). January 2012, Steam Tip Sheet #26A, Consider Installing a Condensing Economizer. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. The average temperature drop is assumed to be ½ way between the existing and efficient temperature minimum, ( 480°F + 135°F ) / 2 = 308°F.

United States EPA, Climate Wise: Wise Rules for Industrial Efficiency, July 1998. The Wise Rules indicate savings range of 1-2% per 40°F reduction, so utilizing 1% is a conservative approach.

These average values should be utilized in absence of actual temperature data. An economizer with a zero temperature change between the existing and the efficient temperatures would not be installed, so these average values are conservative.

PA Consulting, Focus on Energy Evaluation, Business Programs: Measure Life Study, August 25, 2009.

Cleaver Brooks. March 2012, Boiler Efficiency Guide, Pg. 7, Figure 1.

The minimum stack temperature for a non-condensing economizer is 250°F from Department of Energy (DOE). January 2012, Steam Tip Sheet #26A, Consider Installing a Condensing Economizer. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. The average temperature drop is assumed to be ½ way between the existing and efficient temperature minimum, ( 425°F + 250°F ) / 2 = 338°F.

The minimum stack temperature for a non-condensing economizer is 250°F from Department of Energy (DOE). January 2012, Steam Tip Sheet #26A, Consider Installing a Condensing Economizer. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. The average temperature drop is assumed to be ½ way between the existing and efficient temperature minimum, ( 480°F + 250°F ) / 2 = 365°F.

The minimum stack temperature for a condensing economizer is 250°F from Department of Energy (DOE). January 2012, Steam Tip Sheet #26A, Consider Installing a Condensing Economizer. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. The average temperature drop is assumed to be ½ way between the existing and efficient temperature minimum, ( 425°F + 135°F ) / 2 = 280°F.

The minimum stack temperature for a condensing economizer is 250°F from Department of Energy (DOE). January 2012, Steam Tip Sheet #26A, Consider Installing a Condensing Economizer. Advanced Manufacturing Office. Washington, DC: U.S. Department of Energy. The average temperature drop is assumed to be ½ way between the existing and efficient temperature minimum, ( 480°F + 135°F ) / 2 = 308°F.

United States EPA, Climate Wise: Wise Rules for Industrial Efficiency, July 1998. The Wise Rules indicate savings range of 1-2% per 40°F reduction, so utilizing 1% is a conservative approach.

These average values should be utilized in absence of actual temperature data. An economizer with a zero temperature change between the existing and the efficient temperatures would not be installed, so these average values are conservative.

Work Paper – Tune up for Boilers serving Space Heating and Process Load by Resource Solutions Group, January 2012

”Gates Corporation Announces New EPDM Molded Notch V-Belts,” The Gates Rubber Co., June 2010 (Assumed 3% efficiency improvement).

“Synchronous Belt Drives Offer Low Cost Energy Savings,” Baldor. February 2009. (attached in Reference Documents).

"Energy Savings from Synchronous Belts," The Gates Rubber Co., February 2014. (Assumed 5% efficiency improvement).

“Motor System Tip Sheet #5, Replace V-Belts with Cogged or Synchronous Belt Drives,” USDOE-EERE, September 2005. (Assumed 2% efficiency improvement).

ComEd Trm June 1, 2010 page 139. The Office hours is based upon occupancy from the eQuest model developed for EFLH, since it was agreed the ComEd value was too low.

“DEER2014-EUL-table-update_2014-02-05.xlsx,” Database for Energy Efficiency Resources (DEER), DEER2014 EUL Table. (attached in Reference Documents).

Grainger catalog on-line web-site for Dayton v-belt pricing.

Assumed to be $150 based on mechanical contractor estimate.

Based on review and trend fitting cost data from Grainger online. See reference document “Notched V Belts costs.xlsx” for derivation.

Note that kWConnected may be determined using various methodologies. The examples provided use rated HP and assumed load factor. Other methodologies include rated voltage and full load current with assumed load factor, or actual measured voltage and current.

Com Ed TRM June 1, 2010.

Efficiency values for motors less than one HP taken from Baldor Electric Catalog 501, standard motor product catalog.

Hours per year are estimated using the eQuest models as the total number of hours the fans are operating for heating, cooling and ventilation for each building type.

Based on information found in Advanced Manufacturing Office, US DOE, “Replace V-Belts with Notched or Synchronous Drives”, (US Department of Energy Motor Systems Tip Sheet #5, DOE/GO-102012-3740,  November 2012). V-belt drives can have a peak efficiency of 95% and synchronous belts operate at 98%, therefore ESF is (1-95%/98%) = 3.1%.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

American Standard Heating & Air Conditioning, Maintenance for Indoor Units

Assumed consistent with other tune-up measures.

Fe is estimated using TRM models for the three most popular building types for programmable thermostats: low-rise office (10.2%), sit-down restaurant (8.6%), and retail – strip mall (4.4%). 7.7% reflects the average Fe of the three building types. See “Fan Energy Factor Example Calculation 2021-06-23.xlsx” for reference.

Higher Heating Value (HHV): refers to the heating value of the fuel and is defined as the total thermal energy available, including the heat of condensation of water vapors, resulting from complete combustion of the fuel versus the Lower Heating Value (LHV), which assumes the heat of condensation is not available.

For complex systems this value may be obtained from a CHP System design/financial analysis study.

These values are subject to regular updates so should be reviewed regularly to ensure the current assumptions are correct. Refer to the latest EPA eGRID data. Current values, based on eGrid 2018 are:

- Non-Baseload RFC West: 10,024 Btu/kWh * (1 + Line Losses)

- Non-Baseload SERC Midwest: 9,871 Btu/kWh * (1 + Line Losses)

- All Fossil Average RFC West: 9,575 Btu/kWh * (1 + Line Losses)

- All Fossil Average SERC Midwest: 10,369 Btu/kWh * (1 + Line Losses)

For complex systems this value may be obtained from a CHP System design/financial analysis study.

220 ILCS 5/8-103; 220 ILCS 5/16-111.5B

220 ILCS 5/8-104

As used in this measure characterization, EEPS programs are defined as those energy efficiency programs implemented pursuant to Sections 8-103, 8-104, and 16-111.5B of the Illinois Public Utilities Act. Technically, EEPS programs pertain to energy efficiency programs implemented pursuant to 220 ILCS 5/8-103 and 220 ILCS 5/8-104. However, for simplicity in presentation, this measure defines EEPS programs as also including those programs implemented pursuant to 220 ILCS 5/16-111.5B (these programs are funded through the same energy efficiency riders established pursuant to Section 8-103).

Approaches range from ignoring the increased gas use entirely (i.e., no “penalty”) to applying approximately 40-60% “penalties”, depending on the CHP efficiency and based on the equivalent grid kWh that the increased gas use represents.

Consider, for example, a hypothetical CHP system that produces 5 million kWh annually, consumes 50 million kBtu of gas annual to generate that electricity (i.e. electric efficiency of approximately 34.8% HHV), reduces on-site gas use for space heating by 26 million kBtu of gas (i.e. equivalent to approximately 81.5% CHP thermal output utilization displacing gas used in a 70% efficient space heating boiler) and has a total annual CHP efficiency of 70.6% HHV.  In this example, the net increase in on-site gas use is 24 million kBtu. At a carbon dioxide emission rate of 53.06 kg/MMBtu for burning natural gas, that translates to an increase in on-site carbon dioxide emissions of 1404 tons per year.  At an estimated marginal emission rate of 1.098 tons of carbon dioxide per MWh in Illinois, that is equivalent to electric grid production of approximately 1.28 million kWh, or penalty of about 25.6% of the CHP system’s electrical output if a precise calculation of carbon equivalency was utilized to assign savings.  In comparison, the simplified table above would entitle an electric utility to claim savings equal to 75.6% of the electric output (i.e., a penalty of 24.4% of electrical output) if it was the only utility promoting the system.  In a gas and electric example, the electric savings claimed would be 70% of the production (a penalty of 30% of the CHP system’s electrical output) and 12.5% of the recovered thermal output, equivalent to 2.23 million kBtu. The difference between the electric only scenario and the electric and gas, on the electric side, is 5% of the electric output or 250,000 kWh, which would require 2.45 million kBtu input at an efficiency of 34.8% HHV.

If some or all of the existing electric chiller peak demand is no longer needed due to new waste heat powered chillers (e.g., absorption), the coincidence factor should be adjusted appropriately.

In most cases, it is expected that waste-heat-to-power systems will not provide any new net useful thermal energy output, since the CHP system will be driven by thermal energy that was otherwise being wasted.  If additional natural gas or other purchased energy is used onsite, it should be properly accounted for.

“EPA Combined Heat and Power Partnership Resources” Oct 07, 2014, in the document “Catalog of CHP Technologies”, US EPA, September 2017, pages 2-16,, 3-14, 4-14, 5-14, and 6-16.

Spentzas, Steve, et. al, “1009: Commercial and Industrial Air Curtains – Public Project Report,” Nicor Gas Emerging Technology Program (Oct 2014): 9.

Navigant Consulting Inc, Measures and Assumptions for Demand Side Management (DSM) Planning: Appendix C: Substantiation Sheets, “Air Curtains – Single Door,” Ontario Energy Board, (April 2009): C-137.

2014 Database for Energy-Efficient Resources, EUL/RUL (Effective/Remaining Useful Life) Values, February 4, 2014.

Based on manufacturer interviews and air curtain specification sheets.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

ASHRAE, “Ventilation and Infiltration,” in 2013 ASHRAE Handbook – Fundamentals (2013): Ch 16.1 - 16.37.

National Solar Radiation Data Base – 1991 – 2005 Update: Typical Meteorological Year 3, NREL.

Spentzas, Steve, et. al, “1009: Commercial and Industrial Air Curtains – Public Project Report,” Nicor Gas Emerging Technology Program (Oct 2014): 10.

Wang, Liangzhu, “Investigation of the Impact of Building Entrance Air Curtain on Whole Building Energy Use,” Air Movement and Control International, Inc. (2013). 4.

Wang, Liangzhu, “Investigation of the Impact of Building Entrance Air Curtain on Whole Building Energy Use,” Air Movement and Control International, Inc. (2013). 4.

National Solar Radiation Data Base – 1991 – 2005 Update: Typical Meteorological Year 3, NREL.

Note that cooling days (CD) are calculated by first determining its value from the TMY3 data associated with the appropriate weather station as defined by and used elsewhere in the Illinois TRM. Using the TMY3 outdoor air dry bulb hourly data,  the annual hours are totaled for every hour that the outdoor air dry bulb temperature is above a designated zero heat loss balance point temperature or base temperature for cooling. For commercial and industrial (C&I) buildings, a base temperature for heating of 55 oF is designated in the Illinois TRM, but building specific base temperatures are recommended for large C&I projects. Additionally, the TRM uses a 30-year normal data for degree-days while the CD calculation was based on TMY3 data; in order to account for this, calculations of CD were also normalized by the ratio of CDD to align the calculated values more closely with the TRM.

Note that Heating Days (HD) are calculated following the same approach outlined in the Cooling Days section.

Average enthalpies were estimated following ASHRAE guidelines for perfect gas relationships for dry air associated with hourly TMY3 data. Enthalpies were then averaged for all values associated with a dry-bulb outdoor air temperature that exceeded the indoor air temperature setpoint. Other enthalpy values may be interpolated for indoor air temperature setpoints not represented in the table. Note that while outdoor air enthalpies increase with higher temperature setpoints, the change in enthalpy from indoor to outdoor will decrease.

Average wind speeds are calculated based on the TMY3 wind speed data. Because this data is collected at an altitude of 33 ft, wind speed is approximated for a 5 ft level based on ASHRAE Handbook guidelines using the urban/suburban parameters for adjusting wind speed based on altitude (Layer thickness (ft) δ = 1200, Exponent a = 0.22).

ASHRAE, “Airflow Around Buildings,” in 2013 ASHRAE Handbook – Fundamentals (2013): p 24.3.

ASHRAE, “Ventilation and Infiltration,” in 2013 ASHRAE Handbook – Fundamentals (2013): p 16.13

ASHRAE, “Ventilation and Infiltration,” in 2013 ASHRAE Handbook – Fundamentals (2013): p 16.13.

Based on binned data from TMY3 & adjusted bracketed thermostat setpoint temperatures. Interpolate other values as needed.

Assumed conservative estimate based on referenced study results and ASHRAE 2004 effectiveness range of 60-80% for air curtains. Jaramillo, Julian, et. Al. “Application of Air Curtains in Refrigerated Chambers,” International Refrigeration and Air-Conditioning Conference, Purdue University e-Pubs (July 14-17, 2008).

ASHRAE, “Room Air Distribution Equipment,” in 2004 ASHRAE Handbook – HVAC Systems and Equipment (2004): p 17.8.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year

Note that Heating Days (HD) are calculated following the same approach outlined in the Cooling Days section.

ASHRAE, “Ventilation and Infiltration,” in 2013 ASHRAE Handbook – Fundamentals (2013): p 16.13

Assumed conservative estimate based on referenced study results and ASHRAE 2004 effectiveness range of 60-80% for air curtains. Jaramillo, Julian, et. Al. “Application of Air Curtains in Refrigerated Chambers,” International Refrigeration and Air-Conditioning Conference, Purdue University e-Pubs (July 14-17, 2008).

ASHRAE, “Room Air Distribution Equipment,” in 2004 ASHRAE Handbook – HVAC Systems and Equipment (2004): p 17.8.

Assumes approximately 1 hour of maintenance (include cleaning out filters, greasing, and checking that the designed angle of attack on the blower nozzle is at the designed position) based on manufacturer input and product spec sheets.

Kosar, Doug, “1026: Destratification Fans – Public Project Report,” Nicor Gas, Emerging Technology Program (Oct 2014): 16.

Kosar, Doug, “1026: Destratification Fans – Public Project Report,” Nicor Gas, Emerging Technology Program (Oct 2014): 16.

Consistent with both 2008 Database for Energy-Efficient Resources, EUL/RUL (Effective/Remaining Useful Life) Values, October 10, 2008 and GDS Associates, Inc, “Measure Life Report: Residential and Commercial/Industrial Lighting and HVAC Measures,” New England Stat Program Working Group (June 2007), p30.

Costs were obtained from manufacturer interviews and are based off of average or typical prices for base model HVLS fans. Costs include materials and labor to install the fans and tie fans into an existing electrical supply located near the fan.

Minimum heating efficiency standards for heat pumps are sourced from the Code of Federal Standards for Small and Large Commercial Package Air Conditioning and Heating Equipment (Air Cooled), 10 CFR 431.97 with compliance dates of June 16, 2008; January 1, 2010; January 1, 2017; and January 1, 2018. As the first federal appliance standards for heating efficiency for commercial heat pumps went into effect in June 2008, assuming efficiency standards equivalent to residential heat pumps prior to that date.

These were calculated at various base temperatures using TMY3 data and adjusted to make consistent with the 30 year normal data used elsewhere. For more information see ‘Destratification Fan Workpaper’; Robert Irmiger, Gas Technology Institute, 9/6/2015.

Professional judgement was used to address older vintage structures and an estimate of 50% of current code standard was used.

Consistent with IECC 2015/2018 code requirements.

Kosar, Doug, “1026: Destratification Fans – Public Project Report,” Nicor Gas, Emerging Technology Program (Oct 2014): 10-11. Field testing results indicated approximately 0.6 oF/ft for a garden center.

Aynsley, Richard, “Saving Heating Costs in Warehouses,” ASHRAE Journal (Dec 2005): 48. Identifies a 0.8 oF/ft gain.

Kosar, Doug, “1026: Destratification Fans – Public Project Report,” Nicor Gas, Emerging Technology Program (Oct 2014): 10-11. Field testing results indicated approximately 0.6 oF/ft for a garden center.

Aynsley, Richard, “Saving Heating Costs in Warehouses,” ASHRAE Journal (Dec 2005): 48.

Aynsley, Richard, “Saving Heating Costs in Warehouses,” ASHRAE Journal (Dec 2005): 51.

Because heat loss through the walls is estimated using the average space temperature pre- and post- destratification. There are a number of factors that can impact the average space temperature causing deviations from estimates of many degrees in some cases. As such, it is recommended that a conservative value for the thermal resistance through the walls, Rw, be used. A recommended method for determining Rw would be to use the highest R-value for the wall space, neglecting lower R-values associated with windows, thermal bridges, etc.

ANSI/ASHRAE/IESNA 100-1995, “Energy Conservation in Existing Buildings,” ASHRAE Standard (1995). Additionally, professional judgement was used to address older vintage structure prior to adoption of the 1995 standard and an estimate of 50% of current code standard was used.

ANSI/ASHRAE/IESNA Standard 90.1-2007, “Energy Standard for Buildings Except Low-Rise Residential Buildings,” ASHRAE Standard (2007): Table 5.5-4 and Table 5.5-5.

Aynsley, Richard, “Saving Heating Costs in Warehouses,” ASHRAE Journal (Dec 2005): 48.

Enbridge Gas Distribution, Inc., “Big Fans Deliver Big Bonus,” (Aug 2007). Additionally, multiple utilities have adopted this definition in their programs in including Enbridge Gas and Consumers Energy.

ASHRAE, Standard 90.1-2013

DEER 2014 (DEER2014 EUT Table D08 v2.05).

For more information on methodology, please refer to workpaper submitted by CLEAResult titled “CLEAResult_Economizer Repair_151020_Finalv2.doc”. Note that the original ComEd eQuest models were used in the analysis, rather than the VEIC developed models used elsewhere. VEIC do not consider this a significant issue as adjustments from the ComEd models were focused on calibrating EFLH values, not to overall energy use metrics. We also believe using the ComEd models is likely more conservative. It may be appropriate to update the analysis with the updated models at a later time.

This approach allows the savings estimate to account for the operational attributes of the baseline as well as the proposed case, yielding a better estimate than an approach that assumes a particular baseline or proposed energy use to determine savings.

DNV GL, “HVAC Impact Evaluation Final Report WO32 HVAC – Volume 1: Report,” California Public Utilities Commission, Energy Division, HVAC Commercial Quality Maintenance (CQM) (1/28/14).

Technician rule of thumb taken from CPUC ‘HVAC Impact Evaluation Final Report’, WO32, 28Jan 2015, p18.

The Brooklyn Union Gas Company, High Efficiency Heating and Water and Controls, Gas Energy Efficiency Program Implementation Plan.

NREL, “Steam Balancing and Tuning for Multifamily Residential Buildings in Chicagoland-Second Year of Data Collection”, August 2013.

“Steam Balancing and Tuning for Multifamily Residential Buildings in Chicagoland-Second Year of Data Collection”, NREL, August 2013, states that test buildings with steam balancing measures saved an average of 10.2%. The energy savings estimate assumes additional system balancing through the installation of large capacity air vents on steam main lines and the replacement of radiator vents. This work is assumed to be done in concert with any system being retrofitted with averaging controls.

Illinois Statewide Technical Reference Manual (TRM), Version 4.0 (effective June 1, 2015), 2015.

American National Standards Institute (ANSI), ANSI Z21.47 Standard for Central Gas-Fired Central Furnaces, 2012.

Department of Energy (DOE), Commercial Warm Air Furnace Standard DOE 10 CFR, Part 431, Subpart D – Commercial Warm Air Furnaces, 2004.

American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE), ASHRAE Standard 90.1 Energy Standard for Buildings Except Low-Rise Residential Buildings, 2013.

Department of Energy (DOE), Rulemaking for Commercial Warm Air Furnace Standard, Technical Support Document 2015.

Department of Energy (DOE) National Renewable Energy Laboratory, Commercial Reference Building Models of the National Building Stock, 2011.

Department of Energy (DOE) National Renewable Energy Laboratory, User’s Manual for TMY3 Data Sets, 2008.

National Climatic Data Center, 1981-2010 Climate Normals, 2015.

New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs V4, April 2016 (New York TRM).

Cost estimates from customer invoices and vendors. Material costs can be lower for bulk orders.

Infiltration equation and values for stack and wind coefficient equations from “The Use of Blower Door Data.” Max Sherman, 1998. The equation is adjusted for wall leakage area (i.e. no ceiling or floor leakage).

Average effective leakage area for multi-family building AC units from “There are Holes in Our Walls.” Prepared for Urban Green Council by Steven Winter Associates, April 2011.

“Heating Period” is defined as hours when the TMY3 dry bulb temperature is less than 55°F (balance point).

Based on NREL’s Typical Meteorological Year 3 (TMY3) data for different weather stations.

Shielding and terrain class descriptions and constants from “The Use of Blower Door Data.” Max Sherman, 1998” and “Wind and Infiltration Interaction for Small Buildings.” MH Sherman and DT Grimsrud, Lawrence Berkley Laboratory, 1982.

Based on TMY3 data, see “Covers for Room AC_11092016.xls” for more information.

Although in theory the hours should be all hours that infiltration is expected (i.e. all hours <55F), the IL TAC has agreed to use the Equivalent Full Load Hours to keep the savings at a more conservative level.

From IECC 2012 Minimum Efficiency Requirements.  For a 1 ton PTHP, COP = 2.9 – (0.026 * 12,000/1,000).

Energy Independence and Security Act of 2007 – averaged for hot water and steam boilers.

Based on “Field Demonstration of High Efficiency Gas Heaters”, prepared for Better Buildings Alliance, US. DOE, Jim Young, Navigant Consulting, 2014.

Average costs from CLEAResult’s evaluation of 9 different projects in the Chicagoland area.

Based on data collected in “Field Demonstration of High Efficiency Gas Heaters”, prepared for Better Buildings Alliance, US. DOE, Jim Young, Navigant Consulting, 2014.

Based on data collected in “Field Demonstration of High Efficiency Gas Heaters”, prepared for Better Buildings Alliance, US. DOE, Jim Young, Navigant Consulting, 2014. This study replaced four standard unit heaters with HTHV units, and the electrical energy increased from 0.4 kWh/HDD to 1.44 kWh/HDD. Therefore savings are assumed to be 1.04 kWh /HDD.

30-year normals from the National Climactic Data Center (NCDC), assuming base temperature 55.

Efficiency of existing systems assumed from ASHRAE 90.1 – 2010 and manufacturer’s specification sheets for various equipment. Steam unit heaters have a lower efficiency due to steam distribution losses.

Baseline stratification rate is based on data collected in “Field Demonstration of High Efficiency Gas Heaters”, prepared for Better Buildings Alliance, US. DOE, Jim Young, Navigant Consulting, 2014. The study also verifies that the proposed ceiling temperature can be maintained within 2-4°F of the setpoint.

Use Typical Meteorological Year (TMY3) data from NREL.

Typical infiltration rate assumed from Infiltration Modeling Guidelines for Commercial Building Energy Analysis, prepared for US. DOE by Pacific Northwestern National Laboratory, 2009.

Roof and Wall Insulation R-values are based on ASHRAE 90.1- 2010. (Jim Young 2014) (K. Gowri 2009).

Based on DOE’s Commercial Prototype Modeled Warehouse building (in Chicago), via the Building Energy Codes Program.

Electronic Code of Federal Regulations: 10 CFR 431.97, last modified September 27, 2016. Minimum EER standards are scheduled to increase to 11.0 EER on September 23, 2019.

Average of 15-18 year lifetime estimate made by the Consortium for Energy Efficiency in 2010.

Based on discussion with TTW Manufacturers at AHR 2018 Show in Chicago, IL.

Based on metering of 24 homes with central AC during PY4 and PY5 in Ameren Illinois service territory.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

If an ECM motor in the packaged system is present, savings should be claimed for this measure by referring to the Residential Furnace Blower Motor measure in the IL TRM.

Full load hours for Chicago, Moline and Rockford are provided in “Final Evaluation Report: Central Air Conditioning Efficiency Services (CACES), 2010, Navigant Consulting”, p.33. An average FLH/Cooling Degree Day (from NCDC) ratio was calculated for these locations and applied to the CDD of the other locations in order to estimate FLH. There is a county mapping table in Volume 1, Section 3.7  providing the appropriate city to use for each county of Illinois.

Electronic Code of Federal Regulations: 10 CFR 431.97, last modified September 27, 2016. Minimum EER standards are scheduled to increase to 11.0 EER on September 23, 2019.

Based on metering of 24 homes with central AC during PY4 and PY5 in Ameren Illinois service territory.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

See section 4.4 for details.

Katipamula, S., et al, “Advanced Rooftop Control (ARC) Retrofit: Field-Test Results”, Pacific Northwest National Laboratory, July 2013.

Based on IL TRM v6.0 Vol. 2 – 4.4.19 Demand Controlled Ventilation.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Energy Center of Wisconsin, ComEd Portfolio Modeling Report, July 30, 2010.

Values for electric heat are based on converting the gas therm/kBtuh factors to electric kWh/ton factors factoring in the gas heating efficiencies used in the models and assuming a 2.3 COP heat pump. See ‘ARC_ElectricHeatCalculation.xls’ for calculation.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Robert Mowris & Associates, Inc., “Laboratory Test Results of Commercial Packaged HVAC Maintenance Faults,” California Public Utilities Commission, Feb 15, 2016 page 203.

Assumed to be one third of effective useful life of an RTU (15 years).

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Energy Center of Wisconsin, ComEd Portfolio Modeling Report, July 30, 2010.

Robert Mowris & Associates, Inc., “Laboratory Test Results of Commercial Packaged HVAC Maintenance Faults,” California Public Utilities Commission, Feb 15, 2016 Section 5.4.

The average cooling energy savings for all building types and climate zones, as determined by modeling 13 small commercial building types across 5 weather zones utilizing the prototype TRM eQuest models. For additional reference on the methodology and approach to the calculation of the deemed savings factor, see “Packaged RTU Sealing_End Use Analysis_IL TRM 09042018.xlsx”.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

The Technical Advisory Committee agreed that if the cost of repair is less than 20% of the new baseline replacement cost (defined in the Measure Costs section), it can be considered early replacement.

System life of indoor components as per US DOE estimates from the Office of Energy Efficiency & Renewable Energy. The ground loop has a much longer life, but the compressor and other mechanical components are the same as an ASHP.

U.S. DOE Office of Energy Efficiency & Renewable Energy, Energy Saver details and descriptions for Geothermal Heat Pumps

Assumed to be one third of effective useful life of replaced equipment.

Assume full measure life (16 years) for replacing electric resistance as we would not expect that resistance heat would fail during the lifetime of the efficient measure.

Average calculated based on reviewing cost information received from Chicagoland GSHP installers.

Average calculated from Energy Star and RSMeans Mechanical Cost Data 2015.

Average calculated based on RSMeans Mechanical Cost Data 2015.

Average calculated based on RSMeans Mechanical Cost Data 2015 for Scroll, air cooled condenser chillers.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

From Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder.

From Res GSHP measure of the IL-TRM: As per conversations with David Buss territory manager for Connor Co, the EER rating of an ASHP equate most appropriately with the full load EER of a GSHP.

Electric resistance has a COP of 1.0 which equals 1/0.293 = 3.41 HSPF.

As per Res GSHP measure.

Assumes that the desuperheater can provide two thirds of hot water needs for eight months of the year (2/3 * 2/3 = 44%). Based on input from Doug Dougherty, Geothermal Exchange Organization.

Methodology based on Cadmus analysis. Annual hot water usage in gallons based on CBECS (2012) and RECS (2009) consumption data of East North Central (removed outliers of 1,000 kBtuh or less) to calculate hot water usage. Annual hot water gallons per tank size gallons based on the tank sizing methodology found in ASHRAE 2011 HVAC Applications. Chapter 50 Service Water Heating. Demand assumptions (gallons per day) for each building type based on ASHRAE Chapter 50 and to LBNL White Paper. LBL-37398 Technology Data Characterizing Water Heating in Commercial Buildings: Application to End Use Forecasting. Assumes hot water heater efficiency of 80%.

According to CBECS 2012 “Lodging” buildings include Dormitories, Hotels, Motel or Inns and other Lodging and “Nursing” buildings include Assisted Living and Nursing Homes.

Methodology based on Cadmus analysis. Annual hot water usage in gallons based on CBECS (2012) and RECS (2009) consumption data of East North Central (removed outliers of 1,000 kBtuh or less) to calculate hot water usage. Annual hot water gallons per tank size gallons based on the tank sizing methodology found in ASHRAE 2011 HVAC Applications. Chapter 50 Service Water Heating. Demand assumptions (gallons per day) for each building type based on ASHRAE Chapter 50 and to LBNL White Paper. LBL-37398 Technology Data Characterizing Water Heating in Commercial Buildings: Application to End Use Forecasting. Assumes hot water heater efficiency of 80%.

According to CBECS 2012 “Lodging” buildings include Dormitories, Hotels, Motel or Inns and other Lodging and “Nursing” buildings include Assisted Living and Nursing Homes.

Table 4 in Chen, et. al., “Calculating Average Hot Water Mixes of Residential Plumbing Fixtures”, June 2020, reports a value of 50.7°F for inlet water temperature for U.S. Census Division 3.

Fe is estimated using TRM models for the three most popular building types for programmable thermostats: low-rise office (10.2%), sit-down restaurant (8.6%), and retail – strip mall (4.4%). 7.7% reflects the average Fe of the three building types. See “Fan Energy Factor Example Calculation 2021-06-23.xlsx” for reference.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Expected lifetime based on median years of axial fans and dampers from the ASHRAE Equipment Life Expectancy Chart.

Default measure cost is based on sales information and labor cost estimates provided by a major Original Equipment Manufacturer (OEM) of AAC units. The OEM's estimates are based on prior installation experiences and case studies.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

The default value of 0.7 for FR is based on a survey of previous case studies which documented the field installation of AAC modules in existing HVAC systems.

The default cooling COP value of 4.0 is an approximation consistent with cooling analysis in the LEED rating system, and approximates a modern, moderate efficiency water-cooled chiller (COP = 6.0) with cooling tower and pump energy usage.

The default heating COP value of 2.5 is an approximation representing an air-source heat pump of moderate efficiency.

8 years is based upon ASHRAE Applications (2003), Section 36, Table 3 estimate of 16 years for the equipment life, reduced by 50% to account for persistence issues.

RSMeans, “Instrumentation and Control for HVAC”, Mechanical Cost Data , Kingston, MA: Reed Construction Data, 2010, pg. 255 & 632.

ASHRAE Technical Support Document, 4.2.3.2 “Estimate the Average Computer Server Heat Load”, page 4-15.

J. Brandon. “Going Green In The Data Center: Practical Steps For Your SME To Become More Environmentally Friendly. Processor”, 29, Sept. 2007.

The estimated per unit costs based on anecdotal discussion with multiple potential manufacturers.

Hardik Shah and Feibi Yuan, “Project #1113: Air Deflector for Unit Ventilator (ADUV) Interim Pilot Assessment Public Report,” Gas Technology Institute for Nicor Gas Company, Emerging Technology Program. October 29, 2018. The % savings was adjusted from 16.9% to 12% based on averaging the North orientation result, with two times the East (assuming East and West is comparable).

See “Small Commercial Thermostats Research,” memorandum from Guidehouse to ComEd dated May 15, 2020.

Based on 2017 Residential Smart Thermostat Workpaper, prepared by SCE and Nest for SCE (Work Paper SCE17HC054, Revision #0). Estimate ability of smart systems to continue providing savings after disconnection and conduct statistical survival analysis which yields 9.2-13.8 year range.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year. Multiplied by 50%.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year. Multiplied by 50%.

Electrical savings are a function of both heating and cooling energy usage reductions. For heating this is a function of the percent of electric heat (heat pumps) and fan savings in the case of a natural gas furnace.

Based on percentage of customers in ComEd Small Business Thermostat program with electric heat.

Average capacity of 705 installs of thermostats in Ameren Illinois territory installed from 2015-2020.

Assumed equal to assumption for Residential Advanced Thermostats with manual thermostat baseline, before adding savings from Thermostat Optimization (which is not applicable to small commercial customers). Note that a Guidehouse billing study in CY2020 did not find a statistically significant basis for adjusting this assumption for commercial applications, see ”Small Commercial Thermostats TRM Research” memo. April 21, 2021.

Estimates of heating and cooling reduction factors are based on consumption data analyses with matching to non-participants and are therefore net with respect to participant spillover and between net and gross with respect to free ridership. Like all consumption data analyses, they are gross with respect to non-participant spillover. For more detail, see Table 5-3 in Volume 4 of the IL-TRM. Consistent with Section 7.2 of the Illinois EE Policy Manual, applicable net-to-gross adjustments to these factors will be determined as part of the annual SAG net-to-gross process.

Fe is estimated using TRM models for the three most popular building types for programmable thermostats: low-rise office (10.2%), sit-down restaurant (8.6%), and retail – strip mall (4.4%). 7.7% reflects the average Fe of the three building types. See “Fan Energy Factor Example Calculation 2021-06-23.xlsx” for reference.

Average capacity of 639 installs of thermostats on units <=10tons in Ameren Illinois territory installed from 2015-2020 and 706 installs on units <=10tons in ComEd territory in 2021.

Based on research conducted by Guidehouse on a sample of IL Small Commercial programmable thermostat installations, which found a range of savings values depending on the modeling assumptions used. Guidehouse recommended selecting the midpoint of this range, which it deemed preferable to continuing to rely on Residential assumptions, while also accounting for the relative uncertainties involved. See “Small Commercial Thermostats Research” memo completed in 2020.

Estimates of heating and cooling reduction factors are based on consumption data analyses with matching to non-participants and are therefore net with respect to participant spillover and between net and gross with respect to free ridership. Like all consumption data analyses, they are gross with respect to non-participant spillover. For more detail, see Table 5-3 in Volume 4 of the IL-TRM. Consistent with Section 7.2 of the Illinois EE Policy Manual, applicable net-to-gross adjustments to these factors will be determined as part of the annual SAG net-to-gross process.

This factor represents the ratio of thermostat adjustment savings to thermostat replacement savings. It is based on actual thermostat algorithm data (i.e., degrees of setback, hours values, fan modes) from two years of ComEd AirCare Plus Program data (PY9+ and CY2018), including 382 thermostat adjustment installations and 3,847 thermostat replacement installations. An analysis of the data showed that on average, thermostat adjustments saved 61% and 59% of the thermostat replacement cooling savings and heating savings, respectively. For simplicity, a value of 0.6 was selected for both cooling and heating savings adjustment. See IL TRM Workpaper “4.4.48 Small Commercial Thermostats”, Guidehouse, 6/23/2021 for details.

Review of ComEd’s 2020 Baseline Study and 2019-2020 Program Data indicates that approximately half of installs are in buildings with existing manual thermostats, and half with existing programmable thermostats.

Based on Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder. Note this is appropriate for single speed units only.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year. Multiplied by 50%.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year. Multiplied by 50%.

NSF/ANSI/CAN 60 Standard: “If you manufacture, sell or distribute water treatment chemicals in North America, your products are required to comply with NSF/ANSI/CAN 60: Drinking Water Treatment Chemicals – Health Effects by most governmental agencies that regulate drinking water supplies.”

‘Study on Benefits of Removal of Water Hardness (Calcium and Magnesium Ions) from a Water Supply’, Battelle Memorial Institute, accessed April 2020.

The Water Quality Reports from ‘Illinois American Water’ were analyzed for all five TRM zones in Illinois. Based on the water hardness level and Iron content, a correlation was made to the estimated usage of hydronic equipment before de-scaling is required. See page v of ‘Study on Benefits of Removal of Water Hardness (Calcium and Magnesium Ions) from a Water Supply’, Battelle Memorial Institute and “Water Quality Summary.xlsx” for reference.

Averaged from quotes from two chemical de-scaling solution manufacturers. Quote based on one day service with two personnel, including circulating pumps, tank assembly and other necessary fittings. Quotes based on pilot project study done by Nicor Gas Emerging Technology Program and Gas Technology Institute (GTI), “Descaling of Steam Boiler Systems”, 2019-2020. A 20% RYDLYME solution is assumed for cost, based on the pilot.

Estimates based on pilot project study done by Nicor Gas Emerging Technology Program and Gas Technology Institute (GTI), “Descaling of Steam Boiler Systems”, 2019-2020, and review of the following studies:

‘Clean Firetube Boiler Waterside Heat Transfer Surfaces’, U.S. Department of Energy, April 2012.

‘Energy Conservation Program Guide for Industry and Commerce’, NBS Handbook 115 Supplement 1, U.S. Department of Energy, December 1975, accessed April 2020.

As recommended in Navigant “ComEd Effective Useful Life Research Report”, May 2018. (EUL_Summary_10-1-08.xls)

Based on chiller manufacturer provided data

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

S. Goel, M. Rosenberg, C. Eley, "ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual,” September 2017, page 3.222.

S. Goel, M. Rosenberg, C. Eley, "ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual,” September 2017, page 3.231.

Mid-range part load data was provided by multiple chiller manufacturers from typical selection data. Regression analysis was used to determine the performance curves based on part load and the differential between leaving chilled water temperature and entering condenser water temperature.  These curves are provided in the reference document “VSD Chiller Modeling – IL TRM BLDG Types_2021-0510-Rev.xlsb”

Based on DOE2.2 Curves as provided by 2016 Nonresidential Alternative Calculation Method (ACM) Reference Manual, Appendix 5.7 Performance Curves. DOE2.2 path B screw chiller modeling curves were pulled directly from eQuest, as the chiller curves in the ACM were found to go negative at low loads for this specific chiller type.  All curves specified are found in the resource document “VSD Chiller Modeling – IL TRM BLDG Types_2021-0510-Rev.xlsb.”

All models are provided in the resource document “VSD Chiller Modeling – IL TRM BLDG Types_2021-0510-Rev.xlsb.”

Values from “VSD Chiller Modeling – IL TRM BLDG Types_2021-0510-Rev.xlsb”

Estimated values based on previous models

Values from “VSD Chiller Modeling - IL TRM BLDG Types.xlsb”.

* Based on max chiller capacity as stated by vendors for V screw chillers, these chillers are not available over 550 tons; ** Values taken from ASHRAE 90.1-2016, page 286. The one exception was the allowance of chillers to go to 1,000 tons per the characterization boundaries.

Value taken from ASHRAE 90.1-2016, page 286.

Value taken from ASHRAE 90.1-2016, page 281.

S. Goel, M. Rosenberg, C. Eley, "ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual,” September 2017, page 3.224.

Values from “VSD Chiller Modeling - IL TRM BLDG Types.xlsb”.

Based on life cycle of a switch reluctance motor from P. Andrada, B. Blanque, E. Martınez, J.I. Perat, J.A. Sanchez, and M. Torrent, “Environmental and life cycle cost analysis of one switched reluctance motor drive and two inverter-fed induction motor drives,” IET Electric Power Applications (2010): page 8.

Based on cost data form Software Motor Company (SMC) on HRSRM motors, https://softwaremotor.com/.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year

Korbaga Woldekidan, Daniel Studer, and Ramin Faramarzi, “Performance Evaluation of Three RTU Energy Efficiency Technologies,” 2019.

These are based on the fan setting from a forthcoming ComEd field study.

Average cooling savings for all building types from paper entitled “Performance Evaluation of Three RTU Energy Efficiency Technologies.” Savings averaged by RTU compressor type.

Based on forthcoming ComEd Field Study (final results TBD)

Hours per year are estimated using the eQuest or OpenStudio models as the total number of hours the fans are operating for heating, cooling and ventilation for each building type.

Day, Paul and Balmer, Paul. “Independent Study Shows Sludge Build-up Significantly Affects Hydronic Heating System Performance,” May, 2011. Accessed 03/25/20.

The thermal properties of Iron Oxide are referenced from the following: Takeda, Mikako and Onishi, Takashi and Nakakubo, Shouhei and Fujimoto, Shinji. “Physical Properties of Iron-Oxide Scales on Si-Containing Steels at High Temperature,” Materials Transactions Vol 50, No. 9 (2009): pp. 2242-2246. dio:10.2320/matertrans.M2009097.

Assumptions based on typical operating hot water/steam supply temperatures for cast-iron radiators of 170°F and 220°F. ‘Clogged’ surface temperature assumptions based on temperatures below which performance of radiators starts dropping considerably.

Examples from the following source use “system design lives” of 20 and 25 years, and cite the service lifetimes of a cast iron hydronic radiator’s boiler to often be “30 years or more”.

Siegenthaler, John, Modern Hydronic Heating: For Residential and Light Commercial Buildings 3rd Edition, Delmar Cengage Learning, Clifton Park, New York, 2012.

There is limited information available on system lifetimes of hydronic radiators, as well-built and well-maintained systems tend to last for decades. We assume that a midpoint of the “design-lifes” cited above (25) can correspond to the time a hydronic radiator system begins to underperform, with one known reason for underperformance (which also happens to be the focus of this measure) being the corrosion of piping materials and/or the presence of precipitated mineral contaminates restricting flow rate and thus hindering heat transfer.

Average calculated from RSMeans Cost Data 2020 for Hydronic Heating Radiators, Cast Iron.

Express Radiant, “Calculating Radiator Output”, 2014. This reference shows a representation of how a section of a typical radiator is defined.

Assumptions as per IL TRM which references CEC for these values.

Assumptions as per IL TRM which references CEC for these values.

The pipe diameter is assumed to be 2 inches and the thickness of mineral deposits in a fouled radiator (which, recall, are assumed to be composed of iron oxide), is a function of the percent of the pipe diameter which is clogged and the assumed pipe diameter.

For a steam system, the supply temperature is assumed to be 220°F. For a hot water system, the supply temperature is assumed to be 170°F. This implies convective heat transfer coefficients of 1,100 Btu/hr.ft2.°F and 700 Btu/hr.ft2.°F for steam and hot water, respectively, the inverses of which equate to steam’s or hot water’s thermal resistances.

Recall that iron oxide has a thermal conductivity of 3.01 Btu/hr.ft2.°F.

Stefan-Boltzmann constant is assumed to be 1.714×10−9 BTU⋅hr−1⋅ft−2⋅°R−4.

The convective heat transfer coefficient of Air is assumed to be 1.844 Btu/hr.ft2.°F. Emissivity of radiator surface is assumed to be 0.6.

Efficiency Vermont TRM 2021 for HVAC VSD motors.

U.S. Department of Energy Fans and Blowers Working Group

Costs are based on the U.S. Department of Energy Fans and Blowers Working Group spreadsheet: EERE-2013-BT-STD-0006-0189_attachment_1.xlsx.

“Fan Energy Index Market Research: Final Report”, prepared for ComEd by Slipstream, May 2021.

Hours per year are estimated using the eQuest or OpenStudio models as the total number of hours the fans are operating for heating, cooling and ventilation for each building type.

Methodology developed and tested in Del Balso, Ryan Joseph. “Investigation into the Reliability of Energy Efficiency/Demand Side Management Savings Estimates for Variable Frequency Drives in Commercial Applications”. A project report submitted to the Faculty of the Graduate School of the University of Colorado, 2013.

Modular boiler arrays have greater combustion efficiencies as compared to traditional steam boilers. This has been verified via a field study done by Nicor Gas ETP. The study covered an industrial manufacturing facility with (10) modular process steam boiler systems; the effective efficiency was found to be in line with the rated manufacturer efficiency of 87%.

For all boilers > 300,000 Btu/hr, Code of Federal Regulations, 10 CFR 431.87. https://www.ecfr.gov/cgi-bin/retrieveECFR?gp=&SID=1ad7fa59319aa2d3c02e66c7ead09e75&mc=true&n=sp10.3.431.e&r=SUBPART&ty=HTML.

Ibid.

Ibid.

https://www.govinfo.gov/content/pkg/FR-2020-01-10/pdf/2019-26356.pdf.

California ETRM measure “Process Boiler”, https://www.caetrm.com/measure/SWWH008/01/ , accessed April 16, 2021..

Ibid.

Miura Modular Boilers, https://s29958.pcdn.co/wp-content/uploads/2019/03/LXBrochure2016.pdf

Illinois TRM v9.0,measure 4.4.3 Process Boiler Tune-up, “Work Paper – Tune up for Boilers serving Space Heating and Process Load by Resource Solutions Group, January 2012”.

U.S. Energy Information Administration | Assumptions to the Annual Energy Outlook 2021: Commercial Demand Module: https://www.eia.gov/outlooks/aeo/assumptions/pdf/commercial.pdf

Assumed to be one third of effective useful life of replaced equipment.

U.S. Energy Information Administration (EIA), Updated Buildings Sector Appliance and Equipment Costs and Efficiencies: https://www.eia.gov/analysis/studies/buildings/equipcosts/pdf/full.pdf

Values taken from established TRM references in section 4.4.44 and based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Values taken from established TRM references in section 4.4.44 and based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm M-F, June through August) is divided by the maximum AC load during the year.

The Federal baseline for gas-fired hot water boilers <300,000 btu/hr changes from 82% to 84% in January 2021. To prevent a change in baseline mid-program, and to account for inventory meeting the old standard still in distribution, the increase in efficiency is delayed until January 2022 when a new program year starts.

Code of Federal Regulations, effective January 15, 2021 (10 CFR 432(e)(3)).

Thermal Efficiency. Code of Federal Regulations, effective March 2, 2012 (10 CFR 431.87).

Combustion Efficiency. Code of Federal Regulations, effective March 2, 2012 (10 CFR 431.87).

US DOE Building America Program, Building America Analysis Spreadsheet (for Chicago, IL), Office of Energy Efficiency & Renewable Energy.

Methodology based on Cadmus analysis. Annual hot water usage in gallons based on CBECS (2012) and RECS (2009) consumption data of East North Central (removed outliers of 1,000 kBtuh or less) to calculate hot water usage. Annual hot water gallons per tank size gallons based on the tank sizing methodology found in ASHRAE 2011 HVAC Applications. Chapter 50 Service Water Heating. Demand assumptions (gallons per day) for each building type based on ASHRAE Chapter 50 and to LBNL White Paper. LBL-37398 Technology Data Characterizing Water Heating in Commercial Buildings: Application to End Use Forecasting. Assumes hot water heater efficiency of 80%.

According to CBECS 2012 “Lodging” buildings include Dormitories, Hotels, Motel or Inns and other Lodging and “Nursing” buildings include Assisted Living and Nursing Homes.

Methodology based on Cadmus analysis. Annual hot water usage in gallons based on CBECS (2012) and RECS (2009) consumption data of East North Central (removed outliers of 1,000 kBtuh or less) to calculate hot water usage. Annual hot water gallons per tank size gallons based on the tank sizing methodology found in ASHRAE 2011 HVAC Applications. Chapter 50 Service Water Heating. Demand assumptions (gallons per day) for each building type based on ASHRAE Chapter 50 and to LBNL White Paper. LBL-37398 Technology Data Characterizing Water Heating in Commercial Buildings: Application to End Use Forecasting. Assumes hot water heater efficiency of 80%.

According to CBECS 2012 “Lodging” buildings include Dormitories, Hotels, Motel or Inns and other Lodging and “Nursing” buildings include Assisted Living and Nursing Homes.

Specific heat is the amount of heat required to change the temperature of a mass by one degree.

All Residential sized Federal Standards are from DOE Standard 10 CFR 430, Residential-Duty and Commercial Federal Standard are from DOE Standard 10 CFR 431.

Definitions provided in 10 CFR 430, Subpart B, Appendix E, Section 5.4.1.

Determination of the appropriate heat rate values for use in these calculations is complex and contentious. Values provided here are those recommended by VEIC for use in v10, but these values will continue to be discussed during the v11 update. Lifetime grid heat rate was estimated based on review of multiple sources and methodologies, and represents the estimated average marginal grid heat rate over the lifetime of the measure. Note, if legislation is passed that dictates that fuel conversion calculations should be performed at site, the site conversion factor of 3,412 BTU/kWh shall be utilized in place of the grid heat rates presented here for the specified application and timeframe.

First year heat rate was estimated in 2021, based on review of multiple sources and methodologies, and represents the estimated IL grid marginal heat rate. Note, these values will continue to be discussed during the v11 update however if legislation is passed that dictates that fuel conversion calculations should be performed at site, the site conversion factor of 3,412 BTU/kWh shall be utilized in place of the grid heat rates presented here for the specified application and timeframe.

Applying the first year heat rate for 6 years, followed by this PostAdjHgrid value for the remaining measure life produces a lifetime savings that is consistent with application of the lifetime heat rate provided. Note, these values will continue to be discussed during the v11 update however if legislation is passed that dictates that fuel conversion calculations should be performed at site, the site conversion factor of 3,412 BTU/kWh shall be utilized in place of the grid heat rates presented here for the specified application and timeframe.

The 2021 TAC discussed whether it was appropriate to apply a factor to account for any marginal gas system and distribution losses relating to the gas savings in these equations. The TAC were unable to reach agreement and so this issue will be reviewed again next year. Since this is a new assumption, and likely to be a relatively small value, it was decided to set at 0% for 2022.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Fixtures hours of use are based upon schedule assumptions used in the eQuest models, except for those building types where Illinois based metering results provide a statistically valid estimate (currently: College, Elementary School, High School, Manufacturing, Low and Mid rise Office, Retail Department Store and Warehouse) or Grocery which is based on logging survey at 28 grocery stores in a Massachusetts DNV-GL “Lighting Hours of Use Study” report, April 12,2019. Miscellaneous is a weighted average of indoor spaces using the relative area of each building type in the region (CBECS).

Hours of use for screw based bulbs are derived from DEER 2008 by building type for cfls.  Garage, exterior and multi-family common area values are from the Hours of Use Table in this document.  Miscellaneous is an average of interior space values. Some building types are averaged when DEER has two values: these include office, restaurant and retail. Healthcare clinic uses the hospital value.

The Waste Heat Factor for Energy and is developed using EQuest models for various building types base on Chicago Illinois (closest to statewide average HDD and CDD). Exterior and garage values are 1, unknown is a weighted average of the other building types.

Coincident diversity factors are based on either combined IL evaluation results (College, Elementary School, High School, Manufacturing, Low and Mid rise Office, Retail Department Store and Warehouse), case lighting projects performed over several years by Michaels Energy in Illinois and other jurisdictions (Refrigerated and Freezer Cases), or based upon schedules defined in the eQuest models described (all others).

IFkWh Resistance value is developed using EQuest or OpenStudio models consistent with methodology for Waste Heat Factor for Energy.

Heat penalty assumptions are based on converting the IFkWh Resistance multiplier value in to IFtherms or IF kWhHeat Pump  by applying relative heating system efficiencies. The gas efficiency was assumed to be 80% AFUE and the electric resistance is assumed to be 100%, for Heat Pump is assumed to be 2.3COP.

Agriculture lighting loadshapes, operational hours, and HVAC interactive factors were developed based on field experience and research material for the general agriculture, indoor agriculture, poultry and dairy commodities. Please see the excel files, ‘General Agriculture Loadshape’ and ‘Indoor Agriculture Lighting Loadshape’ on the 8760-calculation approach and for more detail. Due to livestock housing having little to no mechanical cooling systems, waste heat cooling and associated demand factors were assumed to be 1.00.

Based on Navigant verified value using 2014 Astronomical Applications Department, U.S. Naval Observatory data for ComEd’s service territory. See Navigant Memorandum ‘RE: LED Street Lighting Program Hours of Use for the ComEd and DCEO Programs. June 21, 2017’.

For closed refrigerated case lighting (open cases should use building type WHF), the value is 1.29 (calculated as (1 + (1.0 / 3.5))). Based on the assumption that all lighting in refrigerated cases is mechanically cooled, with a typical 3.5 COP refrigeration system efficiency, and assuming 100% of lighting heat needs to be mechanically cooled at time of summer peak. Assumes 3.5 COP for medium temp cases based on the average of standard reciprocating and discus compressor efficiencies with Saturated Suction Temperatures of 20°F and a condensing temperature of 90°F.

For closed freezer case lighting (open cases should use building type WHF), the value is 1.50 (calculated as (1 + (1.0 / 2.0))). Based on the assumption that all lighting in freezer cases is mechanically cooled, with a typical 2.0 COP freezer system efficiency, and assuming 100% of lighting needs to be mechanically cooled at time of summer peak. Assumes 2.0 COP for low temp cases based on the average of standard reciprocating and discus compressor efficiencies with Saturated Suction Temperatures of -20°F and a condensing temperature of 90°F.

Interior controls % savings based except where noted on LBNL, Williams et al, "Lighting Controls in Commercial Buildings", 2012, p172. ESF for Vacancy Sensors is based on Papamichael, Konstantions, Bi-Level Switching in Office Spaces, California Lighting Technology Center, February 1,2010. See Figure 8 on page 10 for relevant study results. The study shows a 30% extra savings above a typical occupancy sensor; 24% * 1.3 = 31%.

ESF for Luminaire Level Lighting Controls, and 10% High End Trim adder are based upon review of:

- Pacific Northwest National Laboratory, “Evaluation of Advanced Lighting Control Systems in a Working Office Environment”, November 2018.

- Schuetter et al., “Cree SmartCast Lighting Retrofit Demonstration: LED Fixtures and Controls for Advanced Holistic Lighting Solutions”, September 2020 (expected).

- DesignLights Consortium and NEEA, “Energy Savings from Networked Lighting Control and Luminaire-level Lighting Control Systems: 2020 Update”,  2020 (expected).

Refrigerated Case occupancy sensors ESF is based on percentage of operating hours spent in low-power operation during vacant periods, found in SDG&E workpaper: WPSDGENRLG0027.

Exterior sensors are based upon data from "Application Assessment of Bi-Level LED Parking Lot Lighting" p6.

Calculated using the eQuest model by finding the total number of hours of exterior lighting consumption between dusk and midnight and dividing by 365 (2261 / 365 = 6.19 hours per day).

See “IL TRM Ext Lighting.xlsx” for calculation.

Based on ComEd’s 2019 Baseline Survey results indicating approximately 40% of linear fixtures are T12s.

Based on the assessment of active projects in the 2008-09 ComEd Smart Ideas Program.  See files “ltg costs 12-10-10.xl.” and “Lighting Unit Costs 102605.doc”.

Default wattage reduction is based on averaging the savings from moving from a 2 to 1, 3 to 2 and 4 to 3 lamp fixture, as provided in the Standard Performance Contract Procedures Manual: Appendix B: Table of Standard Fixture Wattages, Version 3.0, SCE, March 2004. An adjustment is made to the T8 delamped fixture to account for the significant increase in ballast factor. See ‘Delamping calculation.xls’ for details.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Based on weighted average of Final ComEd’s Instant Discounts program data from PY7 and PY9. For Residential installations, hours of use assumptions from ‘5.5 Interior Hardwired Compact Fluorescent Lamp (CFL) Fixture’ measure should be used.

Consortium for Energy Efficiency (CEE) Energy Efficiency Program Library, High-Performance T8 Specification, June 30, 2009.

Consortium for Energy Efficiency (CEE) Energy Efficiency Program Library, Reduced Wattage T8 Specification, July 29, 2013.

12 years is based on average of mostly CEE lamp products (9 years), T5 lamps (10.7 years) and GDS Measure Life Report, June 2007, (15 years), as recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

ibid

Illinois evaluation of PY1 through PY3 has not found that fixtures or lamps placed into storage to be a significant enough issue to warrant including an “In-Service Rate” when commercial customers complete an application form.

Based on ComEd’s Instant Incentives program data from PY7 and PY9, see “IL Commercial Lighting ISR_2018.xlsx”.

The 98% Lifetime ISR assumption is based upon review of two evaluations:

‘Nexus Market Research, RLW Analytics and GDS Associates study; “New England Residential Lighting Markdown Impact Evaluation, January 20, 2009’ and ‘KEMA Inc, Feb 2010, Final Evaluation Report:, Upstream Lighting Program, Volume 1.’ This implies that only 2% of bulbs purchased are never installed. The second and third year installations are based upon Ameren analysis of the Californian KEMA study showing that 54% of future installs occur in year 2 and 46% in year 3. The 2nd and 3rd year installations should be counted as part of those future program year savings. Note that this Final Install Rate does NOT account for leakage of purchased bulbs being installed outside of the utility territory. EM&V should assess how and if data from evaluation should adjust this final installation rate to account for this impact

Negative value because this is an increase in heating consumption due to the efficient lighting.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Watt, lumen, lamp life, and ballast factor assumptions for efficient measures are based upon Consortium for Energy Efficiency (CEE) Commercial Lighting Qualifying Product Lists.  Watt, lumen, lamp life, and ballast factor assumptions for baseline fixtures are based upon manufacturer specification sheets.  Baseline and efficient measure cost data comes from lighting suppliers, past Efficiency Vermont projects, and professional judgment.

Watt, lumen, lamp life, and ballast factor assumptions for efficient measures are based upon Consortium for Energy Efficiency (CEE) Commercial Lighting Qualifying Product Lists.  Watt, lumen, lamp life, and ballast factor assumptions for baseline fixtures are based upon manufacturer specification sheets.  Baseline and efficient measure cost data comes from lighting suppliers, past Efficiency Vermont projects, Xcel Energy Lighting Efficiency Input Wattage Guide and professional judgment.

Watt, lumen, lamp life, and ballast factor assumptions for efficient measures are based upon Consortium for Energy Efficiency (CEE) Commercial Lighting Qualifying Product Lists.  Watt, lumen, lamp life, and ballast factor assumptions for baseline fixtures are based upon manufacturer specification sheets.  Baseline and efficient measure cost data comes from lighting suppliers, past Efficiency Vermont projects, and professional judgment.

Cost assumptions for baseline fixtures are based upon manufacturer specification sheets.  Baseline and efficient measure cost data comes from lighting suppliers, past Efficiency Vermont projects, and professional judgment.

Cost assumptions for baseline fixtures are based upon manufacturer specification sheets.  Baseline and efficient measure cost data comes from lighting suppliers, past Efficiency Vermont projects, and professional judgment.

RES v C&I split is based on a weighted (by sales volume) average of ComEd PY8, PY9 and CY2018 and Ameren PY8 in store intercept survey results. See ‘RESvCI Split_2019.xlsx.

Based on ComEd’s Instant Discounts program CY2018, CY2019 and CY2020 (Rounds 1 and 2) Purchaser Survey analysis. See ComEd Instant Discounts Enduser Survey TRM Updates.xlsx. For Residential installations, hours of use assumptions from ‘5.5.6 LED Downlights’ should be used for LED fixtures and ‘5.5.8 LED Screw Based Omnidirectional Bulbs’ should be used for LED bulbs.

ENERGY STAR Program Requirements Product Specifications for Lamps (Light Bulbs), version 2.1, effective January 2, 2017.

US Department of Energy, “Energy Savings Forecast of Solid State Lighting in General Illumination Applications”, December 2019. The resultant forecast is provided on the SharePoint site “Lamp Forecast Workbook.xls”.

Based on recommendation in the Dunsky Energy Consulting, Livingston Energy Innovations and Opinion Dynamics Corporation; NEEP Emerging Technology Research Report, p 6-18.

See file “LED Lamp Updates 2021-06-09” for details on Guidehouse lamp wattage calculations based on equivalent baseline wattage and LED wattage of available ENERGY STAR product

ENERGY STAR Lamps Center Beam Intensity Benchmark Tool and Calculator

The Energy Star Center Beam Candle Power tool does not accurately model baseline wattages for lamps with certain bulb characteristic combinations – specifically for lamps with very high CBCP.

Illinois evaluation of PY1 through PY3 has not found that fixtures or lamps placed into storage to be a significant enough issue to warrant including an “In-Service Rate” when commercial customers complete an application form.

Based on ComEd’s Instant Discounts program CY2019 and CY2020 (Rounds 1 and 2) Purchaser Survey analysis. See ComEd Instant Discounts Enduser Survey TRM Updates.xlsx

In the absence of any data for LEDs specifically it is assumed that the same proportion of bulbs eventually get installed as for CFLS. The 98% CFL assumption is based upon review of two evaluations:

‘Nexus Market Research, RLW Analytics and GDS Associates study; “New England Residential Lighting Markdown Impact Evaluation, January 20, 2009’ and ‘KEMA Inc, Feb 2010, Final Evaluation Report: Upstream Lighting Program, Volume 1.’ This implies that only 2% of bulbs purchased are never installed. The second and third year installations are based upon Ameren analysis of the Californian KEMA study showing that 54% of future installs occur in year 2 and 46% in year 3. The 2nd and 3rd year installations should be counted as part of those future program year savings. Note that this Final Install Rate does NOT account for leakage of purchased bulbs being installed outside of the utility territory. EM&V should assess how and if data from evaluation should adjust this final installation rate to account for this impact.

Based on ComEd’s Instant Discounts program CY2019 and CY2020 (Rounds 1 and 2) Purchaser Survey analysis. See ComEd Instant Discounts Enduser Survey TRM Updates.xlsx

Based on ComEd’s Instant Discounts program CY2019 and CY2020 (Rounds 1 and 2) Purchaser Survey analysis. See ComEd Instant Discounts Enduser Survey TRM Updates.xlsx

First year ISR is average ISR from CY2018, CY2019 and CY2020 ComEd Small Business Kit participant installation surveys. Please see file “SB Kits Survey Analysis TRMv10 Support.xlsx”

Same lifetime as direct mail residential kits. The second and third year ISRs use the ratios from the direct mail residential kits. Please see file “SB Kits Survey Analysis TRMv10 Support.xlsx”

The appropriate T12 midlife adjustment factor was developed by the TAC Lighting Working Group. The results of a 2019 ComEd study provided survey response data on the planned replacement upon the burnout of a T12 ballast. This was adjusted by first year NTG to remove first year freeriders and therefore estimate what the non-freerider population would do at the end of T12 life. See “Linear Forecast Workbook_2020.xls” for information on calculation.

Negative value because this is an increase in heating consumption due to the efficient lighting.

See IL LED Lighting Systems TRM Reference Tables_2018.xlsx for breakdown of component cost assumptions.

The manufacturers of the new minimally compliant EISA Halogens are using regular incandescent lamps with halogen fill gas rather than halogen infrared to meet the standard and so the component rated life is equal to the standard incandescent.

Baseline and LED lamp costs are based on field data collected by CLEAResult and provided by ComEd.  See ComEd Pricing Projections 06302016.xlsx for analysis. Given LED prices are expected to continue declining assumed costs should be reassessed on an annual basis and replaced with IL specific LED program information when available.

Watt, lumen, lamp life, and ballast factor assumptions for efficient measures are based upon Consortium for Energy Efficiency (CEE) Commercial Lighting Qualifying Product Lists alongside past Efficiency Vermont projects and PGE refrigerated case study.  Watt, lumen, lamp life, and ballast factor assumptions for baseline fixtures are based upon manufacturer specification sheets.  Baseline cost data comes from lighting suppliers, past Efficiency Vermont projects, and professional judgment. Efficient cost data comes from 2012 DOE “Energy Savings Potential of Solid-State Lighting in General Illumination Applications”, Table A.1.   See "LED Lighting Systems TRM Reference Tables_2018.xlsx" for more information and specific product links.

LED Case Lighting is based on an average of DLC Horizontal and Vertical Lighting less than 80 W. This filter was intended to exclude vaportight fixtures from the average. The horizontal and vertical averages, provided by Guidehouse in 5/2020, were 4.1 W/ft and 3.7 W/ft, respectively.

Note that some measures have blended baselines (T12:T8 18:82). All values are provided to enable calculation of appropriate O&M impacts. Total costs include lamp, labor and disposal cost assumptions where applicable, see IL LED Lighting Systems TRM Reference Tables_2018.xlsx for more information.

Estimate of remaining life of existing unit being replaced.

Price includes new exit sign/fixture and installation. LED exit cost cost/unit is $22.50 from the NYSERDA Deemed Savings Database and assuming IL labor cost of 15 minutes @ $40/hr.

Assuming continuous operation of an LED exit sign, the Summer Peak Coincidence Factor is assumed to equal 1.0.

Based on review of available product.

Average CFL single sided (5W, 7W, 9W) from Appendix B 2013-14 Table of Standard Fixture Wattages.

Average LED single sided (2W) from Appendix B 2013-14 Table of Standard Fixture Wattages.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Consistent with assumption for a Standard CFL bulb ($2.45) with an estimated labor cost of $10 (assuming $40/hour and a task time of 15 minutes).

Assumes a lamp life of 12,000 hours and 8766 run hours 12000/8766 = 1.37 years.

ACEEE, (1998) A Market Transformation Opportunity Assessment for LED Traffic Signals

Ibid.

Technical Reference Manual for Pennsylvania Act 129 Energy Efficiency and Conservation Program and Act 213 Alternative Energy Portfolio Standards. Pennsylvania Public Utility Commission. May 2009.

Technical Reference Manual for Ohio, August 6, 2010.

Refer to the referenced code documents for specifics on calculating lighting power density using either the whole building method or the Space by Space method.

Measure Life Report, Residential and Commercial/Industrial/Industrial Lighting and HVAC Measures, GDS Associates, June 2007.

See Reference Code documentation for additional information.

Negative value because this is an increase in heating consumption due to the efficient lighting.

In cases where both a general building area type and a more specific building area type are listed, the more specific building area type shall apply.

Where lighting equipment is specified to be installed to highlight specific merchandise in addition to lighting equipment specified for general lighting and is switched or dimmed on circuits different from the circuits for general lighting, the small of the actual wattage of the lighting equipment installed specifically for merchandise, or additional lighting power as determined below shall be added to the interior lighting power determined in accordance with this line item.

15 years is used based on assumption that most product using this measure will be LED.

Illinois evaluation of PY1 through PY3 has not found that fixtures or lamps placed into storage to be a significant enough issue to warrant including an “In-Service Rate” when commercial customers complete an application form.

Based on assumptions from 4.5.3 High Performance and Reduced Wattage T8 fixtures.

The 98% Lifetime ISR assumption is based upon review of two evaluations:

‘Nexus Market Research, RLW Analytics and GDS Associates study; “New England Residential Lighting Markdown Impact Evaluation, January 20, 2009’ and ‘KEMA Inc, Feb 2010, Final Evaluation Report:, Upstream Lighting Program, Volume 1.’ This implies that only 2% of bulbs purchased are never installed. The second and third year installations are based upon Ameren analysis of the Californian KEMA study showing that 54% of future installs occur in year 2 and 46% in year 3. The 2nd and 3rd year installations should be counted as part of those future program year savings.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Consistent with Lighting control measure.

Goldberg et al, State of Wisconsin Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs: Incremental Cost Study, KEMA, October 28, 2009.

Based on results from “Lighting Controls Effectiveness Assessment: Final Report on Bi-Level Lighting Study” published by the California Public Utilities Commission (CPUC), prepared by ADM Associates.

Negative value because this is an increase in heating consumption due to the efficient lighting.

By applying the ESF and the same coincidence factor for general lighting savings we are in essence assuming that the savings from multi-level switching are as likely during peak periods as any other time. In the absence of better information this seems like a reasonable assumption and if anything may be on the conservative side since you might expect the peak periods to be generally sunnier and therefore more likely to have lower light levels. It is also consistent with the control type reducing the wattage lighting load, the same as the general lighting measures.

Based on research conducted by Guidehouse, interviewing 46 contractors, reported in ‘ComEd Retrofit Add-On EUL Results Memo. January 27, 2020.

Based on indicative product cost review as performed for Efficiency Vermont TRM. Cost assumption for Luminaire Level Lighting Controls is based on the average of ‘clever’ and ‘clever-hybrid’ LLLC incremental costs, including a per fixture contribution to the necessary gateway, servers and installation labor from Kisch et al, “2020 Luminaire Level Lighting Controls Incremental Cost Study”, Energy Solutions on behalf of NEEA, January 2021. Cost assumptions for Interior Networked Lighting Controls is based on the average of “office”, “warehouse”, and “retail” by building size from Schwartz et al., “The Value Proposition for Cost-Effective, Demand Responsive-Enabling Nonresidential Lighting System Retrofits in California Buildings”, Lawrence Berkeley National Laboratory and Energy Solutions prepared for California Energy Commission, April 2019.This includes both material and labor cost estimates.

Cost for High End Trim / Institutional Tuning is based on estimate provided by SlipStream based on field implementation.

Estimates of watts controlled are based on Efficiency Vermont data as provided in the 2018 TRM. Future evaluation should determine appropriate assumptions based on Illinois program data. Estimated kilowatts per sqft for interior networked lighting controls is based on the lighting power density (LPD) assumption in the Wisconsin Focus on Energy 2019 Technical Reference Manual and divided by 1000. To determine the total KWControlled multiply by the controlled sqft. Either the total KWControlled or the total sqft must be reported to estimate savings from interior networked lighting controls.

These are the general building types and the inferred baseline operating hours reported in DesignLights Consortium and NEEA, “Energy Savings from Networked Lighting Control (NLC) Systems with and without LLLC” Energy Solutions, September 2020. The inferred operating hours for “Assembly”, “Healthcare”, and “Restaurant” were excluded due to the reported small sample size (n=3, n-2, n=3 respectively). The mapping of the general building types to the building/space types listed in Section 4.5 Reference Table was completed by Guidehouse Inc.

It is recommended that evaluation is performed to assess the extent to which daylighting and high-end trim benefits are appropriately utilized in the field.

Interior controls % savings based except where noted on LBNL, Williams et al, "Lighting Controls in Commercial Buildings", 2012, p172. ESF for Vacancy Sensors is based on Papamichael, Konstantions, Bi-Level Switching in Office Spaces, California Lighting Technology Center, February 1,2010. See Figure 8 on page 10 for relevant study results. The study shows a 30% extra savings above a typical occupancy sensor; 24% * 1.3 = 31%.

ESF for Luminaire Level Lighting Controls, Networked Lighting Controls and the 13% High End Trim adder are based upon

the weighted average of results from:

- Pacific Northwest National Laboratory, “Evaluation of Advanced Lighting Control Systems in a Working Office Environment”, November 2018.

- Schuetter et al., “Cree SmartCast Lighting Retrofit Demonstration: LED Fixtures and Controls for Advanced Holistic Lighting Solutions”, September 2020 (expected).

- DesignLights Consortium and NEEA, “Energy Savings from Networked Lighting Control (NLC) Systems with and without LLLC” Energy Solutions, September 2020.. LLLC ESF used in weighted average is the average of all 98 sites with NLCs w/LLLC. NLC ESF is the average of all 194 buildings. High-end trim adder used for other lighting control types is based on the results for the 96 sites w NLCs w/o LLLC and using the “Other Control Strategies” savings where the baseline had influences from high-end trim removed.

Refrigerated Case occupancy sensors ESF is based on percentage of operating hours spent in low-power operation during vacant periods, found in SDG&E workpaper: WPSDGENRLG0027.

Exterior sensors are based upon data from "Application Assessment of Bi-Level LED Parking Lot Lighting" p6.

The ESFEE  for interior dual occupancy & daylight sensor with high-end trim is estimated to be higher than the interior networked lighting control ESFEE since this measure requires that the sensors be integrated or fixture mounted which has been documented to lead to higher savings than zone or wall sensors. The NLC measure is not specific to fixture, zone, or wall sensors.

The ESFEE  for LLLC is not separated out based on the inclusion of high-end trim since the DesignLights Consortium Technical Requirements Version NLC5 (1/25/21) requires that high-end trim is included for all interior networked lighting controls including LLLC.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Coincidence Factor Study Residential and Commercial Industrial Lighting Measures, RLW Analytics, Spring 2007.  Note, the connected load used in the calculation of the CF for occupancy sensor lights includes the average ESF.

Equal to the manufacturers standard warranty.

Based on review of solar lighting installers websites (e.g.,  elitesolarsystems.com).

The savings from solar light tubes are only realized during the sunlight hours. It is therefore appropriate to apply the single shift (8/5) loadshape to this measure.

Solatube Test Report (2005). http://www.mainegreenbuilding.com/files/file/solatube/stb_lumens_datasheet.pdf.

Ibid. The lumen values presented in the kW table represent the average of the lightest 2400 hours.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Based on weighted average of Final ComEd’s BILD program data from PY5 and PY6. For Residential installations, hours of use assumptions from ‘5.5 Interior Hardwired Compact Fluorescent Lamp (CFL) Fixture’ measure should be used.

12 years is based on average of mostly CEE lamp products (9 years), T5 lamps (10.7 years) and GDS Measure Life Report, June 2007, (15 years), as recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Illinois evaluation of PY1 through PY3 has not found that fixtures or lamps placed into storage to be a significant enough issue to warrant including an “In-Service Rate” when commercial customers complete an application form.

1st year in service rate is based upon review of PY5-6 evaluations from ComEd’s commercial lighting program (BILD) (see ‘IL Commercial Lighting ISR_2014.xls’ for more information.

The 98% Lifetime ISR assumption is based upon review of two evaluations:

‘Nexus Market Research, RLW Analytics and GDS Associates study; “New England Residential Lighting Markdown Impact Evaluation, January 20, 2009’ and ‘KEMA Inc, Feb 2010, Final Evaluation Report: Upstream Lighting Program, Volume 1.’ This implies that only 2% of bulbs purchased are never installed. The second and third year installations are based upon Ameren analysis of the Californian KEMA study showing that 54% of future installs occur in year 2 and 46% in year 3. The 2nd and 3rd year installations should be counted as part of those future program year savings.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Adapted from Efficiency Vermont Technical Reference User Manual (TRM) Measure Savings Algorithms and Cost Assumptions, October 26, 2011.

Ibid.

Adapted from Efficiency Vermont Technical Reference User Manual (TRM) Measure Savings Algorithms and Cost Assumptions, October 26, 2011.

Efficiency Vermont Technical Reference User Manual (TRM) Measure Savings Algorithms and Cost Assumptions, October 26, 2011

EPE Program Downloads. (Copy of LSF_2012_v4.04_250rows.xls). Kuiken et al, Focus on Energy Evaluation. Business Programs:  Deemed Savings Manual v1.0, Kema, March 22, 2010.

Consistent with Lighting Controls measure.

Consistent with the Multi-level Fixture measure with reference to Goldberg et al, State of Wisconsin Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs: Incremental Cost Study, KEMA, October 28, 2009. Also consistent with field experience of about $250 per fixture and $25 install labor.

Average found from the four buildings in the State of California Energy Commission Lighting Research Program

Bi-Level Stairwell Fixture Performance Final Report, October 2005.

Value determined from the Pacific Gas and Electric Company: Bi-Level Lighting Control Credits study for Interior Corridors of Hotels, Motels and High Rise Residential, June 2002.

Conservative estimate.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Coincidence Factor Study Residential and Commercial Industrial Lighting Measures, RLW Analytics, Spring 2007.  Note, the connected load used in the calculation of the CF for occupancy sensor lights includes the average ESF.

15 years from GDS Measure Life Report, June 2007.

Measured average demand data. Southern California Edison, “Replace Neon Open Sign with LED Open Sign”, Workpaper SCE13LG070, Revision 2, October 2015. Pg. 10.

Ibid.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Savings can be calculated for additional building types using the default values provided in the Reference Table in Section 4.5.

Negative value because this is an increase in heating consumption due to the efficient lighting.

Based on research conducted by Guidehouse and reported in “ComEd LED St Lighting EUL Results Memo,” January 27, 2020, Guidehouse reviewed a cross-section of products covered in 2019 energy conservation programs; these fixtures include the most commonly selected manufacturers and output spanning from 4,000 to 25,000 lumens. This review found that manufactures for the majority of LED streetlights installed through programs in IL have recently doubled the expected rated life to 100,000 hours.

Assuming an existing mercury vapor ballast with a typical rated life of 40,000. Assuming 1/3 remaining useful life and standard operation this equates to 40,000/3/4303 = 3 year remaining life, and 40,000/3/8760 = 1.5 year remaining life for 8760 operation.

High Pressure Sodium replacement cost (lamp and labor) was provided by ComEd based on their composite maintenance rate.

Assuming standard operation of streetlight occurs outside the summer peak period of 1-5 PM. Coincidence Factor is assumed to equal 0.

Based on Navigant verified value using 2014 Astronomical Applications Department, U.S. Naval Observatory data for ComEd’s service territory. See Navigant Memorandum ‘RE: LED Street Lighting Program Hours of Use for the ComEd and DCEO Programs. June 21, 2017’.

Assumes a rated life of the High Pressure Sodium lamp of 24,000 hours. High Pressure Sodium replacement cost (lamp and labor) was provided by ComEd based on their composite maintenance rate.

Estimated remaining life of an exterior lamp running 8760 hours.

Wisconsin Focus on Energy TRM 2017 based on historical project data cost of 643 units over 31 projects from 2014 to 2018.

Exterior lighting with broken photocells are typically identified by visual inspection during the daytime and it is assumed that exterior lighting that is found to be on during daylight hours is on during all day and night hours.

Assumption for Dusk to Dawn as provided in Section 4.5.

The savings for this measure will be throughout the daytime hours when the repaired photocell turns lighting off.

Source: DEER 2014.

Ibid.

Measure savings from ComEd TRM developed by KEMA. June 1, 2010.

Code of Federal Regulations at 10 CFR 431. Subpart Q §431.296.

Measure Life Study, prepared for the Massachusetts Joint Utilities, Energy & Resource Solutions, November 2005.

Measure Data and Specifications for the ”Vending and Beverage Merchandise Controller”, from the California eTRM, last updated 12/27/2018. Measure cost + Labor cost. The refrigerated machine was an average of several types (Double, single and triple doors). Please see file: SWAP011-01 MeasureDataSpec - Vending and Beverage Merchandise Controller r0.6.xlsm

Assumed that the peak period is coincident with periods of high traffic diminishing the demand reduction potential of occupancy based controls.

Occupied hours of Use per IL TRM Section 4.5 Lighting, Fixture Annual Operating Hours.

If location is known, but hours are unknown, see IL TRM Section 4.5 Lighting, for list of various locations and Annual Hours.

See 3.4.5 LED Fixtures for the F32T8 Standard Lamp - 4 foot x 2 bulbs.

Per Houghton, D. 1996. “Refrigerated Vending Machines - Overlooked Devices Hold Opportunities for Efficiency, New Services.” E Source Tech Update, TU-96-7, the typical backlit display for a refrigerated beverage vending machine consists of two five-foot linear fluorescent lamps.” (PGE, SWAP011-01 Vending and Beverage Merchandise Controller measure, MeasureDataSpec file)

See 3.4.5 LED Fixtures for the TLED Lamp x 2 bulbs.

10 CFR 431. Subpart Q §431.296

U.S. Department of Energy (DOE), Office of Energy Efficiency and Renewable Energy, Federal Energy Management Program. (n.d.) “Purchasing Energy-Efficient Refrigerated Beverage Vending Machines.” Updated January 2020.

Those standards are the most stringent and therefore savings would be conservative.

Itron, Inc. 2005. 2004-2005 Database for Energy Efficiency Resources (DEER) Update Study - Final Report. Prepared for the California Public Utilities Commission. Pg 3-22.

As recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Door heater control unit costs are based on historical cost data, specific to the state of Illinois, collected by Ameren.  See reference “Door Heater Costs AIC.xlsx” for more detail.

Source partial list from DEER 2008.

The summer peak coincidence factor is sourced from; Cadmus, “Commercial Refrigeration Loadshape Project Final Report”, Northeast Energy Efficiency Partnership, Regional Evaluation, Measurement, and Verification Forum, Lexington, MA, 2015 (table 39). The coincidence factor is based on the run-time profile of anti-sweat door heater controls, for all control types, for summer peak hours, and represents an average of the monitored reduced run time between heaters with and without controls.

Wattages per door derived from NEEP Refrigeration Loadshape Report. The Cadmus Group, Commercial Refrigeration Loadshape Project Final Report, Northeast Energy Efficiency Partnerships, Regional Evaluation, Measurement, and Verification Forum, Lexington, MA 2015 (pg. 57). For more detail, see reference file: IL TRM_Door Heater Control_Analysis_Jun 2021.xlsx

Difference in effective runtime of an uncontrolled heater and all control style heater controls. Anti-sweat door heater control reduced run time. The Cadmus Group, Commercial Refrigeration Loadshape Project Final Report, Northeast Energy Efficiency Partnerships, Regional Evaluation, Measurement, and Verification Forum, Lexington, MA 2015. Page 69, Section 4.1.4, Table 37.

Cooler and freezer bonus factors are from NEEP Refrigeration Loadshape Report. The Cadmus Group, Commercial Refrigeration Loadshape Project Final Report, Northeast Energy Efficiency Partnerships, Regional Evaluation, Measurement, and Verification Forum, Lexington, MA 2015 (pg. 78)

Energy Efficiency Supermarket Refrigeration, Wisconsin Electric Power Company, July 23, 1993.

The summer peak coincidence factor is sourced from; Cadmus, “Commercial Refrigeration Loadshape Project Final Report”, Northeast Energy Efficiency Partnership, Regional Evaluation, Measurement, and Verification Forum, Lexington, MA, 2015 (table 39). The coincidence factor is based on the run-time profile of anti-sweat door heater controls, for all control types, for summer peak hours, and represents an average of the monitored reduced run time between heaters with and without controls.

DEER, Work Paper PGE3PREF126 ECM for Walk-In Evaporator with Fan Controller Revision # 2

DEER, Work Paper PGE3PREF126 ECM for Walk-In Evaporator with Fan Controller Revision # 2

Default motor size for EC Evaporator was found to be ≤ 1/15 HP per the ComEd Standard Program data. See

ECM Motor Size Supplement.xlsx.

Ibid.

Ibid.

ENERGY STAR Program Requirements Specification for Refrigerated Beverage Vending Machines, Version 4.0

ENERGY STAR

ENERGY STAR

CFR Title 10: Energy. PART 431—ENERGY EFFICIENCY PROGRAM FOR CERTAIN COMMERCIAL AND INDUSTRIAL EQUIPMENT

Appendix C of the American National Standards Institute (ANSI)/ American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) Standard 32.1 - 2010, ‘‘Methods of Testing for Rating Vending Machines for Bottled, Canned or Other Sealed Beverages.” For combination vending machines, the refrigerated volume does not include any non-refrigerated compartments.

As recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Source: DEER, Work Paper PGE3PREF126 ECM for Walk-In Evaporator with Fan Controller Revision # 2

See reference Excel files in TRM Reference Documents folder for derivation of TRM values.

Database for UES Measures, Regional Technical Forum, Strip Curtains, version 2.1, September 2019

The scale factors have been determined with tracer gas measurements on over 100 walk-in refrigeration units during the California Public Utility Commission’s (CPUC) evaluation of the 2006-2008 CA investor owned utility energy efficiency programs. The door-open and close times, and temperatures of the infiltrating and refrigerated airs are taken from short-term monitoring of over 100 walk-in units. “Commercial Facilities Contract Group 2006-2008 Direct Impact Evaluation”, CPUC, February 2010.

Pennsylvania Public Utility Commission Technical Reference Manual, Volume 3: Commercial and Industrial Measures, State of Pennsylvania Act 129 Energy Efficiency and Conservation Program & Act 213 Alternative Energy Portfolio Standards, Revised February 2021 -- Chapter 3.5.8 Strip Curtains for Walk-in Freezers and Coolers.

DEER 2014 Effective Useful Life.

The reference for incremental cost is $10.22 per square foot of door opening (includes material and labor). 2008 Database for Energy-Efficiency Resources (DEER), Version 2008.2.05, “Cost Values and Summary Documentation”, California Public Utilities Commission, December 16, 2008.

The summer coincident peak demand reduction is assumed as the total annual savings divided by the total number of hours per year, effectively assuming the average demand reduction is realized during the peak period. This is a reasonable assumption for refrigeration savings.

The source algorithm from which the savings per square foot values are determined is based on Tamm’s equation (an application of Bernoulli’s equation) [Kalterveluste durch kuhlraumoffnungen. Tamm W,.Kaltetechnik-Klimatisierung 1966;18;142-144;] and the ASHRAE handbook [American Society of Heating, Refrigeration, and Air-Conditioning Engineers (ASHRAE). 2010. ASHRAE Handbook, Refrigeration: 13.4, 13.6].

Database for UES Measures, Regional Technical Forum, Strip Curtains, version 2.1, September 2019. Custom edits were made to the workbook in order for savings approach to align with this measure workpaper. The In-Service-Rate (described as the Removal Rate by the RTF workbook) was changed from 25% to 0%. Additionally, a 58% efficacy value was inputted for sites that had existing, but inefficient strip curtains prior to retrofit. This value is sourced from tracer gas measurements on over 100 walk-in refrigeration units during the California Public Utility Commission’s (CPUC) evaluation of the 2006-2008 CA investor owned utility energy efficiency programs. The baseline curtain efficacy rates are taken from short-term monitoring of over 100 walk-in units. “Commercial Facilities Contract Group 2006-2008 Direct Impact Evaluation”, CPUC, February 2010.

Estimated life from Efficiency Vermont TRM.

Based on the assumption that humidity levels will most likely be relatively high during the peak period, reducing the likelihood of demand savings.

Savings table uses Economizer Calc.xls. Assume 5HP compressor size used to develop kWh/Hp value. No floating head pressure controls and compressor is located outdoors.

In the source TRM (VT) this value was 2,996 hrs based on 38° F cooler setpoint, Burlington VT weather data, and 5 degree economizer deadband. The IL numbers were calculated by using weather bin data for each location (number of hours < 38F at each location is the Hours value).

A 50% duty cycle is assumed based on examination of duty cycle assumptions from Richard Travers (35%-65%), Cooltrol (35%-65%), Natural Cool (70%), Pacific Gas & Electric (58%). Also, manufacturers typically size equipment with a built-in 67% duty factor and contractors typically add another 25% safety factor, which results in a 50% overall duty factor. (as referenced by the Efficiency Vermont, Technical Reference User  Manual).

Based on a weighted average of 80% shaded pole motors at 132 watts and 20% PSC motors at 88 watts.

Wattage of fan used by Freeaire and Cooltrol.  This fan is used to circulate air in the cooler when the evaporator fan is turned off.  As such, it is not used when fan control is not present.

Average of two manufacturer estimates of 50% and 75%.

Bonus factor (1+ 1/3.5) assumes COP of 3.5, based on the average of standard reciprocating and discus compressor efficiencies with a Saturated Suction Temperature of 20°F and a condensing temperature of 90°F.

The 227 watts for an economizer is calculated from the average of three manufacturers: Freeaire (186 Watts), Cooltrol (285 Watts), and Natural Cool (218 Watts).

2014 Database for Energy-Efficiency Resources (DEER), Version 2014, “Cost Values and Summary Documentation”, California Public Utilities Commission, January, 2014.

2014 Database for Energy-Efficiency Resources (DEER), Version 2014, “Cost Values and Summary Documentation”, California Public Utilities Commission, January, 2014.

Energy Conservation Standards for Commercial Refrigeration Equipment: Technical Support Document, U.S. Department of Energy, September 2013. The information required to estimate annual energy savings for refrigerated display cases is taken from the 2013-2014 U.S. Department of Energy (DOE) energy conservation standard rulemaking for Commercial Refrigerated Equipment. During the rulemaking process, DOE estimates the energy savings specific to night covers through extensive simulation and energy models that are validated by both manufacturers of night covers and refrigerated cases. The information is also referenced from a study done by Southern California Edison and testing by Technischer Uberwachungs-Verein Rheinland, which are used by DOE for the rulemaking process.

Southern California Edison Refrigeration Technology and Test Center. Effects of the Low Emissivity Shields on Performance and Power Use of a Refrigerated Display Case. 1997. Southern California Edison, Rancho Cucamonga, CA.

Technischer Uberwachungs-Verein Rheinland E.V. Laboratory test results for energy savings on refrigerated dairy case, conducted for Econofrost.

As recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Rite Hite – Industrial High Speed Doors

Taken to represent the overall annual average temperature in Illinois. TMY3 data for the five weather regions defined by the TRM indicate averages that fall within the range of 47.6 (Rockford) to 55.9 (Marion).

Refrigerated Warehouse, 2013 California Building Energy Standards, CODES AND STANDARDS ENHANCEMENT INITIATIVE (CASE), March 2011,

Taken to represent the overall annual average in Illinois. TMY3 data for the five weather regions defined by the TRM indicate averages that fall within the range of 69.1 (Springfield) to 72.1 (Rockford).

ASHRAE, “Refrigerated –Facility Loads”, in Refrigeration Handbook 2014: ASHRAE, 2014, 24.7.

Professional judgement, in alignment with typical freezer and cooler performance found in the Michigan Energy Measures Database (MEMD).

ASHRAE, “Refrigerated –Facility Loads”, in Refrigeration Handbook 2014: ASHRAE, 2014, 24.11

ASHRAE, “Refrigerated –Facility Loads”, in Refrigeration Handbook 2014: ASHRAE, 2014, 24.6

Professional judgement.

ASHRAE, “Refrigerated –Facility Loads”, in Refrigeration Handbook 2014: ASHRAE, 2014, 24.7

Rite Hite – Industrial High Speed Doors, product line commonly uses 2HP drives.

Based on a ComEd survey that obtained the number of hours per week certain building types operate. Warehouses had an average response of 55.6 and industrials had 58.2. Calculated by taking the simple average of the two and multiplying by 52 weeks/yr.

Assumes approximately 1 hour of maintenance, based on manufacturer product spec sheets.

Customers should be encouraged to check with the manufacturer to determine any impact on warranty of new equipment due to installing Q-sync fan/motor assemblies.

Based on communication with QM Power representative, April 16, 2018. See reference document “4.16.2018 Email.msg”.

Based on communication with QM Power representative, April 24, 2018. See reference document “4.24.2018 Email.msg”.

Brian A. Fricke and Bryan R. Becker, “Q-Sync Motors in Commercial Refrigeration: Preliminary Test Results and Projected Benefits,” Oak Ridge National Laboratory, September 2015.

M. Valmiki and Antonio Corradini, “Energy Savings of Permanent Magnet Synchronous Fan Motor Assembly Refrigerated Case Evaporators,” Alternative Energy Systems Consulting, August 2016.

Xiaohui Zhou, et al, “Q-Sync Motor Performance in Walk-in Coolers and Freezers: Field Test for ComEd Emerging Technologies,” Slipstream, March 2019.

Brian A. Fricke and Bryan R. Becker, “Permanent Magnet Synchronous Motors for Commercial Refrigeration: Final

Report,” Oak Ridge National Laboratory, July 2018.

Brian A. Fricke and Bryan R. Becker, “Q-Sync Motors in Commercial Refrigeration: Preliminary Test Results and Projected Benefits,” Oak Ridge National Laboratory, September 2015.

NCI (Navigant Consulting Inc.) and PNNL (Pacific Northwest National Laboratory), “Preliminary Technical Support Document (TSD): Energy Conservation Program for Certain Commercial and Industrial Equipment: Commercial Refrigeration Equipment,” Appliances and Commercial Equipment Standards, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, US Department of Energy, Washington, D.C., 2011.

M M. Valmiki and Antonio Corradini, “Energy Savings of Permanent Magnet Synchronous Fan Motor Assembly Refrigerated Case Evaporators,” Alternative Energy Systems Consulting, August 2016.

Michael Deru, et al, “U.S. Department of Energy Commercial Reference Building Models of National Building Stock,” NREL Report TP-5500-46861, February 2011.

Michael Deru, et al, “U.S. Department of Energy Commercial Reference Building Models of National Building Stock,” NREL Report TP-5500-46861, February 2011.

ASHRAE, “ASHRAE Handbook – Refrigeration,” ASHRAE, 2018.

NCI (Navigant Consulting Inc.) and PNNL (Pacific Northwest National Laboratory), “Preliminary Technical Support Document (TSD): Energy Conservation Program for Certain Commercial and Industrial Equipment: Commercial Refrigeration Equipment,” Appliances and Commercial Equipment Standards, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, US Department of Energy, Washington, D.C., 2011.

Brian A. Fricke and Bryan R. Becker, “Permanent Magnet Synchronous Motors for Commercial Refrigeration: Final

Report,” Oak Ridge National Laboratory, July 2018.

Brian A. Fricke and Bryan R. Becker, “Q-Sync Motors in Commercial Refrigeration: Preliminary Test Results and Projected Benefits,” Oak Ridge National Laboratory, September 2015.

M M. Valmiki and Antonio Corradini, “Energy Savings of Permanent Magnet Synchronous Fan Motor Assembly Refrigerated Case Evaporators,” Alternative Energy Systems Consulting, August 2016.

Based on communication with QM Power representative, August 22, 2018. See reference document “8.22.2018 Email.msg”.

Romberger, Jeff. Wed. “Chapter 18: Variable Frequency Drive Evaluation Protocol. The Uniform Methods Project: Methods for Determining Energy Efficiency Savings for Specific Measures”. United States. doi:10.2172/1365710.

Efficiency Vermont TRM  3/16/2015 pp 19 for motor end use-variable frequency drives.

Pre- and post-VFD retrofit kWh consumption were derived from measurement of 14 condensers at 4 supermarkets in Rockford, Il. Annual savings in each Zone is the product of the number of hours in each 5-degree F Typical Meteorological Year temperature bin multiplied by the mean savings across the 14 condensers measured in the study. These estimates represent means from 10,000 simulations that include confidence intervals at the 90 percent level of +/-330, +/-330, +/-300, +/-320, and +/-310 for zones 1, 2, 3, 4, and 5, respectively. Detailed methods, assumptions, and calculations are found in “Variable Frequency Drive Energy Savings in Supermarkets Report. Slipstream, September, 30 2018” [pending report publication by ComEd.] Once published, the report will be made available to Illinois TRM Stakeholders for reference.

The measure life is sourced from the PG&E Workpaper, “Add Doors to Open Medium Temperature Cases – PGE3PREF116 R3”, June 2019.

The incremental cost is sourced from the PG&E Workpaper, “Add Doors to Open Medium Temperature Cases – PGE3PREF116 R3”, June 2019. The incremental cost for retrofitting new doors on existing refrigerated display cases is the material cost of the door and the labor cost required for installation. The material cost of the doors is $331 per linear foot with LED lighting and $301 per linear foot without LED lighting. And the installation cost is $88 per linear foot.

The change in heat gain is sourced as the typical value for a medium temperature vertical display case adding doors from the PG&E Workpaper, "Add Doors to Open Medium Temperature Cases - PGE3PREF116 R3", June 2019. The workpaper assumes a net reduction in heat gain with the installation of doors on open refrigerated display cases. The primary benefits account for the decrease in excess heat entering the display case from air infiltration. Radiation and conduction heat gains were also included in the derivation of this value. Additionally, the net heat gain has built in assumptions on how often the refrigerated case doors will be used and the display case accessed by customers and site associates, reducing some of the air infiltration benefits of the new door.

Average load difference between Hussmann open horizontal cases and lid horizontal cases across various configurations.

Average EER values were calculated as the average of standard reciprocating and discus compressor efficiencies, using a typical condensing temperature of 90°F and saturated suction temperatures (SST) of 20°F for medium temperature applications. The efficiency analysis and product review is sourced from the Efficiency Vermont TRM, which utilizes data from Emerson Climate Technology software. Medium temperature cases have an EER value of 11.36.

The measure assumes the baseline equipment is not employing night covers or any other covering but is in fact left open for the duration of its operation.

The MMBtu increase on the HVAC cooling equipment is based on an outdoor air temperature bin analysis, the total hours of operation of the cooling system, and the building's overall loss of additional cooling as a result of the installation of the doors on the open refrigerated display case. The analysis assumes a certain amount of conditioned air has to be treated to replace the air previously cooled by the display case. Furthermore, the analysis assumes an increased load on the cooling system, at outdoor temperatures above 60°F. A 25% disabling factor was also applied to account for some of the cold air pouring out of the display case and subcooling the site's conditioned space, which will not trigger a thermostatic response from the HVAC equipment. For more information on the analysis used to derive the load increase on the HVAC cooling equipment per linear foot of display case, please see the 'HVAC IE' tab in the "IL TRM_Add Doors_Analysis_Mar 2021.xlsx".

In light of limited existing market data for the efficiency of commercial air condition equipment in Iowa grocery and convenience stores, SEER assumptions are conservatively sourced from IECC 2012.

Southern California Edison Refrigeration Technology and Test Center. Effects of the Low Emissivity Shields on Performance and Power Use of a Refrigerated Display Case. 1997. Southern California Edison, Rancho Cucamonga, CA. See ‘4.6.9 Night Covers’ for more detail.

Technischer Uberwachungs-Verein Rheinland E.V. Laboratory test results for energy savings on refrigerated dairy case, conducted for Econofrost. See ‘4.6.9 Night Covers’ for more detail.

The total combined hours in which the site is providing cooling is based on an outdoor air temperature bin analysis, where the site is conditioning cold air at outdoor temperatures of 60°F and above. Weather data was sourced from TMY3 data for the specific locations. For more information on the derivation of these hours, please see 'HVAC IE' tab in the "IL TRM_Add Doors_Analysis_Mar 2021.xlsx" Night covers are not included in the peak demand savings algorithm because night covers are deployed at night, outside of the peak demand period.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

The MMBtu decrease on the HVAC heating equipment is based on an outdoor air temperature bin analysis, the total hours of operation in which the site is providing heat, and the building's overall reduced heating load as a result of the installation of the doors on the open refrigerated display case. The analysis assumes a certain reduction of conditioned air that had to be treated to make up for the air previously cooled by the display case. The reduced heat gain on the refrigerated display case equals the reduced heat loss by the site and a heating load that no longer has to be provided by the HVAC system. Furthermore, the analysis assumes a decrease load on the heating system, at outdoor temperatures below 60°F. A 25% disabling factor was also applied to account for some of the cold air pouring out of the display case and subcooling the site's conditioned space, which will not trigger a thermostatic response from the HVAC equipment. For more information on the analysis used to derive the load decrease on the HVAC heating equipment per linear foot of display case, please see the 'HVAC IE' tab in the "IL TRM_Add Doors_Analysis_Mar 2021.xlsx".

Typical heating system efficiency of 80%, consistent with current heating efficiency assumptions for lighting HVAC interactive effects for commercial fossil fuel-fired systems.

California DEER 2014 Effective Useful Life (EUL) table.

Costs are based on number of additional valves per condenser motor for different HP ratings and includes installation labor costs. Costs are averaged and shown on a per HP basis. See reference document ComGroceryFHPCSingleCompressor_v2_1.xlsm, worksheet 'CostData&Analysis,' blue highlighted cells. A comparison of prevailing wages in the Pacific Northwest showed high similarity to Illinois and therefore a simple inflation technique (using the US BLS's CPI Inflation Calculator, comparing the purchasing power of $1.00 in January 2012 to May 2021) was used to convert 2012$ to 2021$ (a multiplier of 1.19).

Unknown values based on weighted average; 2010 ASHRAE Refrigeration Handbook, page 15.1 “Medium- and low-temperature display refrigerator line-ups account for roughly 68% and 32%, respectively, of a typical supermarket’s total display refrigerators.

For unit type unknown, it is assumed 50/50 split of self-contained and remote condensing units.

Derived from RTF saving estimates for the NW climate zone and extrapolated to Illinois climate zones by using heating degree-days for a 65 degree F setpoint as established in Measure 4.4.37 Unitary HVAC Condensing Furnace measure. See reference file “fhp-savings-extrapolation-xlsx-Adjusted for Illinois.xlsx,” 2021.

Department of Energy Technical Support Document.

Adjustment for inflation since incremental cost study is in $2008. The U.S. Bureau of Labor Statistic CPI Inflation Calculator was used to adjust $2008 (January) to $2021 (January). The resulting factor was 1.24. This adjustment was evaluated against current pricing of compressors (2021)  and found to be a reasonable and appropriate.

Conversion factor and offset based on a linear regression analysis of the relationship between air compressor motor nominal horsepower and incremental cost, as sourced from the Efficiency Vermont Technical Reference Manual (TRM).  Several Vermont vendors were surveyed to determine the cost of equipment.

Conversion factor based on Survey of CAGI data sheets from 200 compressors. See “IL TRM VSD Air Compressor – Supporting Information.xls” for more information.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Compressor factors were developed using DOE part load data for different compressor control types as well as load profiles from 50 facilities employing air compressors less than or equal to 40 hp, as sourced from the Efficiency Vermont TRM.(The “variable speed drive” compressor factor has been adjusted up from the 0.675 presented in the analysis to 0.705 to account for the additional power draw of the VSD).

Compressor factors were developed using DOE part load data for different compressor control types as well as load profiles from 50 facilities employing air compressors less than or equal to 40 hp, as sourced from the Efficiency Vermont TRM. (The “variable speed drive” compressor factor has been adjusted up from the 0.675 presented in the analysis to 0.705 to account for the additional power draw of the VSD). See “IL TRM VSD Air Compressor – Supporting Information.xls” for more information.

Compressor factors for this size range were developed using DOE part-load data for different compressor control types as well as load profiles from 45 compressors and 20 facilities. This data comes from ComEd Custom and Insustrial Systems programs. The compressors were filtered to reflect only rotary screw compressors, between 50 and 200 hp, and operating a minimum of 4 hour per day, Additionally, compressors with clear and consistent baseload profiles were excluded from this analysis. See “IL TRM VSD Air Compressor – Supporting Information.xls” for more information.

Compressor factors were developed using DOE part load data for different compressor control types as well as load profiles from 50 facilities employing air compressors less than or equal to 40 hp, as sourced from the Efficiency Vermont TRM.(The “variable speed drive” compressor factor has been adjusted up from the 0.675 presented in the analysis to 0.705 to account for the additional power draw of the VSD). See “IL TRM VSD Air Compressor – Supporting Information.xls” for more information.

Compressor factors for this size range were developed using DOE part-load data for different compressor control types as well as load profiles from 45 compressors and 20 facilities. This data comes from ComEd Custom and Insustrial Systems programs. The compressors were filtered to reflect only rotary screw compressors, between 50 and 200 hp, and operating a minimum of 4 hour per day, Additionally, compressors with clear and consistent baseload profiles were excluded from this analysis. See “IL TRM VSD Air Compressor – Supporting Information.xls” for more information.

Ibid.

Based on survey of manufacturer claims (Zeks, Van Air, Quincy), as recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Incremental cost research found in LPDF Costs. xlsx.

See “Industrial System Standard Deemed Saving Analysis.xls”.

See “Industrial System Standard Deemed Saving Analysis.xls”.

Assumed pressure will be reduced from a roughly 3 psi pressure drop through a filter to less than 1 psi, for a 2 psi savings

“Optimizing Pneumatic Systems for Extra Savings,” Compressed Air Best Practices, DOE Compressed Air Challenge, 2010.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Industrial System Standard Deemed Saving Analysis.xls

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Based on empirical project data from ComEd Comprehensive Compressed Air Study program and VEIC review of pricing data found in CAS Cost Data.xlsx.

Efficiency Vermont Technical Reference Manual (TRM) Measure Savings Algorithms and Cost Assumptions, August 10, 2016.

Reduced CFM consumption is based on a timer drain opening for 10 seconds every 300 seconds as the baseline. See “Industrial System Standard Deemed Saving Analysis.xls”.

Calculated based on the type of compressor control. This assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. See “Industrial System Standard Deemed Saving Analysis.xls”.

Table 8.2.3, Technical Support Document. US Department of Energy

US DOE, Evaluation of the Compressed Air Challenge® Training Program, Page 19.

PA Consulting Group (2009). Business Programs: Measure Life Study. Prepared for State of Wisconsin Public Service Commission.

Costs are from EXAIR’s website and are an average of nozzles that meet the flow requirements. Models include Atto Super, Pico Super, Nano Super, Micro Super, Mini Super, Super and Large Super nozzles. Accessed March 20, 2014.

Review of manufacturer’s information.

Technical Reference Manual (TRM) for Ohio Senate Bill 221”Energy Efficiency and Conservation Program” and 09-512-GE-UNC, October 15, 2009. Pages 170-171.

Conservative estimate based on average values provided by the Compressed Air Challenge Training Program, Machinery’s Handbook 25th Edition, and manufacturers’ catalog.

Calculated based on the type of compressor control. This assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. See “Industrial System Standard Deemed Saving Analysis.xls”.

Assumes 50% handheld air guns and 50% stationary air nozzles. Manual air guns tend to be used less than stationary air nozzles, and a conservative estimate of 1 second of blow-off per minute of compressor run time is assumed. Stationary air nozzles are commonly more wasteful as they are often mounted on machine tools and can be manually operated resulting in the possibility of a long term open blow situation. An assumption of 5 seconds of blow-off per minute of compressor run time is used.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Ibid.

As recommended in Navigant ‘ComEd Effective Useful Life Research Report’, May 2018.

Analysis of material cost between cycling and non-cycling dryers according to online prices from Grainger. Cost provided is the average incremental cost when comparing non-cycling and cycling dryers of the same CFM capacity.

Compressed Air Challenge: Compressed Air Best Practice; “Cycling Air Dryers – Are Savings Significant?”  Fox, Timothy J. and Marshall, Ron.

Engineering judgement, based on the assumption that on average, compressed air systems will operate at 50% capacity.

Compressed Air Challenge: Compressed Air Best Practice; “Cycling Air Dryers – Are Savings Significant?”  Fox, Timothy J. and Marshall, Ron.

Ibid.

DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Enclosure Cooling Solutions, Hoffman. 2018. https://hoffman.nvent.com/wcsstore/AuroraStorefrontAssetStore/User%20Downloads/Literature%20Requests/content_Bro-00127.pdf

Vortex Tube Short Course, Vortec. February 2017. https://www.vortec.com/vortex-tube-short-course

Eliminate Inappropriate Uses of Compressed Air, US Department of Energy. August 2004. https://www.energy.gov/sites/prod/files/2014/05/f16/compressed_air2.pdf

The thermostatic control lifetime is conservatively estimated at 5 years due to installation in a dirty, hazardous, or corrosive environment. Engineering judgement.

Based on a survey of Vortec and Exair product offerings. See “IL TRM Vortex Cooler Thermostat - Supporting Information.xls” for more detail.

Calculated based on the type of compressor control. This assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. See “Industrial System Standard Deemed Saving Analysis.xls”.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

This is a conservative assumption based on available case studies and conversations with distributors. Broadly, the minimum savings factor is equal to the safety factor used when sizing. This assumes that the heat generation inside the cabinet is constant. Since this not likely, the savings factor should be greater than the safety factor. 25% was selected as it was the most conservative of the case studies and a reasonable safety factor. See “IL TRM Vortex Cooler Thermostat - Supporting Information.xls” for more detail.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

The dew point limitation of the most common refrigerant-type air dryer. Improving Compressed Air System Performance: A Sourcebook for Industry, US Department of Energy. Page 48. https://www.energy.gov/sites/prod/files/2016/03/f30/Improving%20Compressed%20Air%20Sourcebook%20version%203.pdf

Lessons Learned: Saving Energy Costs with Heated Blower Purge Desiccant Dryers, Marshall, Ron. https://airbestpractices.com/system-assessments/air-treatmentn2/lessons-learned-saving-energy-costs-heated-blower-desiccant-dry-0

Regenerative Desiccant Compressed Air Dryers. White, Donald. https://airbestpractices.com/technology/air-treatmentn2/regenerative-desiccant-compressed-air-dryers

Types of Compressed Air Dryers 2: Refrigerant and Regenerative Desiccant, Compressed Air and Gas Institute (CAGI). https://airbestpractices.com/technology/air-treatment/n2/types-compressed-air-dryers-refrigerant-and-regenerative-desiccant

Regenerative Desiccant Compressed Air Dryers. White, Donald. https://airbestpractices.com/technology/air-treatmentn2/regenerative-desiccant-compressed-air-dryers

Regenerative Desiccant Compressed Air Dryers. White, Donald. https://airbestpractices.com/technology/air-treatmentn2/regenerative-desiccant-compressed-air-dryers

Focus on Energy Evaluation Business Programs: Measure Life Study, p. 91-92. PA Consulting Group. August 25, 2009. https://focusonenergy.com/sites/default/files/bpmeasurelifestudyfinal_evaluationreport.pdf

Analysis of equipment cost between heatless, heated, blower purge dryers according to available online pricing. The capacity range considered was 250 – 1,500 CFM. Cost provided is the average incremental cost when comparing heated and blower purge dryers to baseline heatless dryers of the same CFM capacity. See “IL TRM Deissciant Dryers – Supporting Information.xls” file for more detail.

Typical estimates of purge flow for heatless dryers range from 15-20% of dryer rated capacity. 15% was selected as a conservative value.

Consistent with Air Nozzle measure, this assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. See “Industrial System Standard Deemed Saving Analysis.xls”.

Lessons Learned: Saving Energy Costs with Heated Blower Purge Desiccant Dryers, Marshall, Ron. https://airbestpractices.com/system-assessments/air-treatmentn2/lessons-learned-saving-energy-costs-heated-blower-desiccant-dry-0

Based on a review of data sheets from six manufacturers. These values reflect average heater kW and not nominal heater kW. The heater operation will vary based on moisture load to the dryer. See “IL TRM Deissciant Dryers – Supporting Information.xls” file for more detail.

The heater operation will be controlled by temperature to avoid overheating the desiccant media. Lessons Learned: Saving Energy Costs with Heated Blower Purge Desiccant Dryers, Marshall, Ron. https://airbestpractices.com/system-assessments/air-treatmentn2/lessons-learned-saving-energy-costs-heated-blower-desiccant-dry-0

Based on a review of data sheets from six manufacturers. These values reflect average blower kW and not nominal blower kW. The blower operation will in many cases vary based on moisture load to the dryer. See “IL TRM Deissciant Dryers – Supporting Information.xls” file for more detail.

“For heatless desiccant dryers, the reduction in purge tends to be proportional only to the reduction of flow, not the reduction in moisture load due to the lower inlet temperatures.” The 50% value is based on the TRM’s assumption of a 50% dryer load factor used Illinois TRM Measure 4.7.5. Marshall, Ron. Lessons Learned: Saving Energy Costs with Heated Blower Desiccant Dryers. https://www.airbestpractices.com/system-assessments/air-treatmentn2/lessons-learned-saving-energy-costs-heated-blower-desiccant-dry-0

“But for heated style units, the dryer reacts to both reductions. This means some energy is saved due to flow reduction, and additional energy is saved due to the lower moisture load in the cooler inlet air, resulting in more energy savings when compared with heatless styles.” Marshall, Ron. Lessons Learned: Saving Energy Costs with Heated Blower Desiccant Dryers. https://www.airbestpractices.com/system-assessments/air-treatmentn2/lessons-learned-saving-energy-costs-heated-blower-desiccant-dry-0

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

The dew point limitation of the most common refrigerant-type air dryer. Improving Compressed Air System Performance: A Sourcebook for Industry, US Department of Energy. Page 48.

Lessons Learned: Saving Energy Costs with Heated Blower Purge Desiccant Dryers, Marshall, Ron.

Regenerative Desiccant Compressed Air Dryers. White, Donald.

Types of Compressed Air Dryers 2: Refrigerant and Regenerative Desiccant, Compressed Air and Gas Institute (CAGI).

Regenerative Desiccant Compressed Air Dryers. White, Donald.

Regenerative Desiccant Compressed Air Dryers. White, Donald.

Since this is a retrofit, the EUL is one-third of the dryer life which is 15 years (TRM 4.7.7). Focus on Energy Evaluation Business Programs: Measure Life Study, p. 91-92. PA Consulting Group. August 25, 2009.

Desiccant Air Dryer Control: Seeing Isn’t Always Believing. Marshall, Ron.

Lessons Learned: Saving Energy Costs with Heated Blower Purge Desiccant Dryers, Marshall, Ron.

Consistent with Air Nozzle measure, this assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. See “Industrial System Standard Deemed Saving Analysis.xls”.

Based on a review of data sheets from six manufacturers. These values reflect average heater kW and not nominal heater kW. The heater operation will vary based on moisture load to the dryer. See “IL TRM Deissciant Dryers – Supporting Information.xls” file for more detail.

The heater operation will be controlled by temperature to avoid overheating the desiccant media. Lessons Learned: Saving Energy Costs with Heated Blower Purge Desiccant Dryers, Marshall, Ron.

Based on a review of data sheets from six manufacturers. These values reflect average blower kW and not nominal blower kW. The blower operation will in many cases vary based on moisture load to the dryer. See “IL TRM Deissciant Dryers – Supporting Information.xls” file for more detail.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

“For heatless desiccant dryers, the reduction in purge tends to be proportional only to the reduction of flow, not the reduction in moisture load due to the lower inlet temperatures.” The 50% value is based on the TRM’s assumption of a 50% dryer load factor used Illinois TRM Measure 4.7.5. Marshall, Ron. Lessons Learned: Saving Energy Costs with Heated Blower Desiccant Dryers.

“But for heated style units, the dryer reacts to both reductions. This means some energy is saved due to flow reduction, and additional energy is saved due to the lower moisture load in the cooler inlet air, resulting in more energy savings when compared with heatless styles.” Marshall, Ron. Lessons Learned: Saving Energy Costs with Heated Blower Desiccant Dryers.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Ron Marshall, William Scales, Gary Shafer, Paul Shaw, Paul Sheaffer, Rick Stasyshan, H.P. Improving Compressed Air System Performance: A Sourcebook for Industry v3. United States: N. p., 2016.

The 15-year measure life is based on the value for HVAC controls within the ComEd EUL research. The ductwork has an estimated 20-year measure life but is limited by the mechanical and thermostatic controls.

This estimate is based on three representative projects received through the Nicor Custom Program. The costs in these three projects were $73/hp, $76/hp, and $84/hp.

Ron Marshall, William Scales, Gary Shafer, Paul Shaw, Paul Sheaffer, Rick Stasyshan, H.P. Improving Compressed Air System Performance: A Sourcebook for Industry v3. United States: N. p., 2016 (page 14).

The analysis of compressor load factors for the Illinois TRM’s 4.7.1 VSD Air Compressor measure show an average load factor range of 63 – 65%. For more information, please see: “IL TRM VSD Air Compressor – Supporting Information.xls”.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

These values reflect a ratio of the hours below a heating balance point over 8,760. The heating balance point is assumed to be 55°F. The data source is TMY3 data. See “Compressed Air Heat Recovery – Supporting Info” file for derivation.

80% is the federal minimum efficiency of gas-fired unit heaters. Unit heaters are a common heat source in industrial and manufacturing settings, where compressed air is likely to be in place.

The 4.5 cfm/hp rule of thumb is based on a rotary screw compressor delivering 4 to 5 cfm per 1 hp, “Relationship Between Pressure and Flow”, Compressed Air System Best Practices, Industrial Utility Efficiency.

2018 Vermont PUC: Technical Reference User Manual (TRM) Measure Savings Algorithms and Cost Assumptions

Conversion factor based on Survey of CAGI data sheets from 200 compressors. See “IL TRM VSD Air Compressor – Supporting Information.xls” for more information.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Compressor factors were developed using DOE part load data for different compressor control types as well as load profiles from 50 facilities employing air compressors less than or equal to 40 hp, as sourced from the Efficiency Vermont TRM.

Compressor factors were developed using DOE part load data for different compressor control types as well as load profiles from 50 facilities employing air compressors less than or equal to 40 hp, as sourced from the Efficiency Vermont TRM. See “IL TRM VSD Air Compressor – Supporting Information.xls” for more information.

Compressor factors for this size range were developed using DOE part-load data for different compressor control types as well as load profiles from 45 compressors and 20 facilities. This data comes from ComEd Custom and Insustrial Systems programs. The compressors were filtered to reflect only rotary screw compressors, between 50 and 200 hp, and operating a minimum of 4 hour per day, Additionally, compressors with clear and consistent baseload profiles were excluded from this analysis. See “IL TRM VSD Air Compressor – Supporting Information.xls” for more information.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Based on value from ComEd Operational Efficiency CY2018 Impact Evaluation.

Consistent with 4.7.2 Compressed Air Low Pressure Drop Filters. See “Industrial System Standard Deemed Saving Analysis.xls”.

Based on Tables 8.2.2 and 8.2.3 from Technical Support Document: Air Compressors. US Department of Energy. May, 2016.

“Optimizing Pneumatic Systems for Extra Savings,” Compressed Air Best Practices, DOE Compressed Air Challenge, 2010.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Consistent with 4.7.2 Compressed Air Low Pressure Drop Filters. See “Industrial System Standard Deemed Saving Analysis.xls”.

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.

Hank Van Ormer. “Study Proves Potential Energy Savings of AODD Pump Controls,” Compressed Air Best Practices.

https://www.airbestpractices.com/system-assessments/end-uses/study-proves-potential-energy-savings-aodd-pump-controls

“Diaphragm Pump Controller Performance Project Report,” Purdue School of Engineering and Technology. January 12, 2015.

This is an estimated based on lifetimes of similar electronic controls. HVAC controls generally have a 15-year EUL but are typically in less demanding environments than industrial pumping applications (e.g., manufacturing, wastewater treatment, etc.). For this reason, a more conservative value of 10 years was selected.

MizAir.com. Accessed August 4, 2020. https://www.mizair.com/lp-miz

Engineering judgement.

“Demand-Side Savings: Energy Efficiency in Optimizing Compressed Air,” Air Power USA. Page 8-46.

Calculated based on the type of compressor control. This assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. See “Industrial System Standard Deemed Saving Analysis.xls”

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules

This is the average value of several references, the strongest of which is a lab study that reports a savings range of 20% - 50%. “Diaphragm Pump Controller Performance Project Report,” Purdue School of Engineering and Technology. January 12, 2015. For a full list of savings estimates, see the “IL TRM AODD Controls – Supporting Info.xls”

Weighting of 16% single shift, 23% two shift, 25% three shift and 36% continual based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules

SCE Pump Test Final Report (2009), Summit Blue Consulting, LLC. This value is a weighted average of estimates provided by program participants.

Summer Peak Coincidence Factor has been preserved from the “Technical Reference Manual” (TRM) for Ohio Senate Bill 221 Energy Efficiency and Conservation Program and 09-512-GE-UNC,” October 15, 2009. This is likely a conservative estimate, but is recommended for further study (as stated in the OH State TRM, page 269).

“Measured Loading of Energy Efficient Motors - the Missing Link in Engineering Estimates of Savings,” ACEEE 1994 Summer Study Conference, Asilomar, CA.

Published estimates of typical pumping efficiency improvements range from 5 to 40%.  For analysis purposes, assume 15%.

United States Industrial Electric Motor Systems Market Opportunities Assessment December 2002, Table E-7, Page 18.

Measure costs are from the “2010-2012 WO017 Ex Ante Measure Cost Study”, Itron, California Public Utilities Commission, May 2014. The data is provided in a file named “MCS Results Matrix – Volume I”.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

National Solar Radiation Data Base -- 1991- 2005 Update: Typical Meteorological Year 3

National Solar Radiation Data Base -- 1991- 2005 Update: Typical Meteorological Year 3

Fe is estimated using TRM models for the three most popular building types for programmable thermostats: low-rise office (10.2%), sit-down restaurant (8.6%), and retail – strip mall (4.4%). 7.7% reflects the average Fe of the three building types. See “Fan Energy Factor Example Calculation 2021-06-23.xlsx” for reference.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Computers and peripheral equipment are considered 5-year property. 2016 IRS Publication  946. https://www.irs.gov/pub/irs-prior/p946--2016.pdf

Reduced estimate accounting for settings only lasting as long as units are in operation and the ease at which they can be turned off or adjusted in any one individual machine, due to personal preference.

Work Paper WPSCNROE0003 Revision 1, Power Management Software for Networked Computers. Southern California Edison.

Estimate assuming 15 minutes of labor at $40/hour rate.

Northwest Regional Technical Forum Non-Res Network Computer Power Management , January 29, 2015. Analysis can be found in NonResNetCompPwrMgt_v4_1.xlsm. https://rtf.nwcouncil.org/measure/non-res-network-computer-power-management

Northwest Regional Technical Forum Non-Res Network Computer Power Management , January 29, 2015. Analysis can be found in NonResNetCompPwrMgt_v4_1.xlsm. https://rtf.nwcouncil.org/measure/non-res-network-computer-power-management

Northwest Regional Technical Forum Non-Res Network Computer Power Management , January 29, 2015. Analysis can be found in NonResNetCompPwrMgt_v4_1.xlsm. https://rtf.nwcouncil.org/measure/non-res-network-computer-power-management

Based on Dimetrosky, S., Luedtke, J. S., & Seiden, K. (2005). Surveyor Network Energy Manager: Market Progress Evaluation Report, No. 2 (Northwest Energy Efficiency Alliance report #E05-136). Portland, OR: Quantec LLC and review of CLEARResult document providing Qualifying Software Providers for ComEd program and their licensing fees; “Qualifying Vendor Software Comparison.pdf”.

Zhang, Yanda, and Julianna Wei. Commerical Clothes Dryers, CASE Initiative for PY2013: Title 20 Standards Development. California Public Utilities Commission, 2013.

Engineering judgement, based on observed costs during Nicor Gas pilot study. "Nicor Gas Emerging Technology Program, 1036: Commercial Dryer Modulation Retrofit Public Project Report." 2014.

From DOE’s Federal Register Notices, Energy Conservation Program: Energy Conservation Standards for Commercial Clothes Dryers, Office of Energy Efficiency & Renewable Energy.

Ibid.

Average value for dryer cycles in healthcare facility, hotels, drycleaners and laundromats from tests conducted in Nicor Gas Emerging Technology Program’s Commercial Dryer Modulation Retrofit Public Project Report.

Based on Illinois weather data, and average dryer performance for laundromat (30 to 45lb) and hotel (75 to 170 lb) dryers. See GTI Analysis.xlsx for complete derivation.

From DOE’s Federal Register Notices, Energy Conservation Program: Energy Conservation Standards for Commercial Clothes Dryers, Office of Energy Efficiency & Renewable Energy.

Ibid.

Average value for dryer cycles in healthcare facility, hotels, drycleaners and laundromats from tests conducted in Nicor Gas Emerging Technology Program’s Commercial Dryer Modulation Retrofit Public Project Report.

“The Real Size of a Front Load Washer”, Laundromat123

“Assessment of Water Savings for Commercial Washers: Report on the Monitoring and Assessment of Water Savings from the Coin-Operated Multi-Load Clothes Washers Voucher Initiative Program.” San Diego County Water Authority October 2016.

One-third of expected measure life.

Measure costs are based on data from a quote provided by a commercial washer distributor to Franklin Energy Services.

“2014-2015 State of the Self-Service Laundry Industry Report.” Carlo Calma, April 13, 2015.

“Assessment of Water Savings for Commercial Washers: Report on the Monitoring and Assessment of Water Savings from the Coin-Operated Multi-Load Clothes Washers Voucher Initiative Program.” San Diego County Water Authority October 2016.

“Laundry Planning Guide.” EDRO, January 2015.

Based on professional judgement, assuming closed on holidays.

Clothes washer capacity is based on weight of dry clothing.

The EDRO “Laundry Planning Guide” describes moisture retention as “the ratio of retained moisture weight to clean dry textile weight.”  The pounds of water retained by clothing at the end of a wash cycle is calculated by multiplying Capacity (lbs of dry clothing per cycle) by RMC.

Using chart provided (Figure 1) and assuming a 50/50 cloth blend load of cotton and polyester, the retained moisture drops from approximately 65% to 50% when a 100 g washer is replaced with a 200 g washer. Chart from “Laundry Planning Guide.” EDRO, January 2015. The Department of Energy test procedures for commercial clothes washers specifies, “…the use of energy test cloth consisting of a pure finished bleach cloth, made with a momie or granite weave, which is a blended fabric of 50-percent cotton and 50-percent polyester.” – Energy Conservation Program: Energy Conservation Standards for Commercial Clothes Washers; Final Rule, Notice of Proposed Rulemaking, DOE, March 2014 (10 CFR Part 431).

“Laundry Planning Guide.” EDRO, January 2015.

ACEEE (2010), “Are We Missing Energy Savings in Clothes Dryers?” Paul Bendt (Ecos), 2010

“Dryer Field Study.” Northwest Energy Efficiency Alliance, November 20, 2014.

“Assessment of Water Savings for Commercial Washers: Report on the Monitoring and Assessment of Water Savings from the Coin-Operated Multi-Load Clothes Washers Voucher Initiative Program.” San Diego County Water Authority October 2016.

Codes and Standards Enhancement (CASE) Initiative For PY 2013: Title 20 Standards Development. Analysis of Standards Proposal for Computers, August 6, 2013. Section 2.3 Design Life, Page 15.

NEEA Research Into Action, 80 PLUS Market Progress Evaluation Report #5, November 26, 2013. Page 24.

ENERGY STAR Program Requirements for Computers - Eligibility Criteria v8.0, Section 3.5.2.v., Equation 1: TEC Calculation (ETEC) for Desktop, Integrated Desktop, and Notebook Computers, pg 12.

ENERGY STAR Program Requirements for Computers - Eligibility Criteria v8.0, Section 3.5.2.v., Table 4: Mode Weightings for Desktops and Integrated Desktop Computers, pg 13.

Codes and Standards Enhancement (CASE) Initiative For PY 2013: Title 20 Standards Development. Computers: Technical Report - Supplemental Analysis and Test Results, January 21, 2014.

Analysis of current DT I2 Category Desktops in the ENERGY STAR version 8.0 Qualified Products List (QPL) as accessed on 5/6/2020 (see File "ENERGY STAR_Computers_Analysis_2020.xlsx", Sheet "DT I2 Stats").

Analysis of current DT I2 Category Desktops in the ENERGY STAR version 8.0 Qualified Products List (QPL), passing with > 20% margin, as accessed on 5/6/2020 (see File "ENERGY STAR_Computers_Analysis_2020.xlsx", Sheet "DT I2 Stats").

80 PLUS program savings calculator, additional 7% reduction in idle power levels over ENERGY STAR version 7.0 computers with 80 PLUS Silver PSU levels. The program calculator was used to establish relative and comparable savings, and as a result, absolute idle power values do not match. For more details on the derivation of the 6.7% savings factor, please see, "80 PLUS Desktop Savings_25Aug2014_Revised ESv8.xlsx", 'Analysis Summary' tab.

80 PLUS program savings calculator, additional 9.1% reduction in idle power levels over ENERGY STAR version 7.0 computers with 80 PLUS Silver PSU levels. The program calculator was used to establish relative and comparable savings, and as a result, absolute idle power values do not match. For more details on the derivation of the 8.7% savings factor, please see, "80 PLUS Desktop Savings_25Aug2014_Revised ESv8.xlsx", 'Analysis Summary' tab.

It assumed that computers will not be off during peak period, and that the weighting of sleep, long idle and short idle during peak hours is consistent with the whole year. Wattage assumptions are weighted accordingly and coincidence factor is thus assumed to be 1.0 – see “ENERGY STAR Computers Analysis_2020_Revised.xlsx” for calculation.

This is a consistent assumption with 5.2.2 Advanced Power Strip – Tier 2.

Loadshapes were calculated from empirical studies and compared to the existing loadshape in Volume 1, Table 3.5. The studies were:

Acker, Brad et. al, “Office Space Plug Load Profiles and Energy Saving Interventions,” 2012 ACEEE Summer Study on Energy Efficiency in Buildings.

Sheppy, M. et al, “Reducing Plug Loads in Office Spaces” Hawaii and Guam Energy Improvement Technology Demonstration Project, NREL/NAVFAC (January 2014).

Savings algorithm reconstructed from weekday and weekend savings information in Acker, Brad et. al, “Office Space Plug Load Profiles and Energy Saving Interventions,” 2012 ACEEE Summer Study on Energy Efficiency in Buildings, and verified against savings in Acker et. al and savings in: BPA, “Smart Power Strip Energy Savings Evaluation: Ross Complex,” (2011). Office stations are assumed to have zero or minimal standy losses during normal operating hours. Method shown in “Commercial Tier 1 APS Calculations – IL TRM.xlsx”.

Based upon review of the PY2 and PY3 ComEd Direct Install Residential program surveys. This value could be modified based upon commercial application evaluation.

US Department of Energy, “Energy Conservation Program: Energy Conservation Standards for Distribution Transformers; Final Rule”, 10 CFR Part 431, Published April 18, 2013, Compliance effective as of January 1, 2016.

US DOE lists lifetime at 32 years. For consistency with efficiency measure evaluated lifetimes, 30 years is the recommended maximum deemed lifetime. US Department of Energy, “Energy Conservation Program: Energy Conservation Standards for Distribution Transformers; Final Rule”, 10 CFR Part 431, Published April 18, 2013, Effective as of January 1, 2016.

Energy Conservation Program: Test Procedures for Distribution Transformers; Final Rule. Effective May 30, 2006.

Guidelines on The Calculation and Use of Loss Factors, Electric Authority, Te Mana Hiko, February 14, 2013.

Unity power factor for used as default value, as used in the test procedures provided by US DOE. Energy Conservation Program: Test Procedures for Distribution Transformers; Final Rule. Effective May 30, 2006.

Suzanne Foster Porter et al., “Analysis of Standards Options for Battery Charger Systems”, (PG&E, 2010), 45.

Suzanne Foster Porter et al., “Analysis of Standards Options for Battery Charger Systems”, (PG&E, 2010), 42.

Emerging Technologies Program Application Assessment Report #0808, Industrial Battery Charger Energy Savings Opportunities, Pacific Gas & Electric. May 29, 2009.

Jacob V. Renquist, Brian Dickman, and Thomas H. Bradley, :”Economic Comparison of fuel cell powered forklifts to battery powered forklifts”, International Journal of Hydrogen Energy Volume 37, Issue 17, (2012): 2.

Ryan Matley, “Measuring Energy Efficiency Improvements in Industrial Battery Chargers”, (ESL-IE-09-05-32, Energy Technology Conference, New Orleans, LA, May 12-15, 2009), 4.

Number of charges is derived from the following reference and adjusted to the hours and days of the different types of shift operations. These values are based on an estimated 2-charge per 8-hour workday. See reference file Ryan Matley, “Measuring Energy Efficiency Improvements in Industrial Battery Chargers”, (ESL-IE-09-05-32, Energy Technology Conference, New Orleans, LA, May 12-15, 2009), 4.

Ryan Matley, “Measuring Energy Efficiency Improvements in Industrial Battery Chargers”, (ESL-IE-09-05-32, Energy Technology Conference, New Orleans, LA, May 12-15, 2009), 4 (average of SCR and Ferroresonant).

Ibid.

Ibid.

Ibid.

Ibid.

Ibid.

Voltage rating based on the assumption of 35kWh battery with a normalized average amp-hour capacity of 760 Ah charged over a 7.5 hour charge cycle. Pacific Gas & Electric, “Emerging Technologies Program Application Assessment Report #0808”, Industrial Battery Charger Energy Savings Opportunities. May 29, 2009. Page 8, Table 3.

Ampere rating based on the assumption of 35kWh battery with a normalized average amp-hour capacity of 760 Ah charged over a 7.5 hour charge cycle. Pacific Gas & Electric, “Emerging Technologies Program Application Assessment Report #0808”, Industrial Battery Charger Energy Savings Opportunities. May 29, 2009. Page 8, Table 3.

Emerging Technologies Program Application Assessment Report #0808, Industrial Battery Charger Energy Savings Opportunities, Pacific Gas & Electric. May 29, 2009.

Ibid.

Zhang, Yanda, and Julianna Wei. Commerical Clothes Dryers, CASE Initiative for PY2013: Title 20 Standards Development. California Public Utilities Commission, 2013.

Based on Gas Technology Institute’s analysis of cost data from “Nicor Gas Emerging Technology Program, 1069: Moisture Sensor Retrofit, Comprehensive Pilot Assessment Report,” May 1, 2017.

In the absence of loadshape information for commercial applications, this is estimated by adjusting the residential coincidence factor proportionately by the relative number of loads (264 for residential and as described in this measure for commercial applications).

From DOE’s Federal Register Notices - found here: http://energy.gov/eere/buildings/recent-federal-register-notices

Average value for dryer cycles in healthcare facility, hotels, drycleaners and laundromats from tests conducted in Nicor Gas Emerging Technology Program’s Commercial Dryer Modulation Retrofit Public Project Report.

Savings factor based on engineering analysis of savings data from “Nicor Gas Emerging Technology Program, 1069: Moisture Sensor Retrofit, Comprehensive Pilot Assessment Report,” May 1, 2017 and “Advanced Commercial Clothes Dryer Technologies Field Test,” prepared by Gas Technology Institute for the Minnesota Department of Commerce, January 15, 2018.

Estimate based on 45 minutes per cycle.

In the absence of loadshape information for commercial applications, this is estimated by adjusting the residential coincidence factor proportionately by the relative number of loads (264 for residential and as described in this measure for commercial applications).

Savings factor based on engineering analysis of savings data from “Nicor Gas Emerging Technology Program, 1069: Moisture Sensor Retrofit, Comprehensive Pilot Assessment Report,” May 1, 2017 and “Advanced Commercial Clothes Dryer Technologies Field Test,” prepared by Gas Technology Institute for the Minnesota Department of Commerce, January 15, 2018.

Presentation on the “Operating Cost Reduction Strategies for Oxidizers”, presented by Rich Grzanka, during the Chem Show Technology Exposition on October 31, 2007.

Ibid.

EPA Air Pollution Control Cost Manual, Chapter 2, November 2017. The system capital recovery cost is based on an estimated 20-year equipment life. This estimate of oxidizer equipment life is consistent with information available to EPA and is consistent with statements from large vendors for incinerators and oxidizers.

U.S. Environmental Protection Agency, Incinerators and Oxidizers, Chapter 2, November 2017.

ICAC Guidance Method for Estimation of Gas Consumption in a Regenerative Thermal Oxidizer (RTO), July 2002.

Ibid.

Biomass Energy Data Book, 2011, Appendix A: Lower and Higher Heating Values  of Gas, Liquid, and Solid Fuels.

Heat content of natural gas delivered to consumers per the Energy Information Administration, Independent Statistics & Analysis, 2018.

U.S. Environmental Protection Agency, Incinerators and Oxidizers, Chapter 2, November 2017.

Public Service Commission of Wisconsin, “Evaluation – Business Program: Measure Life Study,” Focus on Energy (2009): page 1-4, Table 1-2 Recommended Measure Life by WISeerts Group Description for Building Shell Equip or Tech measure type, accessed March 26, 2019,  https://focusonenergy.com/sites/default/files/bpmeasurelifestudyfinal_evaluationreport.pdf.

Leakage area is estimated based on average door size of installations previously completed in Wisconsin and reported in the Wisconsin Focus on Energy Technical Reference Manual. Average door size is 10 ft x 12 ft, with a side and top perimeter equal to 1 top * (10 ft * 12 in/1 ft) + 2 sides* (12 ft * 12 in/1ft) = 408 in. At 1/8 in perimeter gap, the leakage area is 408 in * 1/8 in = 51 in2.

2017 ASHRAE Handbook—Fundamentals, 16.24, Table 4 “Basic Model Stack Coefficient Cs”, assumed average building height of 16 feet, two-story.

2017 ASHRAE Handbook—Fundamentals, 16.24, Table 6 “Basic Model Wind Coefficient Cw”, assumed average building height of 16 feet and shelter class 3: “Typical shelter caused by other buildings across street from building under study.”

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL, for the average outdoor temperature when the heating system is expected to be operating.

Energy Center of Wisconsin, “Baseline Building Energy Models – Nonresidential Heating Thermostat Setpoint,” ComEd Portfolio Modeling Report (July 2010): page 6.

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL, for the average wind speed when the heating system is expected to be operating, defined as hours where the average temperature is lower than 55°F.

Engineering ToolBox, (2003). Air - Density, Specific Weight and Thermal Expansion Coefficient at Varying Temperature and Constant Pressures. [online] Available at: https://www.engineeringtoolbox.com/air-density-specific-weight-d_600.html [Accessed March 2019].

Engineering ToolBox, (2004). Air - Specific Heat at Constant Pressure and Varying Temperature. [online] Available at: https://www.engineeringtoolbox.com/air-specific-heat-capacity-d_705.html [Accessed March 2019].

To maintain consistency across assumptions within the IL TRM, this value is equal to the furnace efficiency value listed in the Roof Insulation for C&I Facilities measure in the 2019 IL TRM v.7.0 Vol. 2, Page 562.

ComEd Effective Useful Life Research Report (2018)

Recommendations for Verifying Savings for non-HVAC VFDs memorandum calculated an energy savings limit of 67% for process fans using the Toshiba Energy Savings Software for Motors and Drives (2009 version).

Lawrence Berkeley National Laboratory, and Resource Dynamics Corporation. (2008). “Improving Motor and Drive System Performance; A Sourcebook for Industry”. U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy. Golden, CO: National Renewable Energy Laboratory.

Douglass, J. (2005). Induction Motor Efficiency Standards. Washington State University and the Northwest Energy Efficiency Alliance, Extension Energy Program, Olympia, WA, October 2005.

ATD Home Inspection: http://www.atdhomeinspection.com/advice/average-product-life/ is 50 years. 25 years is used to be conservative.

Measure cost assumption from City of Fort Collins, "Green Building Practice Summary," March 21, 2011, page 2. The document states "Information from the EPA WaterSense web site: WaterSense® labeled toilets are not more expensive than regular toilets. MaP testing results have shown no correlation between price and performance. Prices for toilets can range from less than $100 to more than $1,000. Much of the variability in price is due to style, not functional design."

This factor includes 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s Review ‘IL TRM: Energy per Gallon Factor, May 2018’.

U. S. EPA WaterSense. “Water Efficiency Management Guide – Bathroom Suite” (EPA 832-F-17-016d), Nov 2017.

U.S. EPA WaterSense. “WaterSenses Specification for Flushing Urinals Supporting Statement”, Oct 2009.

U. S. EPA WaterSense. “Water Efficiency Management Guide – Bathroom Suite” (EPA 832-F-17-016d), Nov 2017.

U.S. EPA WaterSense. “WaterSenses Specification for Flushing Urinals Supporting Statement”, Oct 2009.

CASE Initiative for PY 2013: Analysis of Standards Proposal for Toilets and Urinals Water Efficiency. July 29, 2013. Pg 18.

Ibid.

U.S. EPA WaterSense. “WaterSenses Specification for Flushing Urinals Supporting Statement”, Oct 2009. Pg 1.

Assuming the work week is Monday through Friday.

Today’s Homeowner with Danny Lipford. “How to Calculate Lawn Irrigation Water Usage and Costs.”

Material pricing taken from Google shopping search on “smart irrigation control system”. The Rain Bird Smart LNK WiFi Irrigation System Indoor Controller (4 Pack) sells for $316 from online retailer Wish.com.. Installation labor pricing taken from online retailer Home Advisor – Lawn and Garden, Repair a Sprinkler System which stated $45 to $200 per hour for a plumber.

This factor include 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

Michael D. Dukes. “Smart Irrigation Controllers: What Makes an Irrigation Controller Smart”. University of Florida, Institute for Food & Agricultural Sciences.

State Climatologist Office for Illinois, Illinois State Water Survey, 2003. Based on 1971 – 2000 data, assessing the number of days between the last spring drop below 32 degrees and the firest fall drop below 32 degrees.

Based on data provided on Home Advisor website, Lawn and Garden, Repair a Sprinkler System.

Assumed lower than residential due to likely significantly higher door usage.

Deemed costs referenced from the Arkansas TRM.

Converts the Therm value to kWh and incorporates the relative COP efficiencies (assumed 0.78 for gas heat, 1 for electric resistance and 2.0 for heat pumps).

Savings are based on lab test results performed by CLEAResult, assuming a 1/8”gap. See ‘Commercial Weather Stripping IL_TRM_Workpaper v1.2’. The results for 1/8”gap are similar to the prescriptive Residential door sweep measure in 5.6.1 Air Sealing (assuming 3 ft doorsweep) and so deemed appropriate by the TAC.

Assumption is based on communication from AT&T program manager indicating an expectation that consolidated equipment should be expected to remain for a minimum of 10 years.

Value based on the average of program data provided by Franklin Energy. See “Network Combing Workpaper Research_v2.xls” for details. Note projects were capped at 40 pieces of equipment in the development of this average.

Value based on the average of program data provided by Franklin Energy. See “Network Combing Workpaper Research_v2.xls” for details. Note projects were capped at 40 pieces of equipment in the development of this average.

Cooling efficiency kW/ton default is based on air cooled units >240 Mbtuh, upflow ducted value as per the ASHRAE 90.1 2016 tables provided in the baseline section. This was the appropriate cooling efficiency value for all but one of Franklin Energy's projects.

California Municipal Utilities Association. Savings Estimation Technical Reference Manual 2017, Third Edition. Section 8.12, p. 8–15.

As estimated in the California Municipal Utilities Association. Savings Estimation Technical Reference Manual 2017, incremental measure cost based on average UPS costs for a range of sizes, assuming a 30% premium for an ENERGY STAR UPS.

10 CFR 430 Energy Conservation Standards for Uninterruptible Power Supplies  https://beta.regulations.gov/document/EERE-2016-BT-STD-0022-0007

ENERGY STAR Uninterruptible Power Supplies Final Version 2.0 Specification.

Calculation and inputs provided in ENERGY STAR Uninterruptible Power Supplies Final Version 2.0 Specification.

Default savings are provided in a calculation file provided by Franklin Energy that averages a number of power ratings within each range. See “ENERGY STAR UPS Calculations.xls” for more information.

Switching mode rectifier (SMR) technologies allows for efficiencies as high as 96% according to the Office of Energy Efficiency & Renewable Energy. Accessed: 12/05/19 https://www.energy.gov/eere/amo/high-efficiency-wide-band-three-phase-rectifiers-and-adaptive-rectifier-management

Mid-range efficiency for most low peak rectifiers (88%-92%) based on information from the Office of Energy Efficiency & Renewable Energy. Accessed: 12/05/19 https://www.energy.gov/eere/amo/high-efficiency-wide-band-three-phase-rectifiers-and-adaptive-rectifier-management

California Municipal Utilities Association. Savings Estimation Technical Reference Manual 2017, Third Edition. Section 8.12, p. 8–15.

Based on market study of twenty 1600 Volt Bridge Rectifiers. Accessed: 12/05/19. https://www.mouser.com/Semiconductors/Discrete-Semiconductors/Diodes-Rectifiers/Bridge-Rectifiers/_/N-ax1mf?P=1yzxhysZ1yzxpaz

Based on industry knowledge of large telecom company set up.

Small IT systems are assumed to have no air-side economizer and to operate continuously throughout the year.

Larger IT systems are assumed to have an air-side economizer that allows the cooling system to be turned off for half the year. This corresponds to approximately a 45°F changeover temperature, which is a conservative assumption.

Mid-range efficiency for most low peak rectifiers (88%-92%) based on information from the Office of Energy Efficiency & Renewable Energy.

Most electric motors are designed to run at 50% to 100% of rated load, from Department of Energy “Determining Electric Motor Load & Efficiency”, June 23, 2020.

Based on common size and type of motor - chart on pages 13-14, “Attachment C” of reference 9, the efficiency of a 50HP motor (TEFC type) at 1200 RPM is 92%. Or 75HP at 900 RPM at 75% TEFC type is 91.8%. These are common sizes and type for manufacturers.

Estimate based on review of a number of studies provided by ExxonMobil and saved in reference folders.

Most electric motors are designed to run at 50% to 100% of rated load, from Department of Energy “Determining Electric Motor Load & Efficiency”, June 23, 2020.

Based on common size and type of motor - chart on pages 13-14, “Attachment C” of reference 9, the efficiency of a 50HP motor (TEFC type) at 1200 RPM is 92%. Or 75HP at 900 RPM at 75% TEFC type is 91.8%. These are common sizes and type for manufacturers.

Estimate based on review of a number of studies provided by ExxonMobil and saved in reference folders.

See Page 6 of New Buildings Institute, “Plug Load Savings Assessment: Part of the Evidence-based Design and Operations PIER Program,” California Energy Commission, Evidence-based Design and Operations PIER Program, March 2013.

From Ross Wiffler, “A Dedicated Power Supply is Critical for Your Office Copier”, Copiers & More, Small Business, Aug. 18th, 2015. https://commonsensebusinesssolutions.com/a-dedicated-power-supply-is-critical-for-your-office-copier/

This is an assumption consistent with 4.8.7 Advanced Power Strip – Tier 1 Commercial.

Based on cost from vendor of typical smart socket on the market, Simply Conserve Smart Socket by AM Conservation Group. 10 amp smart socket: $8.92/each; 15 amp smart socket: $9.00/each.

As referenced in 4.8.7 Advanced Power Strip – Tier 1 Commercial, Loadshapes were calculated from empirical studies and compared to the existing loadshape in Volume 1, Table 3.5. The studies were:

Acker, Brad et. al, “Office Space Plug Load Profiles and Energy Saving Interventions,” 2012 ACEEE Summer Study on Energy Efficiency in Buildings.

Sheppy, M. et al, “Reducing Plug Loads in Office Spaces” Hawaii and Guam Energy Improvement Technology Demonstration Project, NREL/NAVFAC (January 2014).

Savings algorithm reconstructed from weekday and weekend savings information in Acker, Brad et. al, “Office Space Plug Load Profiles and Energy Saving Interventions,” 2012 ACEEE Summer Study on Energy Efficiency in Buildings, and verified against savings in Acker et. al and savings in: BPA, “Smart Power Strip Energy Savings Evaluation: Ross Complex,” (2011). Office stations are assumed to have zero or minimal standy losses during normal operating hours. Method shown in “Commercial Tier 1 APS Calculations – IL TRM.xlsx”.

Average connected wattage found in Guidehouse, ‘ComEd Small Business Kits CY2020 Impact Evaluation Report 2021-04-01 Final.pdf’.

See Standby Power Summary Table contained in “Standby Power”, Lawrence Berkeley National Laboratory, Building Technology and Urban Systems Division, https://standby.lbl.gov/data/summary-table/

From “iTECH evaluation on the SmartSocket,” ITECH Electronic Co., LTD, 1/28/19. IoT – Related Technical Articles. https://www.itechate.com/uploadfiles/2019/01/201901281143214321.pdf.

See Standby Power Summary Table contained in “Standby Power”, Lawrence Berkeley National Laboratory, Building Technology and Urban Systems Division, https://standby.lbl.gov/data/summary-table/

In the absence of empirical data, a 50% adjustment for appliances assumed to be on during out of hours is applied.

Average smart socket wattage found in Guidehouse, ‘ComEd Small Business Kits CY2020 Impact Evaluation Report 2021-04-01 Final.pdf’.

Unknown hours are based on a Guidehouse review of open hours for 487 participants in this measure.

Based upon review of the PY2 and PY3 ComEd Direct Install Residential program surveys. This value could be modified based upon commercial application evaluation.

This ISR is based on the results of surveys of ComEd Small Business Kit recipients conducted in the Spring of 2021. This result includes the reduction in the installation rate from the survey respondents that indicated they did not install the application which is necessary to use the smart socket as intended.

This ISR is based on the results of the surveys of ComEd Small Business Kit recipients conducted in the Spring of 2021. It is based on an estimate of what the ISR would be if the kit only included a single socket even though all the kits distributed by ComEd included two sockets. Similar to the ISR for the two socket kits, this ISR accounts for the reduction in the installation rate from the survey respondents that indicated they did not install the application which is necessary to use the smart socket as intended.

Lifetime of measure assumed to be limited by the lifetime of the lithium ion charger. See reference file Suzanne Foster Porter et al., “Analysis of Standards Options for Battery Charger Systems”, (PG&E, 2010), 45.

Thomas, Pete. “Is a Lithium Ion Forklift Battery Worth the Extra Expense?” Toyota Material Handling Northern California. Accessed May 5, 2021. https://www.tmhnc.com/blog/lithium-ion-forklift-battery-cost-and-runtime.

Matley, Ryan. May 29, 2009. “Industrial Battery Charger Energy Savings Opportunities.” Emerging Technologies Program Application Assessment Report #0808. Pacific Gas & Electric.

Renquist, Jacob V., Brian Dickman, and Thomas H. Bradley. June 19, 2012. “Economic comparison of fuel cell powered forklifts to battery powered forklifts.” International Journal of Hydrogen Energy, Volume 37, Issue 17.

Matley, Ryan. May 2009. “Measuring Energy Efficiency Improvements in Industrial Battery Chargers.” Energy Systems Laboratory.

Abdulhameed, Alshaebi, Husam Dauod, and Sang Won Yoon. May 2017. “Evaluation of Different Forklift Battery Systems Using Statistical Analysis and Discrete Event Simulation.” Industrial and Systems Engineering Conference. Pittsburg, PA.

Abdulhameed, Alshaebi, Husam Dauod, and Sang Won Yoon. May 2017. “Evaluation of Different Forklift Battery Systems Using Statistical Analysis and Discrete Event Simulation.” Industrial and Systems Engineering Conference. Pittsburg, PA.

Mongird, Kendall, Viswanathan, Vilayanur V., Balducci, Patrick J., Alam, Md Jan E., Fotedar, Vanshika, Koritarov, V S., and Hadjerioua, Boualem. July 2019. "Energy Storage Technology and Cost Characterization Report". U.S. Department of Energy – HydroWires. https://doi.org/10.2172/1573487.

Abdulhameed, Alshaebi, Husam Dauod, and Sang Won Yoon. May 2017. “Evaluation of Different Forklift Battery Systems Using Statistical Analysis and Discrete Event Simulation.” Industrial and Systems Engineering Conference. Pittsburg, PA.

Future evaluation research could explore savings differences between Level I and Level II participants.

Total incremental measure costs from the evaluation, net of O&M adjustments (if applicable), divided by the number of BOC participants.

Opinion Dynamics, ‘Ameren Illinois Company 2020 Business Program Impact Evaluation Report, Final’, April 28th 2021.

Opinion Dynamics, ‘Ameren Illinois Company 2019 Business Program Impact Evaluation Report, Final’, April 30th 2020.

The ComEd evaluation includes both 2018 and 2019 participants. The interview sample did not stratify by program year, so the savings per participant are the same for each year. Guidehouse, ‘ComEd Building Operator Certification Pilot Impact Evaluation Report’, April 12th, 2021.

The weighted average numbers are used to determine the savings parameters within this measure. The savings parameters are set so the average savings using the TRM algorithm, including the building area cap, equals the weighted average savings from the referenced evaluation studies.

Average measure life of capital measures from the ComEd CY2020 evaluation.

Weighted average from referenced evaluation studies which outlined lifetime information.

EUL for operational updates when the controls type is unknown. See Attachment B:Effective Useful Life for Custom Measure. Effective Useful Life for Retro-commissioning and Behavior Programs memo by Guidehouse, September 17, 2019.

The current price to take the BOC training and certification in Illinois. https://www.boccentral.org/training/illinois. Accessed May 2021.

Based on evaluated measure incremental costs, net of O&M adjustments when available, from Ameren Illinois and ComEd BOC programs in Illinois.

Average net savings per participant from the evaluations referenced. See table of evaluations in the Definition of Efficient Equipment section of this measure.

Average net demand savings per participant from the evaluations referenced. See table of evaluations in the Definition of Efficient Equipment section of this measure.

Average net natural gas savings per participant from the evaluations referenced. See table of evaluations in the Definition of Efficient Equipment section of this measure.

West, R.C., M.C. Rodezno, G. Julian, B.D. Prowell, B. Frank, L.V. Osborn, & A.J. Kriech (2014). “NCHRP Report 779:Field Performance of Warm-Mix Asphalt Technologies. Transportation Research Board of the National Academies”, Washington, D.C. doi:10.17226/22272.

West, R.C., M.C. Rodezno, G. Julian, B.D. Prowell, B. Frank, L.V. Osborn, & A.J. Kriech (2014). “NCHRP Report 779:Field Performance of Warm-Mix Asphalt Technologies. Transportation Research Board of the National Academies”, Washington, D.C. doi:10.17226/22272.

West, R.C., M.C. Rodezno, G. Julian, B.D. Prowell, B. Frank, L.V. Osborn, & A.J. Kriech (2014). “NCHRP Report 779:Field Performance of Warm-Mix Asphalt Technologies. Transportation Research Board of the National Academies”, Washington, D.C. doi:10.17226/22272.

West, R.C., M.C. Rodezno, G. Julian, B.D. Prowell, B. Frank, L.V. Osborn, & A.J. Kriech (2014). “NCHRP Report 779:Field Performance of Warm-Mix Asphalt Technologies. Transportation Research Board of the National Academies”, Washington, D.C. doi:10.17226/22272.

West, R.C., M.C. Rodezno, G. Julian, B.D. Prowell, B. Frank, L.V. Osborn, & A.J. Kriech (2014). “NCHRP Report 779:Field Performance of Warm-Mix Asphalt Technologies. Transportation Research Board of the National Academies”, Washington, D.C. doi:10.17226/22272.

Based on studies conducted by two separate parties; Comparative Environmental Life Cycle Assessment of Hand Drying Systems by Quantis (pg 2) and Guidelines to Reduce/Eliminate Paper Towel Use by Installing Electric Hand Dryers by Partners in Pollution Prevention P3 (pg 17).

Cost is the average retail costs for 16 baseline and 10 efficient hand dryers.  See Hand_Dryer_Analysis.xlsx . Cost source: RestroomDirect.com

Industry Standard.  Medium/Moderate Uses per day is supported by both Excel Dryer Data (Cost Savings with Hand Dryers vs Average Cost of Paper Towels https://www.exceldryer.com/calculator-dial/) and World Dryer Data (http://staging.worlddryer.com/savings-calculator)

Illinois TRM v9.0, Days per year, from 4.3.2 Low Flow Faucet Aerators

CLEAResult survey of 24 hand dryers in convenience stores in Arkansas.  See Hand_Dryer_Analysis.xlsx.

CLEAResult cost/specification survey of 10 unique efficient hand dryers.  See Hand_Dryer_Analysis.xlsx.