# Business Energy Efficiency Rebates Program Impact Evaluation Report

Energy Efficiency Plan: Program Year 2025

(01/01/2025-12/31/2025)

Prepared for:

Nicor Gas Company

DRAFT

April 3, 2026

Prepared by:

| Sophie Berne Guidehouse, Inc. | Sagar Phalke Guidehouse, Inc. | Raniel Chan Guidehouse, Inc. |  |
| --- | --- | --- | --- |

Submitted to:

Nicor Gas Company

1844 Ferry Road

Naperville, IL 60563

Submitted by:

Guidehouse Inc.

167 N. Green Street

12th Floor

Chicago, IL 60607

Contact:

| Charles Maglione, Partner 202.481.7352 cmaglione@guidehouse.com | Jeff Erickson, Director 608.616.4962 jeff.erickson@guidehouse.com | Laura Agapay-Read, Associate Director 312.583.4178 laura.agapay.read@guidehouse.com |
| --- | --- | --- |

Charles Ampong, Associate Director

608.616.4922

charles.ampong@guidehouse.com

This report was prepared by Guidehouse for Nicor Gas Company. The work presented in this report represents Guidehouse’s professional judgment based on the information available at the time this report was prepared. Use of this report by any other party for whatever purpose should not, and does not, absolve such party from using due diligence in verifying the report’s contents. Neither Guidehouse nor any of its subsidiaries or affiliates assumes any liability or duty of care to such parties and hereby disclaims any such liability.

Table of Contents

1	Introduction	1

2	Program Description	1

3	Program Savings Detail	3

4	Program Savings by Measure	4

5	Impact Analysis Findings and Recommendations	9

5.1	Impact Parameter Estimates	9

5.2	Findings and Recommendations	10

Appendix A. Impact Analysis Methodology	15

Building Operator Certification	15

All Other Measures	15

Appendix B. Program Specific Inputs for the Illinois TRC	17

Table of Tables, Figures, and Equations

Table 2-1. 2025 Volumetric Findings Detail	1

Table 2-2. 2025 Installed Measure Quantities	2

Table 3-1. 2025 Annual Energy Savings Summary	4

Table 4-1. 2025 Annual Energy Savings by Measure	5

Table 5-1. Verified Gross Savings Parameters	9

Table A-1. BOC Savings Coefficients	15

Equation 1. Annual Natural Gas Energy Savings per Participant	15

# Introduction

This report presents the results of the impact evaluation of the Nicor Gas 2025 Business Energy Efficiency Rebates (BEER) program. It presents a summary of the energy impacts for the total program and broken out by relevant measure and program structure details. The appendices present the impact analysis methodology and inputs to the TRC calculations.  Program year 2025 covers January 1 to December 31, 2025.

# Program Description

The BEER program provides incentives to business (private) and public sector customers that install new, high efficiency space heating, water heating, pipe insulation, commercial kitchen, and weatherstripping equipment covered by the program. The program consists of four delivery paths:

Rebates for prescriptive cost-effective equipment as well as services (such as boiler tune-ups) to improve the energy efficiency of existing equipment.

Free assessments and direct install measures, such as efficient faucet aerators, low-flow showerheads, and pre-rinse sprayers.

Business optimization measures including steam traps and tune-ups.

Midstream commercial food service (CFS) equipment incentives offering using midstream delivery channels. This path’s goals are to reduce barriers for food service operators to purchasing energy efficient equipment and to reduce energy usage in the commercial food service sector.

Also included in this report is the Building Operator Certification (BOC) training and certification program. This program teaches participants how to improve building comfort and efficiency by optimizing a building’s systems. This has been offered for several years by the Midwest Energy Efficiency Alliance, at full tuition reimbursement for ComEd, Ameren Illinois, and natural gas customers who complete the curriculum.

The program had 494 participants in 2025 and completed 442 projects as shown in the following table.

Table 2-1. 2025 Volumetric Findings Detail

| Participation | Building Operator Certification (BOC) | Business Optimization Program (BOP) | Direct Install (DI) | Midstream CFS | Prescriptive (Px) | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Private Sector |  |  |  |  |  |  |
| Participants * | 8 | 98 | 50 | 44 | 115 | 315 |
| Installed Projects † | 8 | 91 | 50 | 41 | 104 | 292 |
| Measure Types Installed ‡ | 1 | 4 | 4 | 7 | 20 | 29 |
| Public Sector |  |  |  |  |  |  |
| Participants * | 16 | 1 | 62 | 9 | 91 | 179 |
| Installed Projects † | 16 | 1 | 59 | 7 | 75 | 150 |
| Measure Types Installed ‡ | 1 | 1 | 6 | 5 | 10 | 21 |
| Program 2025 Total |  |  |  |  |  |  |
| Participants * | 24 | 99 | 112 | 53 | 206 | 494 |
| Installed Projects † | 24 | 92 | 109 | 48 | 179 | 442 |
| Measure Types Installed ‡ | 1 | 4 | 6 | 9 | 21 | 33 |

* Participants are defined as the distinct count of addresses or applicants for the Building Operator Certification path. The row total is a distinct count for the given sector or program total.

† Installed Projects are defined as the distinct count of project ID. The row total is a distinct count for the given sector or program total.

‡ Measure Types Installed are the distinct count of reporting measure names. The row total is a distinct count for the given sector or program total.

Source: Nicor Gas tracking data and evaluation team analysis.

Table 2 summarizes the installed measure quantities that are the basis for verified energy savings.

Table 2-2. 2025 Installed Measure Quantities

| Program Category | Program Path | Measure | Quantity Unit | Installed Quantity |
| --- | --- | --- | --- | --- |
| Private | BOC | BOC | Participant | 8 |
| Private | BOP | Boiler Tune Up, Process | Unit | 21 |
| Private | BOP | Steam Trap, Dry Cleaner | Unit | 719 |
| Private | BOP | Steam Trap, Industrial High Pressure | Unit | 163 |
| Private | BOP | Steam Trap, Industrial Medium Pressure | Unit | 142 |
| Private | DI | Faucet Aerator - Bath | Unit | 306 |
| Private | DI | Garage Door Hinge | Unit | 114 |
| Private | DI | Pre-Rinse Spray Valves | Unit | 29 |
| Private | DI | Showerheads | Unit | 208 |
| Private | CFS | Automatic Conveyor Broiler | Unit | 1 |
| Private | CFS | Combination Oven | Unit | 19 |
| Private | CFS | Convection Oven | Unit | 2 |
| Private | CFS | Dishwasher | Unit | 1 |
| Private | CFS | Fryer | Unit | 40 |
| Private | CFS | Griddle | Unit | 5 |
| Private | CFS | Kitchen Demand Ventilation Controls | Unit | 16 |
| Private | Px | Boiler Tune Up, Process | Unit | 3 |
| Private | Px | Boiler Tune Up, Space Heating | Unit | 20 |
| Private | Px | Combination Oven | Unit | 2 |
| Private | Px | Commercial Pool Covers | Unit | 1 |
| Private | Px | Compressed Air Heat Recovery | Unit | 7 |
| Private | Px | Convection Oven | Unit | 2 |
| Private | Px | Fryer | Unit | 28 |
| Private | Px | Grain Dryer Tune-Up | Unit | 30 |
| Private | Px | High Efficiency Boiler | Unit | 6 |
| Private | Px | High Efficiency Furnace | Unit | 21 |
| Private | Px | Infrared Heaters | Unit | 26 |
| Private | Px | Pipe Insulation | Ln Ft | 4 |
| Private | Px | Rack Oven - Double Oven | Unit | 3 |
| Private | Px | Small Commercial Thermostat | Unit | 2 |
| Private | Px | Steam Trap, Commercial | Unit | 99 |
| Private | Px | Steam Trap, Dry Cleaner | Unit | 35 |
| Private | Px | Steam Trap, Industrial High Pressure | Unit | 41 |
| Private | Px | Steam Trap, Industrial Medium Pressure | Unit | 54 |
| Private | Px | Storage Water Heater | Unit | 4 |
| Private | Px | Tankless Water Heater | Unit | 40 |
| Public | BOC | BOC | Participant | 16 |
| Public | BOP | Steam Trap, Industrial Medium Pressure | Unit | 21 |
| Public | DI | DHW HW Pipe Insulation | Ln Ft | 26 |
| Public | DI | Faucet Aerator - Bath | Unit | 1,377 |
| Public | DI | Garage Door Hinge | Unit | 165 |
| Public | DI | Pre-Rinse Spray Valves | Unit | 13 |
| Public | DI | Showerheads | Unit | 65 |
| Public | DI | Weather Stripping | Ln Ft | 144 |
| Public | CFS | Combination Oven | Unit | 4 |
| Public | CFS | Commercial Steam Cooker | Unit | 1 |
| Public | CFS | Convection Oven | Unit | 1 |
| Public | CFS | Dishwasher | Unit | 3 |
| Public | CFS | Pre-Rinse Spray Valves | Unit | 1 |
| Public | Px | Boiler Chemical Descaling | Unit | 1 |
| Public | Px | Boiler Tune Up, Process | Unit | 5 |
| Public | Px | Boiler Tune Up, Space Heating | Unit | 109 |
| Public | Px | High Efficiency Boiler | Unit | 32 |
| Public | Px | High Efficiency Furnace | Unit | 6 |
| Public | Px | Small Commercial Thermostat | Unit | 3 |
| Public | Px | Steam Trap, Commercial | Unit | 22 |
| Public | Px | Steam Trap, Industrial High Pressure | Unit | 12 |
| Public | Px | Steam Trap, Industrial Medium Pressure | Unit | 32 |
| Public | Px | Tankless Water Heater | Unit | 4 |

Source: Nicor Gas tracking data and evaluation team analysis.

# Program Savings Detail

Table 3 summarizes the energy savings the BEER Program achieved by path in 2025. In several tables in this report, measures are separated into those that were installed in disadvantaged communities (DAC) or a non-DAC community. Participants in DAC are identified based on their census tract or zipcode. Based on SAG Policy, business participants in a DAC with consumption under 35,000 Therms are assigned a NTG of 1.00.

Table 3-1. 2025 Annual Energy Savings Summary

| Program Category | Program Path | Ex Ante Gross Savings (Therms) | Verified Gross RR* | Verified Gross Savings (Therms) | NTG† | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- | --- |
| Private, Non-DAC | BOC | 11,993 | 76% | 9,138 | N/A | 9,138 |
|  | BOP | 1,583,073 | 100% | 1,582,150 | 0.92 | 1,455,578 |
|  | DI | 15,730 | 96% | 15,111 | 0.86 | 12,995 |
|  | CFS | 43,715 | 170% | 74,404 | 0.80 | 59,524 |
|  | Px | 1,195,912 | 111% | 1,324,547 | Varies | 1,139,142 |
| Private, Non-DAC Subtotal |  | 2,850,423 | 105% | 3,005,350 |  | 2,676,377 |
| Private, DAC | BOP | 147,840 | 101% | 149,575 | 1.00 | 149,575 |
|  | DI | 658 | 95% | 624 | 1.00 | 624 |
|  | Px | 131,164 | 101% | 132,034 | 1.00 | 132,034 |
| Private, DAC Subtotal |  | 279,662 | 101% | 282,233 | 1.00 | 282,233 |
| Private Subtotal |  | 3,130,085 | 105% | 3,287,583 |  | 2,958,610 |
| Public, Non-DAC | BOC | 14,076 | 100% | 14,143 | N/A | 14,143 |
|  | BOP | 8,102 | 104% | 8,420 | 0.92 | 7,747 |
|  | DI | 18,684 | 98% | 18,403 | 0.86 | 15,826 |
|  | CFS | 7,483 | 95% | 7,073 | 0.80 | 5,659 |
|  | Px | 245,901 | 98% | 240,554 | Varies | 206,925 |
| Public, Non-DAC Subtotal |  | 294,247 | 98% | 288,593 |  | 250,300 |
| Public, DAC | DI | 6,686 | 95% | 6,377 | 1.00 | 6,377 |
|  | Px | 97,274 | 99% | 96,646 | 1.00 | 96,646 |
| Public, DAC Subtotal |  | 103,960 | 99% | 103,024 | 1.00 | 103,024 |
| Public Subtotal |  | 398,207 | 98% | 391,617 |  | 353,323 |
| Total |  | 3,528,292 | 104% | 3,679,200 |  | 3,311,934 |

* Realization Rate (RR) is the ratio of verified gross savings to ex ante gross savings, based on evaluation research findings.

† NTG, Net to Gross is the deemed value available on the SAG website: https://www.ilsag.info/evaluator-ntg-recommendations-for-2025. Disadvantaged communities (DAC) designated sites based on zip codes have an NTG of 1.00.

N/A: All savings estimating algorithms presented in the IL TRM v13.0 for the Building Operator Certification measure are for net savings. Therefore, this measure does not require additional application of NTG value.

Source: Evaluation team analysis.

# Program Savings by Measure

The program includes 33 measures as shown in the following table. The Steam Trap, Industrial High Pressure and Grain Dryer Tune-Up measures contributed the most savings.

Table 4-1. 2025 Annual Energy Savings by Measure

| Program Category | Program Path | Savings Category | Ex Ante Gross Savings (Therms) | Verified Gross RR* | Verified Gross Savings (Therms) | NTG† | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Private, Non-DAC | BOC | BOC | 11,993 | 76% | 9,138 | N/A | 9,138 |
| Private, Non-DAC | BOP | Boiler Tune Up, Process | 102,146 | 100% | 102,146 | 0.92 | 93,974 |
| Private, Non-DAC | BOP | Steam Trap, Dry Cleaner | 511,456 | 101% | 516,916 | 0.92 | 475,563 |
| Private, Non-DAC | BOP | Steam Trap, Industrial High Pressure | 821,059 | 99% | 810,379 | 0.92 | 745,549 |
| Private, Non-DAC | BOP | Steam Trap, Industrial Medium Pressure | 148,413 | 103% | 152,709 | 0.92 | 140,492 |
| Private, Non-DAC | DI | Faucet Aerator - Bath | 2,501 | 100% | 2,501 | 0.86 | 2,150 |
| Private, Non-DAC | DI | Garage Door Hinge | 5,301 | 88% | 4,682 | 0.86 | 4,026 |
| Private, Non-DAC | DI | Pre-Rinse Spray Valves | 5,698 | 100% | 5,698 | 0.86 | 4,900 |
| Private, Non-DAC | DI | Showerheads | 2,231 | 100% | 2,231 | 0.86 | 1,918 |
| Private, Non-DAC | CFS | Automatic Conveyor Broiler | 863 | 345% | 2,976 | 0.80 | 2,381 |
| Private, Non-DAC | CFS | Combination Oven | 11,238 | 95% | 10,728 | 0.80 | 8,583 |
| Private, Non-DAC | CFS | Convection Oven | 853 | 50% | 427 | 0.80 | 341 |
| Private, Non-DAC | CFS | Dishwasher | 92.38 | 100% | 92.32 | 0.80 | 73.85 |
| Private, Non-DAC | CFS | Fryer | 24,417 | 105% | 25,607 | 0.80 | 20,485 |
| Private, Non-DAC | CFS | Griddle | 1,844 | 1636% | 30,167 | 0.80 | 24,134 |
| Private, Non-DAC | CFS | Kitchen Demand Ventilation Controls | 4,407 | 100% | 4,407 | 0.80 | 3,526 |
| Private, Non-DAC | Px | Boiler Tune Up, Process | 28,052 | 100% | 28,052 | 0.86 | 24,125 |
| Private, Non-DAC | Px | Boiler Tune Up, Space Heating | 19,216 | 100% | 19,216 | 0.86 | 16,525 |
| Private, Non-DAC | Px | Combination Oven | 1,009 | 117% | 1,180 | 0.86 | 1,015 |
| Private, Non-DAC | Px | Commercial Pool Covers | 1,251 | 100% | 1,251 | 0.86 | 1,076 |
| Private, Non-DAC | Px | Compressed Air Heat Recovery | 80,631 | 100% | 80,631 | 0.86 | 69,342 |
| Private, Non-DAC | Px | Convection Oven | 425 | 96% | 409 | 0.86 | 352 |
| Private, Non-DAC | Px | Fryer | 14,622 | 109% | 15,878 | 0.86 | 13,655 |
| Private, Non-DAC | Px | Grain Dryer Tune-Up | 511,617 | 123% | 626,926 | 0.86 | 539,156 |
| Private, Non-DAC | Px | High Efficiency Boiler | 12,176 | 100% | 12,176 | 0.86 | 10,472 |
| Private, Non-DAC | Px | High Efficiency Furnace | 4,848 | 100% | 4,848 | 0.86 | 4,170 |
| Private, Non-DAC | Px | Infrared Heaters | 4,082 | 100% | 4,082 | 0.86 | 3,510 |
| Private, Non-DAC | Px | Pipe Insulation | 185,224 | 100% | 185,224 | 0.86 | 159,293 |
| Private, Non-DAC | Px | Rack Oven - Double Oven | 1,654 | 356% | 5,892 | 0.86 | 5,067 |
| Private, Non-DAC | Px | Small Commercial Thermostat | 371 | 145% | 538 | 0.92 | 495 |
| Private, Non-DAC | Px | Steam Trap, Commercial | 25,750 | 106% | 27,256 | 0.86 | 23,440 |
| Private, Non-DAC | Px | Steam Trap, Dry Cleaner | 7,259 | 101% | 7,337 | 0.86 | 6,310 |
| Private, Non-DAC | Px | Steam Trap, Industrial High Pressure | 196,368 | 101% | 197,964 | 0.86 | 170,249 |
| Private, Non-DAC | Px | Steam Trap, Industrial Medium Pressure | 100,707 | 102% | 102,556 | 0.86 | 88,198 |
| Private, Non-DAC | Px | Storage Water Heater | 508 | 367% | 1,861 | 0.86 | 1,601 |
| Private, Non-DAC | Px | Tankless Water Heater | 141 | 897% | 1,268 | 0.86 | 1,091 |
| Private, Non-DAC Subtotal |  |  | 2,850,423 | 105% | 3,005,350 |  | 2,676,377 |
| Private, DAC | BOP | Steam Trap, Dry Cleaner | 102,020 | 101% | 103,109 | 1.00 | 103,109 |
| Private, DAC | BOP | Steam Trap, Industrial High Pressure | 35,987 | 101% | 36,311 | 1.00 | 36,311 |
| Private, DAC | BOP | Steam Trap, Industrial Medium Pressure | 9,833 | 103% | 10,155 | 1.00 | 10,155 |
| Private, DAC | DI | Faucet Aerator - Bath | 34.30 | 100% | 34.30 | 1.00 | 34 |
| Private, DAC | DI | Garage Door Hinge | 624 | 94% | 589 | 1.00 | 589 |
| Private, DAC | Px | Boiler Tune Up, Process | 2,183 | 100% | 2,183 | 1.00 | 2,183 |
| Private, DAC | Px | Fryer | 2,235 | 108% | 2,406 | 1.00 | 2,406 |
| Private, DAC | Px | Grain Dryer Tune-Up | 77,077 | 100% | 77,077 | 1.00 | 77,077 |
| Private, DAC | Px | High Efficiency Boiler | 6,678 | 100% | 6,678 | 1.00 | 6,678 |
| Private, DAC | Px | High Efficiency Furnace | 1,814 | 100% | 1,814 | 1.00 | 1,814 |
| Private, DAC | Px | Infrared Heaters | 5,846 | 100% | 5,846 | 1.00 | 5,846 |
| Private, DAC | Px | Steam Trap, Dry Cleaner | 15,839 | 101% | 16,008 | 1.00 | 16,008 |
| Private, DAC | Px | Steam Trap, Industrial High Pressure | 16,522 | 101% | 16,671 | 1.00 | 16,671 |
| Private, DAC | Px | Steam Trap, Industrial Medium Pressure | 2,888 | 102% | 2,938 | 1.00 | 2,938 |
| Private, DAC | Px | Tankless Water Heater | 81.34 | 508% | 413 | 1.00 | 413 |
| Private, DAC Subtotal |  |  | 279,662 | 101% | 282,233 |  | 282,233 |
| Private Subtotal |  |  | 3,130,085 | 105% | 3,287,583 |  | 2,958,610 |
| Public, Non-DAC | BOC | BOC | 14,076 | 100% | 14,143 |  | 14,143 |
| Public, Non-DAC | BOP | Steam Trap, Industrial Medium Pressure | 8,102 | 104% | 8,420 | 0.92 | 7,747 |
| Public, Non-DAC | DI | Faucet Aerator - Bath | 10,034 | 100% | 10,034 | 0.86 | 8,629 |
| Public, Non-DAC | DI | Garage Door Hinge | 3,897 | 93% | 3,616 | 0.86 | 3,110 |
| Public, Non-DAC | DI | Pre-Rinse Spray Valves | 3,086 | 100% | 3,086 | 0.86 | 2,654 |
| Public, Non-DAC | DI | Showerheads | 418 | 100% | 418 | 0.86 | 360 |
| Public, Non-DAC | DI | Weather Stripping | 1,249 | 100% | 1,249 | 0.86 | 1,074 |
| Public, Non-DAC | CFS | Combination Oven | 2,255 | 91% | 2,044 | 0.80 | 1,635 |
| Public, Non-DAC | CFS | Commercial Steam Cooker | 3,533 | 100% | 3,530 | 0.80 | 2,824 |
| Public, Non-DAC | CFS | Convection Oven | 391 | 50% | 195 | 0.80 | 156 |
| Public, Non-DAC | CFS | Dishwasher | 1,159 | 100% | 1,159 | 0.80 | 927 |
| Public, Non-DAC | CFS | Pre-Rinse Spray Valves | 145 | 100% | 145 | 0.80 | 116 |
| Public, Non-DAC | Px | Boiler Chemical Descaling | 708 | 100% | 708 | 0.86 | 609 |
| Public, Non-DAC | Px | Boiler Tune Up, Process | 4,830 | 100% | 4,830 | 0.86 | 4,154 |
| Public, Non-DAC | Px | Boiler Tune Up, Space Heating | 96,497 | 100% | 96,497 | 0.86 | 82,987 |
| Public, Non-DAC | Px | High Efficiency Boiler | 129,950 | 95% | 123,929 | 0.86 | 106,579 |
| Public, Non-DAC | Px | High Efficiency Furnace | 2,716 | 100% | 2,716 | 0.86 | 2,336 |
| Public, Non-DAC | Px | Small Commercial Thermostat | 806 | 100% | 809 | 0.92 | 744 |
| Public, Non-DAC | Px | Steam Trap, Commercial | 4,381 | 106% | 4,637 | 0.86 | 3,988 |
| Public, Non-DAC | Px | Steam Trap, Industrial Medium Pressure | 5,990 | 104% | 6,225 | 0.86 | 5,354 |
| Public, Non-DAC | Px | Tankless Water Heater | 23.88 | 851% | 203 | 0.86 | 175 |
| Public, Non-DAC Subtotal |  |  | 294,247 | 98% | 288,593 |  | 250,300 |
| Public, DAC | DI | DHW HW Pipe Insulation | 46.54 | 100% | 46.61 | 1.00 | 47 |
| Public, DAC | DI | Faucet Aerator - Bath | 1,447 | 100% | 1,447 | 1.00 | 1,447 |
| Public, DAC | DI | Garage Door Hinge | 4,677 | 93% | 4,368 | 1.00 | 4,368 |
| Public, DAC | DI | Showerheads | 279 | 100% | 279 | 1.00 | 279 |
| Public, DAC | DI | Weather Stripping | 237 | 100% | 237 | 1.00 | 237 |
| Public, DAC | Px | Boiler Tune Up, Space Heating | 9,680 | 100% | 9,680 | 1.00 | 9,680 |
| Public, DAC | Px | High Efficiency Boiler | 28,285 | 96% | 27,086 | 1.00 | 27,086 |
| Public, DAC | Px | Steam Trap, Industrial High Pressure | 52,793 | 101% | 53,138 | 1.00 | 53,138 |
| Public, DAC | Px | Steam Trap, Industrial Medium Pressure | 6,516 | 103% | 6,743 | 1.00 | 6,743 |
| Public, DAC Subtotal |  |  | 103,960 | 99% | 103,024 |  | 103,024 |
| Public, Subtotal |  |  | 398,207 | 98% | 391,617 |  | 353,323 |
| Total |  |  | 3,528,292 | 104% | 3,679,200 |  | 3,311,934 |

* Verified Gross RR, the realization rate (RR) is the ratio of Verified Gross Savings to Ex Ante Savings

† NTG, Net to Gross is the deemed value available on the SAG website: https://www.ilsag.info/evaluator-ntg-recommendations-for-2025. Disadvantaged communities (DAC) designated sites based on zip codes have an NTG of 1.00,

N/A: All savings estimating algorithms presented in the IL TRM v13.0 for the Building Operator Certification measure are for net savings. Therefore, this measure does not require additional application of NTG value.

Source: Evaluation team analysis.

# Impact Analysis Findings and Recommendations

## Impact Parameter Estimates

Table 5 shows the unit therm savings and realization rate findings by measure from our review. The realization rate is the ratio of the verified savings to the ex ante savings. Following the table, we provide findings and recommendations, including discussion of all measures with realization rates above or below 100%. Appendix A provides a description of the impact analysis methodology.

Table 5-1. Verified Gross Savings Parameters

| Measure | Unit Basis | Ex Ante Gross (therms/unit) | Verified Gross (therms/unit) | Realization Rate | IL TRM v13.0 Section† |
| --- | --- | --- | --- | --- | --- |
| Automatic Conveyor Broiler | Unit | 863 | 2,976 | 345% | 4.2.22 |
| BOC | Participant | 1,086 | 970 | 89% | 4.2.21 |
| Boiler Chemical Descaling | Unit | 708 | 708 | 100% | 4.4.49 |
| Boiler Tune Up, Process | Unit | 4,731 | 4,731 | 100% | 4.4.3 |
| Boiler Tune Up, Space Heating | Unit | 972 | 972 | 100% | 4.4.2 |
| Combination Oven | Unit | 580 | 558 | 096% | 4.2.1 |
| Commercial Pool Covers | Unit | 1,251 | 1,251 | 100% | 4.3.4 |
| Commercial Steam Cooker | Unit | 3,533 | 3,530 | 100% | 4.2.3 |
| Compressed Air Heat Recovery | Unit | 11,519 | 11,519 | 100% | 4.7.9 |
| Convection Oven | Unit | 334 | 206 | 62% | 4.2.5 |
| DHW HW Pipe Insulation | Ln Ft | 2 | 2 | 100% | 5.4.1 |
| Dishwasher | Unit | 313 | 313 | 100% | 4.2.6 |
| Faucet Aerator - Bath | Unit | 8 | 8 | 100% | 4.3.2 |
| Fryer | Unit | 607 | 645 | 106% | 4.2.7 |
| Garage Door Hinge | Unit | 52 | 48 | 91% | 4.8.2 |
| Grain Dryer Tune-Up | Unit | 19,623 | 23,467 | 120% | 4.1.15 |
| Griddle | Unit | 369 | 6,033 | 1636% | 4.2.8 |
| High Efficiency Boiler | Unit | 4,660 | 4,470 | 96% | 4.4.10 |
| High Efficiency Furnace | Unit | 347 | 347 | 100% | 4.4.11 |
| Infrared Heaters | Unit | 382 | 382 | 100% | 4.4.12 |
| Kitchen Demand Ventilation Controls | Unit | 267 | 267 | 100% | 4.2.16 |
| Pipe Insulation | Ln Ft | 46,306 | 46,306 | 100% | 4.4.14 |
| Pre-Rinse Spray Valves | Unit | 208 | 208 | 100% | 4.2.11 |
| Rack Oven - Double Oven | Unit | 551 | 1,964 | 356% | 4.2.18 |
| Showerheads | Unit | 11 | 11 | 100% | 4.3.3 |
| Small Commercial Thermostat | Unit | 235 | 269 | 115% | 4.4.48 |
| Steam Trap, Commercial | Unit | 249 | 264 | 106% | 4.4.16 |
| Steam Trap, Dry Cleaner | Unit | 844 | 853 | 101% | 4.4.16 |
| Steam Trap, Industrial High Pressure | Unit | 5,198 | 5,160 | 99% | 4.4.16 |
| Steam Trap, Industrial Medium Pressure | Unit | 1,134 | 1,164 | 103% | 4.4.16 |
| Storage Water Heater | Unit | 127 | 465 | 367% | 4.3.1 |
| Tankless Water Heater | Unit | 6 | 43 | 764% | 4.3.1 |
| Weather Stripping | Ln Ft | 10 | 10 | 100% | 4.8.16 |

* Program Tracking Data (PTD) provided by Nicor Gas, extract dated January 30, 2026.

† State of Illinois Technical Reference Manual version 13.0 from http://www.ilsag.info/technical-reference-manual.html.

‡ Project files and monthly billing data provided by Nicor Gas. Where conducted, on-site or telephone interview data collected by Guidehouse.

## Findings and Recommendations

Finding 1. The evaluation team used the Energy Star Qualified Products List (QPL) to verify reported tracking data inputs (such as Efficient Production Capacity, Efficient Cooking Energy Rate, and Efficiency). Verified savings used the Energy Star QPL value when the QPL and tracking data disagreed, as well as when a tracking data input was left blank and the model number could be found in the QPL.

Tracking data inputs were left blank for the Automatic Conveyor Broiler measure. The model number could be found in the QPL, so verified savings used the QPL to populate the Efficient Production Capacity, Efficient Idle Energy Rate, and Efficient Cooking Energy Rate input values. The evaluation team was unable to recreate ex ante savings with the QPL values as well as with default values from the Illinois Technical Reference Manual v13.0 (IL TRM v13.0). As noted in the midyear evaluation Interim Impact Review, the model number (Nieco FH94-HE*) could be found in the CY2024 tracking data, and CY2024 ex ante savings align with CY2025 verified savings which lead the evaluation team to the conclusion that a change in savings calculation approach was taken for CY2025 ex ante savings.

Not all values in the tracking data aligned with the QPL for Combination Oven measures. There were also a handful of measures where the evaluation team thought some convection inputs were in steam input columns, and vice versa. Verified savings use the QPL values and followed the IL TRM v13.0 algorithm for calculating the "GasIDLE_ConvEE" and "GasIDLE_SteamEE" inputs.

The evaluation team found all Convection Oven measure model numbers in the QPL. The evaluation team confirmed values in the "PostInstallationEfficiency", "CapacityNewEquipment", "ENERGYSTARPreheatRate", and "ENERGYSTARIDLEEnergyRate" tracking data columns aligned with the QPL for three of the four Convection Oven measures. The evaluation team was unable to recreate ex ante savings for these measures using the tracking data values, resulting in a realization rate of 50%. The fourth instance of the Convection Oven measure did not have values in the tracking data that aligned with the QPL, so verified savings used the QPL values. This measure appeared to use tracking data values in ex ante savings, resulting in a realization rate of 96%.

All Griddle measure model numbers could be found in the QPL, but not all values aligned between the tracking data and QPL. Verified savings used the QPL values for those instances. The evaluation team was unable to recreate ex ante savings using either the QPL values or the tracking data values for those instances. As noted in the midyear evaluation, the evaluation team believes the size of the baseline values in the tracking data contributes to this as the values are much larger than IL TRM v13 default values. Verified savings used the provided large baseline values in the tracking data.

All Fryer measure model numbers could be found in the QPL. The evaluation team used the QPL to confirm or overwrite values in the "PostInstallationEfficiency", "CapacityNewEquipment", "ENERGYSTARPreheatRate", and "ENERGYSTARIDLEEnergyRate" tracking data columns. All measures in the Midstream CFS program path but one have realization rates of 1.00, indicating ex ante savings also used the QPL values. Ex ante savings for the one measure in the Midstream CFS program path (Vendor Project ID 1749) and all measures in the Prescriptive program path indicate they use the tracking data values over the QPL, resulting in realization rates that range from 80% to 210%.

The evaluation team did not find the Rack Oven – Double Oven manufacturer in the QPL. Verified savings sourced the “PostInstallationEfficiency” and “BaselineEfficiency” values from the tracking data provided and used the IL TRM v13.0 for all other input values. The realization rate for this measure is 3.56.

Tracking data inputs were left blank for Dishwasher measures, but the model number could be found in the QPL. The evaluation team used the QPL to populate "WaterUse_ESTAR" and inform the dishwasher type and temperature. Verified savings were calculated with a natural gas building and electric booster water heater assumption. The realization rate is 1.00 for all measure instances, the evaluation team assumes this to be the approach ex ante savings took as well.

Recommendation 1.  Ensure the tracking data is populated with measure inputs needed to calculate savings, and that those inputs align with the Energy Star QPL. Ex ante savings should align with these values and the IL TRM v13.0 algorithms where appropriate.

Finding 2. As noted during the midyear evaluation, the evaluation team observed ex ante savings use the tracking data column “Utilization_Factor” for the temperature of saturated steam (T1) variable value for Steam Trap measures. The source of these values is unclear, the T1 variable should be based on the equation provided in the IL TRM v13.0. Verified savings used the IL TRM v13.0 equation to calculate the T1 value.

Recommendation 2. Provide additional context behind the values in the “Utilization_Factor” tracking data column, why they differ from the IL TRM v13.0 T1 calculation.

Finding 3. The evaluation team was unable to recreate ex ante savings for the following measures:

The Tankless Water Heater measures: As noted in the Interim Impact Review, the tracking data did not contain any information on the measure size in gallons, so verified savings used a value of 50 as has been done in previous evaluations.

Nineteen of the 30 the Grain Dryer Tune-Up measures: Eighteen measures have a realization rate of 1.39 and one measure has a realization rate of 47.47. Verified savings used the “Baseline Production Capacity” from the tracking data and IL TRM v13.0 values for all other inputs.

Eighteen of the 38 High Efficiency Boiler measures: Verified savings used input values from the tracking data.

The Storage Water Heater measures: Verified savings used inputs from the tracking data.

The Steam Trap “Indust HP 250 psig” measures: As noted in the Interim Impact Review, tracking data values for inputs such as “SteamlossPerTrap” and “HeatOfVaporization” do not align with those of a 250 psig. All other steam trap types have values in the tracking data for these inputs that align with the IL TRM v13.0. Verified savings used the tracking data for the "EquivalentFullLoadHours" and "EquipmentEfficiency(%)" values and sourced all other inputs from the IL TRM v13 based on the measure size and type.

The Small Commercial Thermostat measure installed in an Office – Low Rise building type: Verified savings used the “Capacity of Existing Equipment” and “EquivalentFullLoadHours" from the tracking data and the IL TRM v13.0 for all other inputs.

Recommendation 3. Ensure ex ante savings reflect information provided in the tracking data and IL TRM v13.0. Provide supplemental documentation showing how ex ante savings are calculated for the Grain Dryer Tune-Up measure.

Finding 4. Ex ante savings use a per unit value associated with a Warehouse in Climate Zone 1 for all Garage Door Hinge measures. However, verified savings used the building type and climate zone information provided in the tracking data to inform the IL TRM v13.0 deemed savings value.

Recommendation 4.  Ex ante savings should reflect the details provided in the tracking data.

Finding 5. The evaluation team observed the tracking data “Quantity” field had the same value as the “Horsepower” field for seven of the 10 instances of the Kitchen Demand Ventilation Controls measure. The other three instances had a value of 1 in the “Quantity” field. Verified savings used a quantity of 1 for all measures, this produces a realization rate of 1.00 for all measures.

Recommendation 5.  Ensure the tracking data information for quantity and horsepower support ex ante savings values for Kitchen Demand Ventilation Controls measures.

Finding 6. The evaluation team observed a DHW HW Pipe Insulation measure in the tracking data that referenced the Residential volume of the IL TRM v13.0. Although there were values provided in tracking data fields, ex ante savings appears to use the TRM deemed value for an unknown pipe orientation and ½” pipes with an In-Service Rate (ISR) of 100%. Verified savings followed suit so the measures have a 1.00 realization rate.

Recommendation 6.  Provide documentation on how the DHW HW Pipe Insulation  measure is calculated for a Commercial and Industrial program.

Finding 7. For three projects, the evaluation team updated the building area operated by the participant based on online research and detailed review of area information in the project files.

- BOC2025120. The participant reported operating one building with a managed square footage of 65,000 ft2. The evaluation team updated the area using data from the city of Evanston – Benchmarking & Building Performance Standards Program and verified savings for a managed square footage of 114,972 ft2. The evaluation team also referenced additional online resources (e.g., news articles, Evanston public library board meeting packet) to corroborate the updated square footage value.

- BOC2025121. The participant reported operating one building with a managed square footage of 322,196 ft2. The evaluation team updated the area using data from the city of Evanston – Benchmarking & Building Performance Standards Program and verified savings for a managed square footage of 370,638 ft2.

- BOC202577. The participant reported operating one building with a managed square footage of 50,000 ft2. The evaluation team verified a reduced area of 15,000 ft2 for the building using the Google measure tool and estimated verified savings for this updated managed square footage.

Finding 8. For two projects, the evaluation team did not verify any gas savings.

- BOC202510. The participant reported operating one building with a managed square footage of 168,893 ft2. The evaluation team verified electric energy and peak demand savings for the same managed square footage. However, the team verified no gas savings for this project as the participant indicated in the project files that the participating building is all electric.

- BOC202567. Nicor Gas confirmed that the participant for this project did not complete the BOC training program and was mistakenly included in the participation report. Thus, the evaluation team did not verify any savings for this project.

Recommendation 7.  Ensure that the participant has completed the BOC course and that the participating building has gas service before claiming savings for the project.

Finding 9. The evaluation team found the tracking data’s “ClimateZone” field is blank for all measures in the Midstream CFS program path as well as several other projects in the Business Optimization Program and Prescriptive program paths. In these cases, the evaluation team verified a climate zone using an Illinois Zip Code and Climate Zone mapping file to inform verified savings as applicable.

Recommendation 8.  The tracking data should provide a climate zone for every project.

# Appendix A. Impact Analysis Methodology

## Building Operator Certification

The impact evaluation team applied the algorithms from Measure 4.9.21 Building Operator Certification from IL-TRM v13.0. Guidehouse used information collected from the participants and internet research to determine the required inputs for the IL-TRM algorithm. If the square footage managed by a participant exceeded 500,000 ft2, savings were capped at 500,000 ft2 per participant. Table A-1 shows the savings coefficients from IL-TRM v13.0, and they are used in Equation 1 to verify the estimated annual energy savings.

Table A-1. BOC Savings Coefficients

Source: IL-TRM v13.0, Measure 4.9.21

Equation 1. Annual Natural Gas Energy Savings per Participant

Natural Gas Savings = Cg x Area (Minimum of participant ft2 or 500,000 ft2)

## All Other Measures

Guidehouse calculated the verified gross savings for each measure type by conducting a review of the tracking data and applying the algorithms of IL TRM v13.0 Commercial and Industrial volume, except the DHW HW Pipe Insulation measure which referenced the Residential volume, and IL TRM v13.0 Errata Memo. The evaluation team checked that savings inputs provided in the tracking data matched IL TRM v13.0 and that custom inputs were properly used. Then the tracking data and custom values used for the verified savings were adjusted from the tracking data, as necessary. The savings algorithms were applied to determine the verified savings of each measure. Verified gross realization rates are calculated by dividing the verified savings by the ex ante gross savings.

For most Commercial Food Service end use measures (applicable measures can be found in the Direct Install, Midstream CFS, and Prescriptive program paths), Guidehouse conducted an additional tracking data verification step. The evaluation team compared the tracking data values for these ENERGY STAR measures to the ENERGY STAR QPLs by manufacturer and model number. Where the team found tracking data values and QPLs values disagreed, the evaluation team used the QPL values to calculate ex ante savings. This approach aligns with Guidehouse’s process for the ComEd evaluations.

Based on the SAG policy, the evaluation team assigned a NTG of 1.00 to all projects that were in disadvantaged communities (DAC) based on census tract and with consumption under 35,000 Therms.

# Appendix B. Program Specific Inputs for the Illinois TRC

Table B-1 shows the Total Resource Cost (TRC) cost-effectiveness analysis inputs available at the time of producing this impact evaluation report. Additional required cost data (e.g., measure costs, program level incentive and non-incentive costs) are not included in this table and will be provided to the evaluation team later. Guidehouse will include annual and lifetime water savings and greenhouse gas reductions in the end of year summary report.

Table B-1. Verified Cost Effectiveness Inputs

| Program Category | Program Path | Savings Category | DAC Project | Units | Quantity | Effective Useful Life | Early Replacement Flag | Verified Gross Annual Water Savings (Gallons) | Ex Ante Gross Savings (Therms) | Verified Gross Savings (Therms) | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Private | BOC | BOC | FALSE | Participant | 8 | 13.00 | NO |  | 11,993 | 9,138 | 9,138 |
| Private | BOP | Boiler Tune Up, Process | FALSE | Unit | 21 | 2.00 | NO |  | 102,146 | 102,146 | 93,974 |
| Private | BOP | Steam Trap, Dry Cleaner | FALSE | Unit | 603 | 6.00 | NO | 4,294,381 | 511,456 | 516,916 | 475,563 |
| Private | BOP | Steam Trap, Dry Cleaner | TRUE | Unit | 116 | 6.00 | NO | 856,600 | 102,020 | 103,109 | 103,109 |
| Private | BOP | Steam Trap, Industrial High Pressure | FALSE | Unit | 154 | 6.00 | NO | 6,717,315 | 821,059 | 810,379 | 745,549 |
| Private | BOP | Steam Trap, Industrial High Pressure | TRUE | Unit | 9 | 6.00 | NO | 301,082 | 35,987 | 36,311 | 36,311 |
| Private | BOP | Steam Trap, Industrial Medium Pressure | FALSE | Unit | 132 | 6.00 | NO | 1,291,136 | 148,413 | 152,709 | 140,492 |
| Private | BOP | Steam Trap, Industrial Medium Pressure | TRUE | Unit | 10 | 6.00 | NO | 86,111 | 9,833 | 10,155 | 10,155 |
| Private | DI | Faucet Aerator - Bath | FALSE | Unit | 304 | 10.00 | NO | 568,303 | 2,501 | 2,501 | 2,150 |
| Private | DI | Faucet Aerator - Bath | TRUE | Unit | 2 | 10.00 | NO | 7,796 | 34.30 | 34.30 | 34 |
| Private | DI | Pre-Rinse Spray Valves | FALSE | Unit | 29 | 5.00 | NO | 781,747 | 5,698 | 5,698 | 4,900 |
| Private | DI | Showerheads | FALSE | Unit | 208 | 10.00 | NO | 354,096 | 2,231 | 2,231 | 1,918 |
| Private | DI | Garage Door Hinge | FALSE | Unit | 102 | 20.00 | NO |  | 5,301 | 4,682 | 4,026 |
| Private | DI | Garage Door Hinge | TRUE | Unit | 12 | 20.00 | NO |  | 624 | 589 | 589 |
| Private | CFS | Automatic Conveyor Broiler | FALSE | Unit | 1 | 12.00 | NO |  | 863 | 2,976 | 2,381 |
| Private | CFS | Combination Oven | FALSE | Unit | 19 | 12.00 | NO |  | 11,238 | 10,728 | 8,583 |
| Private | CFS | Convection Oven | FALSE | Unit | 2 | 12.00 | NO |  | 853 | 427 | 341 |
| Private | CFS | Dishwasher | FALSE | Unit | 1 | 10.00 | NO |  | 92.38 | 92.32 | 74 |
| Private | CFS | Fryer | FALSE | Unit | 40 | 12.00 | NO |  | 24,417 | 25,607 | 20,485 |
| Private | CFS | Griddle | FALSE | Unit | 5 | 12.00 | NO |  | 1,844 | 30,167 | 24,134 |
| Private | CFS | Kitchen Demand Ventilation Controls | FALSE | Unit | 16.5 | 20.00 | NO |  | 4,407 | 4,407 | 3,526 |
| Private | Px | Boiler Tune Up, Process | FALSE | Unit | 2 | 2.00 | NO |  | 28,052 | 28,052 | 24,125 |
| Private | Px | Boiler Tune Up, Process | TRUE | Unit | 1 | 2.00 | NO |  | 2,183 | 2,183 | 2,183 |
| Private | Px | Boiler Tune Up, Space Heating | FALSE | Unit | 20 | 3.00 | NO |  | 19,216 | 19,216 | 16,525 |
| Private | Px | Combination Oven | FALSE | Unit | 2 | 12.00 | NO |  | 1,009 | 1,180 | 1,015 |
| Private | Px | Commercial Pool Covers | FALSE | Unit | 1 | 6.00 | NO |  | 1,251 | 1,251 | 1,076 |
| Private | Px | Compressed Air Heat Recovery | FALSE | Unit | 7 | 15.00 | NO |  | 80,631 | 80,631 | 69,342 |
| Private | Px | Convection Oven | FALSE | Unit | 2 | 12.00 | NO |  | 425 | 409 | 352 |
| Private | Px | Fryer | FALSE | Unit | 24 | 12.00 | NO |  | 14,622 | 15,878 | 13,655 |
| Private | Px | Fryer | TRUE | Unit | 4 | 12.00 | NO |  | 2,235 | 2,406 | 2,406 |
| Private | Px | Grain Dryer Tune-Up | FALSE | Unit | 27 | 1.00 | NO |  | 511,617 | 626,926 | 539,156 |
| Private | Px | Grain Dryer Tune-Up | TRUE | Unit | 3 | 1.00 | NO |  | 77,077 | 77,077 | 77,077 |
| Private | Px | High Efficiency Boiler | FALSE | Unit | 4 | 25.00 | NO |  | 12,176 | 12,176 | 10,472 |
| Private | Px | High Efficiency Boiler | TRUE | Unit | 2 | 25.00 | NO |  | 6,678 | 6,678 | 6,678 |
| Private | Px | High Efficiency Furnace | FALSE | Unit | 14 | 16.50 | NO |  | 4,848 | 4,848 | 4,170 |
| Private | Px | High Efficiency Furnace | TRUE | Unit | 7 | 16.50 | NO |  | 1,814 | 1,814 | 1,814 |
| Private | Px | Infrared Heaters | FALSE | Unit | 12 | 15.00 | NO |  | 4,082 | 4,082 | 3,510 |
| Private | Px | Infrared Heaters | TRUE | Unit | 14 | 15.00 | NO |  | 5,846 | 5,846 | 5,846 |
| Private | Px | Pipe Insulation | FALSE | Ln Ft | 4 | 15.00 | NO |  | 185,224 | 185,224 | 159,293 |
| Private | Px | Rack Oven - Double Oven | FALSE | Unit | 3 | 12.00 | NO |  | 1,654 | 5,892 | 5,067 |
| Private | Px | Small Commercial Thermostat | FALSE | Unit | 2 | 11.00 | NO |  | 371 | 538 | 495 |
| Private | Px | Steam Trap, Commercial | FALSE | Unit | 99 | 6.00 | NO | 231,827 | 25,750 | 27,256 | 23,440 |
| Private | Px | Steam Trap, Dry Cleaner | FALSE | Unit | 11 | 6.00 | NO | 60,952 | 7,259 | 7,337 | 6,310 |
| Private | Px | Steam Trap, Dry Cleaner | TRUE | Unit | 24 | 6.00 | NO | 132,987 | 15,839 | 16,008 | 16,008 |
| Private | Px | Steam Trap, Industrial High Pressure | FALSE | Unit | 38 | 6.00 | NO | 1,639,454 | 196,368 | 197,964 | 170,249 |
| Private | Px | Steam Trap, Industrial High Pressure | TRUE | Unit | 3 | 6.00 | NO | 138,233 | 16,522 | 16,671 | 16,671 |
| Private | Px | Steam Trap, Industrial Medium Pressure | FALSE | Unit | 53 | 6.00 | NO | 860,051 | 100,707 | 102,556 | 88,198 |
| Private | Px | Steam Trap, Industrial Medium Pressure | TRUE | Unit | 1 | 6.00 | NO | 24,616 | 2,888 | 2,938 | 2,938 |
| Private | Px | Storage Water Heater | FALSE | Unit | 4 | 15.00 | NO |  | 508 | 1,861 | 1,601 |
| Private | Px | Tankless Water Heater | FALSE | Unit | 30 | 20.00 | NO |  | 141 | 1,268 | 1,091 |
| Private | Px | Tankless Water Heater | TRUE | Unit | 10 | 20.00 | NO |  | 81.34 | 413 | 413 |
| Public | BOC | BOC | FALSE | Participant | 16 | 13.00 | NO |  | 14,076 | 14,143 | 14,143 |
| Public | BOP | Steam Trap, Industrial Medium Pressure | FALSE | Unit | 21 | 6.00 | NO | 71,744 | 8,102 | 8,420 | 7,747 |
| Public | DI | DHW HW Pipe Insulation | TRUE | Ln Ft | 26 | 12.00 | NO |  | 46.54 | 46.61 | 47 |
| Public | DI | Faucet Aerator - Bath | FALSE | Unit | 1216 | 10.00 | NO | 2,280,359 | 10,034 | 10,034 | 8,629 |
| Public | DI | Faucet Aerator - Bath | TRUE | Unit | 161 | 10.00 | NO | 328,775 | 1,447 | 1,447 | 1,447 |
| Public | DI | Garage Door Hinge | FALSE | Unit | 75 | 20.00 | NO |  | 3,897 | 3,616 | 3,110 |
| Public | DI | Garage Door Hinge | TRUE | Unit | 90 | 20.00 | NO |  | 4,677 | 4,368 | 4,368 |
| Public | DI | Pre-Rinse Spray Valves | FALSE | Unit | 13 | 5.00 | NO | 423,446 | 3,086 | 3,086 | 2,654 |
| Public | DI | Showerheads | FALSE | Unit | 39 | 10.00 | NO | 66,393 | 418 | 418 | 360 |
| Public | DI | Showerheads | TRUE | Unit | 26 | 10.00 | NO | 44,262 | 279 | 279 | 279 |
| Public | DI | Weather Stripping | FALSE | Ln Ft | 121 | 10.00 | NO |  | 1,249 | 1,249 | 1,074 |
| Public | DI | Weather Stripping | TRUE | Ln Ft | 23 | 10.00 | NO |  | 237 | 237 | 237 |
| Public | CFS | Combination Oven | FALSE | Unit | 4 | 12.00 | NO |  | 2,255 | 2,044 | 1,635 |
| Public | CFS | Commercial Steam Cooker | FALSE | Unit | 1 | 12.00 | NO |  | 3,533 | 3,530 | 2,824 |
| Public | CFS | Convection Oven | FALSE | Unit | 1 | 12.00 | NO |  | 391 | 195 | 156 |
| Public | CFS | Dishwasher | FALSE | Unit | 3 | 10.00 | NO |  | 1,159 | 1,159 | 927 |
| Public | CFS | Pre-Rinse Spray Valves | FALSE | Unit | 1 | 5.00 | NO | 19,869 | 145 | 145 | 116 |
| Public | Px | Boiler Chemical Descaling | FALSE | Unit | 1 | 6.00 | NO |  | 708 | 708 | 609 |
| Public | Px | Boiler Tune Up, Process | FALSE | Unit | 5 | 2.00 | NO |  | 4,830 | 4,830 | 4,154 |
| Public | Px | Boiler Tune Up, Space Heating | FALSE | Unit | 99 | 3.00 | NO |  | 96,497 | 96,497 | 82,987 |
| Public | Px | Boiler Tune Up, Space Heating | TRUE | Unit | 10 | 3.00 | NO |  | 9,680 | 9,680 | 9,680 |
| Public | Px | High Efficiency Boiler | FALSE | Unit | 24 | 25.00 | NO |  | 129,950 | 123,929 | 106,579 |
| Public | Px | High Efficiency Boiler | TRUE | Unit | 8 | 25.00 | NO |  | 28,285 | 27,086 | 27,086 |
| Public | Px | High Efficiency Furnace | FALSE | Unit | 6 | 16.50 | NO |  | 2,716 | 2,716 | 2,336 |
| Public | Px | Small Commercial Thermostat | FALSE | Unit | 3 | 11.00 | NO |  | 806 | 809 | 744 |
| Public | Px | Steam Trap, Commercial | FALSE | Unit | 22 | 6.00 | NO | 39,442 | 4,381 | 4,637 | 3,988 |
| Public | Px | Steam Trap, Industrial High Pressure | TRUE | Unit | 12 | 6.00 | NO | 438,600 | 52,793 | 53,138 | 53,138 |
| Public | Px | Steam Trap, Industrial Medium Pressure | FALSE | Unit | 17 | 6.00 | NO | 53,040 | 5,990 | 6,225 | 5,354 |
| Public | Px | Steam Trap, Industrial Medium Pressure | TRUE | Unit | 15 | 6.00 | NO | 57,260 | 6,516 | 6,743 | 6,743 |
| Public | Px | Tankless Water Heater | FALSE | Unit | 4 | 20.00 | NO |  | 23.88 | 203 | 175 |
| Total or Weighted Average |  |  |  |  |  |  |  | 22,169,879 | 3,528,292 | 3,679,200 | 3,311,934 |

Source: Evaluation team analysis.

Nicor Gas 2025 Interim Impact Review Summary Findings 2025-GH Responses_11.11.25.xlsx

Sourced from http://www.zipcodestogo.com/Illinois/.

Available on the Illinois Stakeholder Advisory Group website: Illinois Statewide Technical Reference Manual Version 13.0.

Ibid.

Obtained from the Implementation Contractor for the 2025 calendar year: https://www.il-foodservicerebates.com/qualifying-equipment.