# Gas Optimization Program Impact Evaluation Report

Energy Efficiency Plan: Program Year 2025

(01/01/2025-12/31/2025)

Prepared for:

Peoples Gas and North Shore Gas

DRAFT

April 20, 2026

Prepared by:

| Eric Ogbe Guidehouse | Roger Hill InCA | Deborah Swarts InCA |  |
| --- | --- | --- | --- |

Submitted to:

Peoples Gas

North Shore Gas

200 East Randolph Street

Chicago, IL 60601

Submitted by:

Guidehouse Inc.

167 N. Green Street

12th Floor

Chicago, IL 60607

Contact:

| Charles Maglione, Partner 202.481.7352 cmaglione@guidehouse.com | Jeff Erickson, Director 608.616.4962 jeff.erickson@guidehouse.com | Laura Agapay-Read, Associate Director 312.583.4178 laura.agapay.read@guidehouse.com |
| --- | --- | --- |

Charles Ampong, Associate Director

608.616.4922

charles.ampong@guidehouse.com

This report was prepared by Guidehouse for People Gas Light and Coke Company (PGL)and North Shore Gas(NSG) companies. The work presented in this report represents Guidehouse’s professional judgment based on the information available at the time this report was prepared. Use of this report by any other party for whatever purpose should not, and does not, absolve such party from using due diligence in verifying the report’s contents. Neither Guidehouse nor any of its subsidiaries or affiliates assumes any liability or duty of care to such parties and hereby disclaims any such liability.

Table of Contents

1	Introduction	1

2	Program Description	1

3	Program Savings Detail	2

4	Program Savings by Measure	2

5	Impact Analysis Findings and Recommendations	3

5.1	Impact Parameter Estimates	3

5.2	Findings and Recommendations	3

Appendix A. Impact Analysis Methodology	5

Appendix B. Program Specific Inputs for the Illinois TRC	6

Table of Tables, Figures, and Equations

Table 1. 2025 Volumetric Summary for PGL	1

Table 2. 2025 Annual Energy Savings Summary for PGL	2

Table 3. 2025 Annual Energy Savings by Measure for PGL	2

Table 4. Profile of Gross Impact Sample for Gas Optimization Projects	5

Table 5. Sample Gross Realization Rates and Summary of Adjustments	5

Table 6. Verified Cost Effectiveness Inputs - PGL	6

# Introduction

This report presents the results of the impact evaluation of the Peoples Gas (PGL) and North Shore Gas (NSG) 2025 Gas Optimization program.  North Shore Gas (NSG) did not offer the program in 2025. This report presents a summary of the energy impacts for the total program and broken out by relevant measure and PGL program structure details. The appendices present the impact analysis methodology and the inputs for cost effectiveness analysis. Program year 2025 covers January 1 to December 31, 2025.

# Program Description

The Gas Optimization program provides a technical assessment service where energy advisors and contracted engineering firms review commercial, industrial, and public sector facilities for operation and maintenance issues that, if corrected, often provide short payback projects. In addition to identifying low-cost and no-cost measures that can be implemented by the customer, Gas Optimization studies also identify capital improvement projects. Incentives to complete recommended improvements include reimbursement for the cost of the technical assessment, rebates, and program implementation support. Projects identified through the Gas Optimization program include Boiler Combustion Control, HVAC Space Conditioning Control, and other energy saving measures. The program does not offer prescribed measures.

The Gas Optimization program had 7 participants in 2025 and completed 8 projects, as shown in Table 1

Table 1. 2025 Volumetric Summary for PGL

| Participation | Private | Public | Total |
| --- | --- | --- | --- |
| Participants * | 5 | 2 | 7 |
| Installed Projects † | 5 | 3 | 8 |
| Measure Types Installed ‡ | 4 | 2 | 5 |

* Participants are defined as unique work order IDs

† Installed Projects are defined as unique retrofit for each participant

‡ Total Measure Types Installed is less than the sum of private and public due to the same Measure Types in different building sectors.

Source: Peoples Gas tracking data and evaluation team analysis.

# Program Savings Detail

Table 2 summarizes the energy savings the PGL Gas Optimization program achieved in 2025, indicating which savings occurred in disadvantaged community (DAC) areas.

Table 2. 2025 Annual Energy Savings Summary for PGL

| Program Category | Ex Ante Gross Savings (Therms) | Verified Gross RR* | Verified Gross Savings (Therms) | NTG† | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- |
| Private, Non-Disadvantaged Communities | 145,647 | 77% | 112,609 | 0.94 | 105,853 |
| Private, Non-DAC Subtotal | 145,647 | 77% | 112,609 | 0.94 | 105,853 |
| Private, Disadvantaged Communities | 32,816 | 100% | 32,816 | 1.00 | 32,816 |
| Private, DAC Subtotal | 32,816 | 100% | 32,816 | 1.00 | 32,816 |
| Public, Non-Disadvantaged Communities | 9,946 | 82% | 8,174 | 0.94 | 7,683 |
| Public, Non-DAC Subtotal | 9,946 | 82% | 8,174 | 0.94 | 7,683 |
| Public, Disadvantaged Communities | 32,589 | 86% | 28,024 | 1.00 | 28,024 |
| Public, DAC Subtotal | 32,589 | 86% | 28,024 | 1.00 | 28,024 |
| Total or Weighted Average | 220,998 | 82% | 181,623 | 0.96 | 174,376 |

* Realization Rate (RR) is the ratio of verified gross savings to ex ante gross savings, based on evaluation research findings.

† NTG, (Net to Gross) is the deemed value available on the SAG website: https://www.ilsag.info/evaluator-ntg-recommendations-for-2025. Projects in DAC areas are assigned an NTG of 1.0.

Source: Evaluation team analysis.

# Program Savings by Measure

Table 3 presents the custom measures processed through the Gas Optimization program in 2025. The realization rate (RR) is the ratio of verified gross savings to ex ante gross savings, based on evaluation research findings for a sample of completed projects. Realization rate findings for individual sampled projects are provided in the Appendix. Boiler Combustion Controls and Boiler Condensate Recovery measures contributed the most savings.

Table 3. 2025 Annual Energy Savings by Measure for PGL

| Program Category | Savings Category | Ex Ante Gross Savings (Therms) |  | Verified Gross RR* |  | Verified Gross Savings (Therms) |  | NTG† |  | Verified Net Savings (Therms) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Private | Boiler Blowdown Reduction | 32,816 |  | 1.00 |  | 32,816 |  | 1.00 |  | 32,816 |  |
|  | Boiler Combustion Controls | 58,508 |  | 0.61 |  | 35,659 |  | 0.94 |  | 33,519 |  |
|  | Boiler Condensate Recovery | 47,287 |  | 0.93 |  | 44,198 |  | 0.94 |  | 41,546 |  |
|  | Others | 39,852 |  | 0.82 |  | 32,752 |  | 0.94 |  | 30,787 |  |
| Public | Space Conditioning Controls | 32,589 |  | 0.86 |  | 28,024 |  | 1.00 |  | 28,024 |  |
|  | Others | 9,946 |  | 0.82 |  | 8,174 |  | 0.94 |  | 7,683 |  |
| Total or Weighted Average |  |  | 220,998 |  | 0.82 |  | 181,623 |  | 0.96 |  | 174,376 |  |

* Realization Rate (RR) is the ratio of verified gross savings to ex ante gross savings, based on evaluation research findings.

† NTG, (Net to Gross) is the deemed value available on the SAG website: https://www.ilsag.info/evaluator-ntg-recommendations-for-2025/. Projects in DAC are assigned an NTG of 1.0.

Source: Evaluation team analysis.

# Impact Analysis Findings and Recommendations

## Impact Parameter Estimates

As a custom program, there are no common parameters across projects.

## Findings and Recommendations

The evaluation findings and recommendations are presented below. The detailed realization rates and evaluation findings for individual sampled projects are provided in Appendix A.

Finding 1. In WO-6567468, a Space Conditioning Controls project, the evaluation found that the ex ante savings calculation applied a condensate flow derived from unit heater capacity with a 90% safety factor, whereas the project documentation indicated lower condensate flow. As a result, the evaluation team used the documented condensate flow values and removed the safety factor in the savings analysis, resulting in a RR of 72%.

Recommendation 1.  The evaluation team recommends that condensate flow inputs be based on documented or measured values and that safety factors not be applied unless clearly justified and supported by project documentation.

Finding 2. In WO-4297269, a Boiler Combustion Controls project, the evaluation team found that the ex ante savings was estimated using a regression approach with a relatively weak correlation (R² = 0.618) and low savings relative to total usage (less than 10%), making it difficult to distinguish savings from data variability. Additionally, the evaluation found that a baseline outlier month significantly reduced production and skewed results. As a result, the evaluation team included additional baseline data and examined scenarios both with and without the outlier to ensure a more stable analysis. The evaluation removed the outlier and calculated a verified gross RR of 61%.

Recommendation 2.  The evaluation team recommends that regression-based savings methods be applied only where model fit is sufficiently strong and savings are distinguishable from data variability, and that baseline data be screened for outliers and supplemented where necessary to ensure robust and reliable results.

# Appendix A. Impact Analysis Methodology

The evaluation selected a simple random sample of five projects from a total of eight projects for review, as shown in Table 4.

Table 4. Profile of Gross Impact Sample for Gas Optimization Projects

| Population Summary |  |  |  |  | Sample Summary |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Program | Sampling Strata | Number of Projects (N) | Ex Ante Gross Savings | Percent of Ex Ante Gross | Sample Size (n) | Ex Ante Gross Savings | Sampled % of Population |
|  |  |  | (Therms) |  |  | (Therms) | (% Therms) |
| PGL Gas Optimization | N/A | 8 | 220,998 | 100% | 5 | 153,864 | 70% |

Source: Evaluation team analysis.

Engineering Review of Project Files

For each selected project, the evaluation did an in-depth application review to assess the engineering methods, parameters and assumptions used to generate all ex ante impact estimates. For each measure in the sampled project, evaluation engineers estimated ex post gross savings based on their review of documentation and engineering analysis.

To support this review, evaluation team reviewed project documentation in electronic format for each sampled project. Documentation included some or all scanned files of hardcopy application forms and supporting documentation from the applicant (invoices, measure specification sheets, and vendor proposals), pre-inspection reports and photos, post inspection reports and photos, and calculation spreadsheets

Table 5 provides a summary of verification results and adjustments for the PGL sampled Gas Optimization projects.

Table 5. Sample Gross Realization Rates and Summary of Adjustments

| Project ID | Measure | Realization Rate | Comments |
| --- | --- | --- | --- |
| WO-5336065 | Boiler Blowdown Reduction | 100% |  |
| WO-6658577 | Space Conditioning Controls | 100% |  |
| WO-6043950 | Boiler Combustion Controls | 61% | Updated regression analysis |
| WO-7121873 | Boiler Condensate Recovery | 100% |  |
| WO-6567468 | Space Conditioning Controls | 72% | Condensate flow update |

Source: Evaluation team analysis

# Appendix B. Program Specific Inputs for the Illinois TRC

Table 6 shows the Total Resource Cost (TRC) cost-effectiveness analysis inputs available at the time of producing this impact evaluation report. Additional required cost data (e.g., measure costs, program level incentive and non-incentive costs) are not included in this table and will be provided to the evaluation team later. Guidehouse will include annual and lifetime water savings and greenhouse gas reductions in the end of year summary report.

Table 6. Verified Cost Effectiveness Inputs - PGL

| Program Category | Savings Category | DAC Project |  | Units |  | Quantity |  | Effective Useful Life |  | Early Replacement Flag† |  | Ex Ante Gross Savings (Therms) |  | Verified Gross Savings (Therms) |  | Verified Net Savings (Therms) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Private | Boiler Blowdown Reduction | TRUE |  | Project |  | 1 |  | 20.0 |  | NO |  | 32,816 |  | 32,816 |  | 32,816 |  |
|  | Boiler Combustion Controls | FALSE |  | Project |  | 1 |  | 20.0 |  | NO |  | 58,508 |  | 35,659 |  | 33,519 |  |
|  | Boiler Condensate Recovery | FALSE |  | Project |  | 2 |  | 20.0 |  | NO |  | 47,287 |  | 44,198 |  | 41,546 |  |
|  | Others | FALSE |  | Project |  | 1 |  | 20.0 |  | NO |  | 39,852 |  | 32,752 |  | 30,787 |  |
| Public | Space Conditioning Controls | TRUE |  | Project |  | 2 |  | 20.0 |  | NO |  | 32,589 |  | 28,024 |  | 28,024 |  |
|  | Others | FALSE |  | Project |  | 1 |  | 20.0 |  | NO |  | 9,946 |  | 8,174 |  | 7,683 |  |
| Total or Weighted Average |  |  |  |  |  |  |  |  | 20.0 |  |  |  | 220,998 |  | 181,623 |  | 174,376 |

Source: Evaluation team analysis.