# Small and Midsize Business Program Impact Evaluation Report

Energy Efficiency Plan: Program Year 2025

(01/01/2025-12/31/2025)

Prepared for:

Peoples Gas and North Shore Gas

DRAFT

April 3, 2026

Prepared by:

| Marlon McClinton Utilivate Technologies | Walter Roberson Utilivate Technologies |  |  |
| --- | --- | --- | --- |

Submitted to:

Peoples Gas

North Shore Gas

200 East Randolph Street

Chicago, IL 60601

Submitted by:

Guidehouse Inc.

167 N. Green Street

12th Floor

Chicago, IL 60607

Contact:

| Charles Maglione, Partner 202.481.7352 cmaglione@guidehouse.com | Jeff Erickson, Director 608.616.4962 jeff.erickson@guidehouse.com | Laura Agapay-Read, Associate Director 312.583.4178 laura.agapay.read@guidehouse.com |
| --- | --- | --- |

Charles Ampong, Associate Director

608.616.4922

charles.ampong@guidehouse.com

This report was prepared by Guidehouse for People Gas Light and Coke Company (PGL)and North Shore Gas (NSG) companies. The work presented in this report represents Guidehouse’s professional judgment based on the information available at the time this report was prepared. Use of this report by any other party for whatever purpose should not, and does not, absolve such party from using due diligence in verifying the report’s contents. Neither Guidehouse nor any of its subsidiaries or affiliates assumes any liability or duty of care to such parties and hereby disclaims any such liability.

Table of Contents

1	Introduction	1

2	Program Description	1

3	Program Savings Detail	4

4	Program Savings by Measure	5

5	Impact Analysis Findings and Recommendations	8

5.1	Impact Parameter Estimates	8

5.2	Findings and Recommendations	9

Appendix A. Impact Analysis Methodology	11

Appendix B. Program Specific Inputs for the Illinois TRC	12

Table of Tables, Figures, and Equations

Table 1. 2025 Volumetric Summary for PGL	1

Table 2. 2025 Installed Measure Quantities for PGL	2

Table 3. 2025 Volumetric Summary for NSG	3

Table 4. 2025 Installed Measure Quantities for NSG	3

Table 5. 2025 Annual Energy Savings Summary for PGL	4

Table 6. 2025 Annual Energy Savings Summary for NSG	4

Table 7. 2025 Annual Energy Savings by Measure for PGL	5

Table 8. 2025 Annual Energy Savings by Measure for NSG	6

Table 9. Verified Gross Savings Parameters	8

# Introduction

This report presents the results of the impact evaluation of the Peoples Gas (PGL) and North Shore Gas (NSG) 2025 Small and Midsize Business (SMB) program. It presents a summary of the energy impacts for the total program and broken out by relevant measure and program structure details. The program covered only private sector measures in 2025. The appendices present the impact analysis methodology and inputs to the TRC calculations. Program year 2025 covers January 1 to December 31, 2025.

# Program Description

The 2025 SMB Program is offered by PGL and NSG. The SMB Program seeks to secure energy savings through direct installation (DI) of low-cost efficiency measures, rebates for the installation of prescriptive (Px) retrofit measures, and custom rebates for non-prescriptive upgrades or for projects that do not follow a one-for-one replacement. A network of partner trade allies (PTA) promotes measures and assists in engaging customers to participate in site assessments to identify savings opportunities. To serve as a PTA, participation and customer satisfaction goals must be achieved. Customers using a PTA will be eligible for enhanced rebate levels.

The SMB Program offered point of sale discount for commercial food service (CFS) equipment using program delivery channels. This path’s goals are to reduce barriers for food service operators to purchasing energy efficient equipment and reduce energy usage in the commercial food service sector.

In several tables in this report, measures are separated into those that were installed in disadvantaged communities (DAC) or a non-DAC community. Participants in DAC are identified based on their census tract or zipcode. Based on SAG Policy, business participants in a DAC with consumption under 35,000 Therms are assigned a NTG of 1.00.

The PGL program had 80 participants in 2025 and completed 81 projects as shown in the following table.

Table 1. 2025 Volumetric Summary for PGL

| Participation | PTA | Px | CFS | Custom | Total |
| --- | --- | --- | --- | --- | --- |
| Participants * | 35 | 20 | 22 | 3 | 80 |
| Installed Projects † | 35 | 20 | 23 | 3 | 81 |
| Measure Types Installed ‡ | 10 | 13 | 6 | 3 | 26 |

* Participants are defined as unique combination of customer name and business name.

† Installed Projects are defined as unique project IDs.

‡ Measure types are defined as unique measures implemented by the program.

Source: Peoples Gas tracking data and evaluation team analysis.

Table 2 summarizes the installed measure quantities that are the basis for verified energy savings for PGL.

Table 2. 2025 Installed Measure Quantities for PGL

| Program Path | Measure | Quantity Unit | Installed Quantity |
| --- | --- | --- | --- |
| PTA | Boiler Tune Up - Process | MBH | 6,000 |
|  | Boiler Tune Up (COM) | MBH | 16,000 |
|  | Steam Pipe Insulation | LN FT | 3,137 |
|  | Steam Pipe Insulation - Fitting | LN FT | 313 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | Each | 17 |
|  | Steam Traps - HVAC Repair/Rep - Audit | Each | 520 |
|  | Steam Traps - Industrial/Process Audit - 15 <= psig < 30 | Each | 5 |
| Px | Boiler - HW <=300MBtu >=88% AFUE (COM) | MBH | 1,198 |
|  | Boiler - HW 300-2500MBtu >88% TE | MBH | 5,000 |
|  | Boiler Tune Up - Process | MBH | 14,999 |
|  | Boiler Tune Up (COM) | MBH | 722 |
|  | Demand Controlled Ventilation (Gas Heating) | SQ FT | 153,600 |
|  | Large Gas Water Heater | MBH | 796 |
|  | Linkageless controls -for new burners | MBH | 46,200 |
|  | Smart Thermostat | Each | 4 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | Each | 5 |
|  | Tankless Water Heater 0.90 UEF | Each | 1,194 |
| CFS | Combination Oven Gas - <15 Pans | Each | 16 |
|  | Convection Oven | Each | 2 |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) | Each | 7 |
|  | Gas Cooktops | Each | 6 |
|  | Griddle Dual | Each | 1 |
|  | High Efficiency Pre-Rinse Spray Valve | Each | 4 |
| PTA-DAC | Boiler - HW 300-2500MBtu >88% TE | MBH | 5,663 |
|  | Boiler Tune Up (COM) | MBH | 1,439 |
|  | HW Pipe Insulation | LN FT | 200 |
|  | Steam Pipe Insulation | LN FT | 360 |
|  | Steam Pipe Insulation - Fitting | LN FT | 20 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | Each | 23 |
|  | Steam Traps - HVAC Repair/Rep - Audit | Each | 110 |
|  | Steam Traps - HVAC Repair/Rep - No Audit | Each | 74 |
| Px-DAC | Boiler Reset Controls | MBH | 1,250 |
|  | Boiler Tune Up (COM) | MBH | 3,012 |
|  | Demand Controlled Ventilation (Gas Heating) | SQ FT | 133,203 |
|  | Ozone Laundry Laundromat | lb-capacity | 1,995 |
|  | Smart Thermostat | Each | 2 |
|  | Steam Traps - HVAC Repair/Rep - No Audit | Each | 87 |
|  | Tankless Water Heater 0.90 UEF | Each | 398 |
| CFS-DAC | Combination Oven Gas - <15 Pans | Each | 6 |
|  | Convection Oven | Each | 1 |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) | Each | 3 |
|  | Griddle Dual | Each | 1 |
| Custom | HVAC - Other - PG SB Custom | Each | 1 |
|  | Process - Insulation >212 F - PG SB Custom | Each | 1 |
|  | Steam Traps-Industrial/Process Audit | Each | 4 |

Source: Peoples Gas tracking data and evaluation team analysis.

The NSG program had 57 participants in 2025 and completed 58 projects as shown in the following table.

Table 3. 2025 Volumetric Summary for NSG

| Participation | PTA | Px | CFS | Custom | Total |
| --- | --- | --- | --- | --- | --- |
| Participants * | 33 | 16 | 8 | 0 | 57 |
| Installed Projects † | 33 | 16 | 9 | 0 | 58 |
| Measure Types Installed ‡ | 1 | 14 | 6 | 0 | 20 |

* Participants are defined as unique combination of customer name and business name.

† Installed Projects are defined as unique project IDs.

‡ Measure types are defined as unique measures implemented by the program.

Source: North Shore Gas tracking data and Guidehouse evaluation team analysis.

Table 4 summarizes the installed measure quantities that are the basis for verified energy savings for NSG.

Table 4. 2025 Installed Measure Quantities for NSG

| Program Path | Measure | Quantity Unit | Installed Quantity |
| --- | --- | --- | --- |
| PTA | Steam Traps - Dry Cleaner Rep. - Audit | Each | 214 |
| Px | Boiler Tune Up - Process | MBH | 2,307 |
|  | DCV - Kitchen | HP | 10 |
|  | Demand Controlled Ventilation (Gas Heating) | SQ FT | 145,300 |
|  | Energy Star Convection Oven | Each | 1 |
|  | Energy Star Dishwasher | Each | 2 |
|  | Energy Star Double Rack Oven | Each | 1 |
|  | Energy Star Fryer | Each | 2 |
|  | Furnace > 95% AFUE (COM) | Each | 1 |
|  | Large Gas Water Heater | MBH | 399 |
|  | Makeup Air Unit | CFM | 3,800 |
|  | Programmable Thermostat | Each | 12 |
|  | Smart Thermostat | Each | 1 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | Each | 12 |
|  | Tankless Water Heater 0.90 UEF | Each | 3,390 |
| CFS | Combination Oven >30 Pans | Each | 2 |
|  | Combination Oven Gas - <15 Pans | Each | 4 |
|  | Dishwasher High Temp - Under Counter - Gas Bldg - Elec Boost | Each | 3 |
|  | Fryer Large Vat Open Deep-Vat Fryer | Each | 1 |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) | Each | 1 |
| PTA-DAC | Steam Traps - Dry Cleaner Rep. - Audit | Each | 51 |
| Px-DAC | DCV - Kitchen | HP | 3 |
|  | Energy Star Dishwasher | Each | 1 |
|  | Energy Star Fryer | Each | 1 |
|  | Furnace > 95% AFUE (COM) | Each | 1 |
|  | Tankless Water Heater 0.90 UEF | Each | 398 |
| CFS-DAC | Automatic Conveyer Broiler Commercial > 26" Conveyor Width | Each | 1 |

Source: North Shore Gas tracking data and Guidehouse evaluation team analysis.

# Program Savings Detail

Table 5 summarizes the energy savings the PGL SMB Prescriptive Program achieved by path in 2025.

Table 5. 2025 Annual Energy Savings Summary for PGL

| Program Category | Program Path | Ex Ante Gross Savings (Therms) | Verified Gross RR* | Verified Gross Savings (Therms) | NTG† | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- | --- |
| Non-DAC | PTA | 466,787 | 0.98 | 459,394 | 0.93 | 427,236 |
|  | Px | 65,912 | 0.95 | 62,986 | 0.93 | 58,598 |
|  | CFS | 20,106 | 0.59 | 12,001 | 0.80 | 9,601 |
|  | Custom | 10,050 | 1.03 | 10,333 | 0.93 | 9,609 |
| Non-DAC Subtotal |  | 562,855 | 0.97 | 544,714 | 0.93 | 505,044 |
| DAC | PTA | 141,353 | 0.90 | 128,517 | 1.00 | 128,517 |
|  | Px | 51,253 | 0.99 | 51,210 | 1.00 | 51,210 |
|  | CFS | 6,458 | 0.71 | 4,634 | 1.00 | 4,634 |
| DAC Subtotal |  | 199,064 | 0.93 | 184,361 | 1.00 | 184,361 |
| Total |  | 761,919 | 0.96 | 729,075 |  | 689,405 |

* Realization Rate (RR) is the ratio of verified gross savings to ex ante gross savings, based on evaluation research findings.

† NTG, Net to Gross is the deemed value available on the SAG website: https://www.ilsag.info/evaluator-ntg-recommendations-for-2025/. The Px NTG is 0.93 for all measures, except for thermostats, which is 0.97.

Source: Evaluation team analysis.

Table 6 summarizes the energy savings the NSG SMB Prescriptive Program achieved by path in 2025.

Table 6. 2025 Annual Energy Savings Summary for NSG

| Program Category | Program Path | Ex Ante Gross Savings (Therms) | Verified Gross RR* | Verified Gross Savings (Therms) | NTG† | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- | --- |
| Non-DAC | PTA | 251,493 | 0.55 | 138,674 | 0.93 | 128,967 |
|  | Px | 32,629 | 0.79 | 25,920 | 0.93 | 24,173 |
|  | CFS | 7,368 | 0.53 | 3,945 | 0.80 | 3,156 |
| Non-DAC Subtotal |  | 291,490 | 0.58 | 168,539 | 0.93 | 156,296 |
| DAC | PTA | 60,979 | 0.54 | 33,048 | 1.00 | 33,048 |
|  | Px | 2,418 | 0.99 | 2,402 | 1.00 | 2,402 |
|  | CFS | 862 | 1.35 | 1,167 | 1.00 | 1,167 |
| DAC Subtotal |  | 64,259 | 0.57 | 36,617 | 1.00 | 36,617 |
| Total |  | 355,749 | 0.58 | 205,156 |  | 192,913 |

* Realization Rate (RR) is the ratio of verified gross savings to ex ante gross savings, based on evaluation research findings.

† NTG, Net to Gross is the deemed value available on the SAG website: https://www.ilsag.info/evaluator-ntg-recommendations-for-2025/. The Px NTG is 0.93 for all measures, except for thermostats, which is 0.97.

Source: Evaluation team analysis.

# Program Savings by Measure

The PGL program includes 43 measures as shown in the following table. The steam traps and linkageless controls measures contributed the most savings.

Table 7. 2025 Annual Energy Savings by Measure for PGL

| Program Path | Savings Category | Ex Ante Gross Savings (Therms) | Verified Gross RR* | Verified Gross Savings (Therms) | NTG† | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- | --- |
| PTA | Boiler Tune Up - Process | 6,136 | 100% | 6,136 | 0.93 | 5,706 |
|  | Boiler Tune Up (COM) | 5,978 | 100% | 5,978 | 0.93 | 5,559 |
|  | Steam Pipe Insulation | 24,671 | 100% | 24,671 | 0.93 | 22,944 |
|  | Steam Pipe Insulation - Fitting | 2,210 | 100% | 2,210 | 0.93 | 2,056 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | 20,326 | 54% | 11,016 | 0.93 | 10,245 |
|  | Steam Traps - HVAC Repair/Rep - Audit | 403,691 | 100% | 405,606 | 0.93 | 377,216 |
|  | Steam Traps - Industrial/Process Audit - 15 <= psig < 30 | 3,790 | 100% | 3,790 | 0.93 | 3,525 |
| Px | Boiler - HW <=300MBtu >=88% AFUE (COM) | 818 | 99% | 818 | 0.93 | 761 |
|  | Boiler - HW 300-2500MBtu >88% TE | 8,390 | 99% | 8,389 | 0.93 | 7,802 |
|  | Boiler Tune Up - Process | 15,340 | 99% | 15,340 | 0.93 | 14,266 |
|  | Boiler Tune Up (COM) | 306 | 100% | 306 | 0.93 | 284 |
|  | Demand Controlled Ventilation (Gas Heating) | 5,376 | 100% | 5,376 | 0.93 | 4,999 |
|  | Large Gas Water Heater | 735 | 99% | 735 | 0.93 | 684 |
|  | Linkageless controls -for new burners | 27,305 | 100% | 27,305 | 0.93 | 25,394 |
|  | Smart Thermostat | 528 | 100% | 528 | 0.97 | 512 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | 5,978 | 54% | 3,240 | 0.93 | 3,013 |
|  | Tankless Water Heater 0.90 UEF | 1,132 | 83% | 944 | 0.93 | 878 |
| CFS | Combination Oven Gas - <15 Pans | 9,171 | 79% | 7,303 | 0.80 | 5,842 |
|  | Convection Oven | 563 | 74% | 418 | 0.80 | 334 |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) | 9,537 | 37% | 3,587 | 0.80 | 2,869 |
|  | Gas Cooktops | 407 | 100% | 407 | 0.80 | 325 |
|  | Griddle Dual | 291 | 51% | 149 | 0.80 | 119 |
|  | High Efficiency Pre-Rinse Spray Valve | 136 | 100% | 136 | 0.80 | 109 |
| Custom | HVAC - Other - PG SB Custom | 2,307 | 100% | 2,308 | 0.93 | 2,146 |
|  | Process - Insulation >212 F - PG SB Custom | 1,612 | 100% | 1,612 | 0.93 | 1,499 |
|  | Steam Traps-Industrial/Process Audit | 6,129 | 104% | 6,413 | 0.93 | 5,964 |
| PTA-DAC | Boiler - HW 300-2500MBtu >88% TE | 6,062 | 100% | 6,062 | 1.00 | 6,062 |
|  | Boiler Tune Up (COM) | 702 | 100% | 702 | 1.00 | 702 |
|  | HW Pipe Insulation | 531 | 100% | 531 | 1.00 | 531 |
|  | Steam Pipe Insulation | 4,611 | 99% | 4,611 | 1.00 | 4,611 |
|  | Steam Pipe Insulation - Fitting | 323 | 100% | 323 | 1.00 | 323 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | 27,500 | 54% | 14,904 | 1.00 | 14,904 |
|  | Steam Traps - HVAC Repair/Rep - Audit | 86,000 | 99% | 85,797 | 1.00 | 85,797 |
|  | Steam Traps - HVAC Repair/Rep - No Audit | 15,620 | 99% | 15,584 | 1.00 | 15,584 |
| Px-DAC | Boiler Reset Controls | 1,678 | 100% | 1,678 | 1.00 | 1,678 |
|  | Boiler Tune Up (COM) | 1,278 | 100% | 1,278 | 1.00 | 1,278 |
|  | Demand Controlled Ventilation (Gas Heating) | 4,662 | 99% | 4,662 | 1.00 | 4,662 |
|  | Ozone Laundry Laundromat | 24,746 | 99% | 24,746 | 1.00 | 24,746 |
|  | Smart Thermostat | 240 | 100% | 240 | 1.00 | 240 |
|  | Steam Traps - HVAC Repair/Rep - No Audit | 18,364 | 99% | 18,321 | 1.00 | 18,321 |
|  | Tankless Water Heater 0.90 UEF | 282 | 100% | 282 | 1.00 | 282 |
| CFS-DAC | Combination Oven Gas - <15 Pans | 3,398 | 80% | 2,738 | 1.00 | 2,738 |
|  | Convection Oven | 540 | 38% | 209 | 1.00 | 209 |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) | 2,228 | 68% | 1,537 | 1.00 | 1,537 |
|  | Griddle Dual | 291 | 51% | 149 | 1.00 | 149 |
| Total |  | 761,919 | 95% | 729,075 |  | 689,405 |

* Realization Rate (RR) is the ratio of verified gross savings to ex ante gross savings, based on evaluation research findings.

† NTG, Net to Gross is the deemed value available on the SAG website: https://www.ilsag.info/evaluator-ntg-recommendations-for-2025/.

Source: Evaluation team analysis.

Table 8. 2025 Annual Energy Savings by Measure for NSG

| Program Path | Savings Category | Ex Ante Gross Savings (Therms) | Verified Gross RR* | Verified Gross Savings (Therms) | NTG† | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- | --- |
| PTA | Steam Traps - Dry Cleaner Rep. - Audit | 251,499 | 55% | 138,682 | 0.93 | 128,979 |
| Px | Boiler Tune Up - Process | 2,359 | 100% | 2,359 | 0.92 | 2,194 |
|  | DCV - Kitchen | 2,133 | 100% | 2,133 | 0.93 | 1,983 |
|  | Demand Controlled Ventilation (Gas Heating) | 5,085 | 100% | 5,085 | 0.93 | 4,729 |
|  | Energy Star Convection Oven | 209 | 99% | 209 | 0.93 | 194 |
|  | Energy Star Dishwasher | 1,222 | 100% | 1,222 | 0.93 | 1,136 |
|  | Energy Star Double Rack Oven | 585 | 100% | 585 | 0.93 | 544 |
|  | Energy Star Fryer | 1,025 | 100% | 1,025 | 0.93 | 953 |
|  | Furnace > 95% AFUE (COM) | 235 | 99% | 235 | 0.93 | 219 |
|  | Large Gas Water Heater | 266 | 100% | 266 | 0.93 | 247 |
|  | Makeup Air Unit | 661 | 100% | 661 | 0.93 | 614 |
|  | Programmable Thermostat | 1,521 | 100% | 1,521 | 0.97 | 1,475 |
|  | Smart Thermostat | 157 | 100% | 157 | 0.97 | 152 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | 14,348 | 54% | 7,776 | 0.93 | 7,231 |
|  | Tankless Water Heater 0.90 UEF | 2,819 | 95% | 2,682 | 0.93 | 2,494 |
| CFS | Combination Oven >30 Pans | 1,328 | 73% | 973 | 0.80 | 779 |
|  | Combination Oven Gas - <15 Pans | 2,143 | 85% | 1,825 | 0.80 | 1,460 |
|  | Dishwasher High Temp - Under Counter - Gas Bldg - Elec Boost | 562 | 37% | 213 | 0.80 | 170 |
|  | Fryer Large Vat Open Deep-Vat Fryer | 1,106 | 38% | 420 | 0.80 | 336 |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) | 2,228 | 22% | 512 | 0.80 | 409 |
| PTA-DAC | Steam Traps - Dry Cleaner Rep. - Audit | 60,979 | 54% | 33,048 | 1.00 | 33,048 |
| Px-DAC | DCV - Kitchen | 693 | 99% | 693 | 1.00 | 693 |
|  | Energy Star Dishwasher | 676 | 100% | 676 | 1.00 | 676 |
|  | Energy Star Fryer | 512 | 100% | 512 | 1.00 | 512 |
|  | Furnace > 95% AFUE (COM) | 205 | 100% | 205 | 1.00 | 205 |
|  | Tankless Water Heater 0.90 UEF | 331 | 95% | 314 | 1.00 | 314 |
| CFS-DAC | Automatic Conveyer Broiler Commercial > 26" Conveyor Width | 862 | 135% | 1,167 | 1.00 | 1,167 |
| Total |  | 355,749 | 57% | 205,156 |  | 192,913 |

Source: Evaluation team analysis.

# Impact Analysis Findings and Recommendations

## Impact Parameter Estimates

Table 9 shows the unit therm savings and realization rate findings by measure from our review. The realization rate is the ratio of the verified savings to the ex ante savings. Following the table, we provide findings and recommendations, including discussion of all measures with realization rates above or below 100%. Appendix A provides a description of the impact analysis methodology.

Table 9. Verified Gross Savings Parameters

| Measure | Unit Basis | Ex Ante Gross (therms/unit) | Verified Gross (therms/unit) | Realization Rate | Illinois TRM v13.0, Section* |
| --- | --- | --- | --- | --- | --- |
| Automatic Conveyer Broiler Commercial > 26" Conveyor Width | Each | 863 | 1,167 | 135% | 4.2.22 |
| Boiler - HW <=300MBtu >=88% AFUE (COM) | MBH | 0.68 | 0.68 | 99% | 4.4.10 |
| Boiler - HW 300-2500MBtu >88% TE | MBH | 1.35 | 1.35 | 100% | 4.4.10 |
| Boiler Reset Controls | MBH | 1.34 | 1.34 | 100% | 4.4.3 |
| Boiler Tune Up - Process | MBH | 1.02 | 1.02 | 100% | 4.4.3 |
| Boiler Tune Up (COM) | MBH | 0.39 | 0.39 | 100% | 4.4.3 |
| Combination Oven >30 Pans | Each | 664 | 487 | 73% | 4.2.1 |
| Combination Oven Gas - <15 Pans | Each | 566 | 456 | 80% | 4.2.1 |
| Convection Oven | Each | 368 | 209 | 56% | 4.2.5 |
| DCV - Kitchen | HP | 213 | 213 | 99% | 4.2.16 |
| Demand Controlled Ventilation (Gas Heating) | SQ FT | 0.03 | 0.03 | 99% | 4.4.16 |
| Dishwasher High Temp - Under Counter - Gas Bldg - Elec Boost | Each | 187 | 71 | 37% | 4.2.6 |
| Energy Star Convection Oven | Each | 209 | 209 | 99% | 4.2.5 |
| Energy Star Dishwasher | Each | 633 | 633 | 100% | 4.2.6 |
| Energy Star Double Rack Oven | Each | 585 | 585 | 100% | 4.2.18 |
| Energy Star Fryer | Each | 513 | 513 | 100% | 4.2.7 |
| Fryer Large Vat Open Deep-Vat Fryer | Each | 1,107 | 421 | 38% | 4.2.7 |
| Fryer Standard Open Deep-Vat Fryer (French Fryer) | Each | 1,272 | 512 | 40% | 4.2.7 |
| Furnace > 95% AFUE (COM) | Each | 221 | 221 | 100% | 4.4.11 |
| Gas Cooktops | Each | 68 | 68 | 100% | 4.2.25 |
| Griddle Dual | Each | 291 | 149 | 51% | 4.2.8 |
| High Efficiency Pre-Rinse Spray Valve | Each | 34 | 34 | 100% | 4.2.11 |
| HVAC - Other - PG SB Custom | Each | 2,308 | 2,308 | 100% | Project File Review† |
| HW Pipe Insulation | LN FT | 2.65 | 2.65 | 100% | 4.4.14 |
| Large Gas Water Heater | MBH | 0.83 | 0.83 | 100% | 4.3.1 |
| Linkageless controls -for new burners | MBH | 0.59 | 0.59 | 100% | 4.4.21 |
| Makeup Air Unit | CFM | 0.17 | 0.17 | 100% | 4.4.37 |
| Ozone Laundry Laundromat | lb-capacity | 12 | 12 | 99% | 4.3.6 |
| Process - Insulation >212 F - PG SB Custom | Each | 1,612 | 1,612 | 100% | Project File Review† |
| Programmable Thermostat | Each | 127 | 127 | 100% | 4.4.48 |
| Smart Thermostat | Each | 132 | 132 | 100% | 4.4.48 |
| Steam Pipe Insulation | LN FT | 8.37 | 8.37 | 99% | 4.4.14 |
| Steam Pipe Insulation - Fitting | LN FT | 7.61 | 7.61 | 100% | 4.4.14 |
| Steam Traps - Dry Cleaner Rep. - Audit | Each | 1,182 | 648 | 54% | 4.4.16 |
| Steam Traps - HVAC Repair/Rep - Audit | Each | 777 | 780 | 100% | 4.4.16 |
| Steam Traps - HVAC Repair/Rep - No Audit | Each | 211 | 211 | 99% | 4.4.16 |
| Steam Traps - Industrial/Process Audit - 15 <= psig < 30 | Each | 758 | 758 | 100% | 4.4.16 |
| Steam Traps-Industrial/Process Audit | Each | 1,532 | 1,603 | 104% | 4.4.16 |
| Tankless Water Heater 0.90 UEF | Each | 0.84 | 0.78 | 92% | 4.3.1 |

* State of Illinois Technical Reference Manual version 13.0 from http://www.ilsag.info/technical-reference-manual.html.

† Project files Review provided by PGL_NSG.

Source: Evaluation team analysis.

## Findings and Recommendations

Finding 1. For the Tankless Water Heater measure under the PGL program, the evaluation team calculated gross realization rates of 94% using IL TRM v13 default values. Evaluators used the 199 MBH value in the tracker file to select the IL TRM v13 gas storage tank capacity default option of 120 gallons for the baseline case. Specifically, the IL TRM v13 “Definition of Draw Pattern” table was used for Commercial Gas Storage Water Heaters >155,000 Btu/h in selecting the gas storage tank capacity value. The building type provided is a large restaurant. Two of the cases yielded a 100% gross realization rate, however, the other case had a realization rate of 83%. For the NSG program, a realization rate of 95% was calculated for all eight installations. The energy savings calculation is quite dependent on the water tank temperature and input water temperature as well as the estimated hot water consumption. The ex ante calculation did not provide these inputs, requiring the evaluation use of IL TRM defaults.

Recommendation 1.    The baseline water storage tank capacity and water tank input and output temperatures should be measured as part of the ex ante energy savings calculation.

Finding 2. For the Steam Traps – Dry Cleaners – Audit measure under both the PGL Program and NSG Program, the evaluation team calculated a combined gross realization rate of 55% using IL TRM v13 default values. The verified gross therms savings was 648 therms per year for one steam trap; the reported ex ante energy savings for that steam trap measure was 648 therms with a 100% gross realization rate. Each of the other forty Steam Trap-Dry Cleaner installations had reported ex ante energy savings of 1,196 therms. The realization rate adjustment for this measure affected the NSG savings the most as the utility had most of this measure installations.

Finding 3. For the Steam Traps – Industrial Process - Audit, the evaluation calculated a gross realization rate of 105%. The evaluation team believes that there is a consistent error in the ex ante energy savings calculation for steam trap measures. The energy savings calculation is quite dependent on the average steam trap inlet and outlet pressure as well as the diameter of the steam trap orifice. These variables have significant impact on the calculated annual energy savings of the steam trap. The ex ante calculation did not provide these inputs, requiring the evaluation use of IL TRM default values.

Recommendation 2.  Carefully review the input assumptions and factors used in its ex ante savings calculations for all steam trap measures, particularly the Steam Traps – Dry Cleaners.

Finding 4. For Custom projects WO-7168172 and WO-7200379, the evaluation team reviewed the input assumptions and found the calculation methods in the ex ante were reasonable and therefore verified a 100% gross realization rate. We observed that some of the ex ante assumptions were hard coded without adequate documentation of sources.

Recommendation 3.  Provide sufficient detail in ex ante energy savings calculations for custom projects, documenting sources of hard coded inputs.

Finding 5. CFS projects completed under both the PGL and NSG programs had a combined realization rate of 71%. CFS projects completed under the PGL program had a realization rate of 72%. CFS projects completed under the NSG program had a gross realization rate of 69%. In all cases, the program tracking data presented for evaluation did not include the manufacturer or model number of the equipment to effectively use the Energy Star Qualified Product List to capture key equipment data inputs for the energy efficient case calculation (e.g., idle energy, preheat energy, and cooking energy). Also, the program data did not provide baseline equipment information to allow calculation of baseline energy performance. Therefore, Guidehouse used the IL TRM v13 default values for both the baseline case and energy efficient case to calculate verified energy savings.

Recommendation 4. The program tracking data should be updated to provide all required information for verifying the ex ante savings. It is important that manufacturer information, including product model numbers for all equipment. Also, equipment installed under the CFS program should be listed on the current Energy Star Qualified Product List. Any custom data inputs used to estimate ex ante savings that are different from Energy Star QPL values should be noted and explained.

# Appendix A. Impact Analysis Methodology

Guidehouse calculated the verified gross savings for each measure by conducting a review of the tracking data and applying the algorithms of the IL TRM v13. The evaluation team checked that the provided savings inputs from the tracking data matched the TRM and that custom inputs were properly used. Then, the tracking data and custom values used for the verified savings were adjusted from the tracking data, as necessary. The savings algorithms were applied to determine the verified savings of each measure. Verified gross realization rates are calculated by dividing the verified savings by the ex ante gross savings.

The evaluation team calculated verified net savings by multiplying the verified gross savings estimates by a NTGR deemed by a consensus process through the SAG. DAC areas were identified by census track and the evaluation used a NTG of 1.00 for projects in DAC areas, based on the Illinois Policy Manual 3.0.

# Appendix B. Program Specific Inputs for the Illinois TRC

Table B-1 shows the Total Resource Cost (TRC) cost-effectiveness analysis inputs available at the time of producing this impact evaluation report. Additional required cost data (e.g., measure costs, program level incentive and non-incentive costs) are not included in this table and will be provided to the evaluation team later. Guidehouse will include annual and lifetime water savings and greenhouse gas reductions in the end of year summary report.

Table B-1. Verified Cost Effectiveness Inputs - PGL

| Program Path | Savings Category | DAC Project | Units | Quantity | Effective Useful Life | Early Replacement Flag† | Verified Gross Annual Water Savings (Gallons) | Ex Ante Gross Savings (Therms) | Verified Gross Savings (Therms) | Verified Net Savings (Therms) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PTA | Boiler Tune Up - Process | No | MBH | 6,000 | 3.00 | NO |  | 6,136 | 6,136 | 5,706 |
|  | Boiler Tune Up (COM) | No | MBH | 16,000 | 3.00 | NO |  | 5,978 | 5,978 | 5,559 |
|  | Steam Pipe Insulation | No | LN FT | 3,137 | 15.00 | NO |  | 24,671 | 24,671 | 22,944 |
|  | Steam Pipe Insulation - Fitting | No | LN FT | 313 | 15.00 | NO |  | 2,210 | 2,210 | 2,056 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | No | Each | 17.00 | 6.00 | NO | 91,519 | 20,326 | 11,016 | 10,245 |
|  | Steam Traps - HVAC Repair/Rep - Audit | No | Each | 520 | 6.00 | NO | 3,079,917 | 403,691 | 405,606 | 377,216 |
|  | Steam Traps - Industrial/Process Audit - 15 <= psig < 30 | No | Each | 5.00 | 6.00 | NO | 68,740 | 3,790 | 3,790 | 3,525 |
| Px | Boiler - HW <=300MBtu >=88% AFUE (COM) | No | MBH | 1,198 | 25.00 | NO |  | 818 | 818 | 761 |
|  | Boiler - HW 300-2500MBtu >88% TE | No | MBH | 5,000 | 25.00 | NO |  | 8,390 | 8,389 | 7,802 |
|  | Boiler Tune Up - Process | No | MBH | 14,999 | 3.00 | NO |  | 15,340 | 15,340 | 14,266 |
|  | Boiler Tune Up (COM) | No | MBH | 722 | 3.00 | NO |  | 306 | 306 | 284 |
|  | Demand Controlled Ventilation (Gas Heating) | No | SQ FT | 153,600 | 6.00 | NO |  | 5,376 | 5,376 | 4,999 |
|  | Large Gas Water Heater | No | MBH | 796 | 15.00 | NO |  | 735 | 735 | 684 |
|  | Linkageless controls -for new burners | No | MBH | 46,200 | 16.00 | NO |  | 27,305 | 27,305 | 25,394 |
|  | Smart Thermostat | No | Each | 4.00 | 11.00 | NO |  | 528 | 528 | 512 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | No | Each | 5.00 | 6.00 | NO | 26,917 | 5,978 | 3,240 | 3,013 |
|  | Tankless Water Heater 0.90 UEF | No | Each | 1,194 | 20.00 | NO |  | 1,132 | 944 | 878 |
| CFS | Combination Oven Gas - <15 Pans | No | Each | 16.00 | 12.00 | NO |  | 9,171 | 7,303 | 5,842 |
|  | Convection Oven | No | Each | 2.00 | 12.00 | NO |  | 563 | 418 | 334 |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) | No | Each | 7.00 | 12.00 | NO |  | 9,537 | 3,587 | 2,869 |
|  | Gas Cooktops | No | Each | 6.00 | 12.00 | NO |  | 407 | 407 | 325 |
|  | Griddle Dual | No | Each | 1.00 | 12.00 | NO |  | 291 | 149 | 119 |
|  | High Efficiency Pre-Rinse Spray Valve | No | Each | 4.00 | 5.00 | NO | 56,160 | 136 | 136 | 109 |
| Custom | HVAC - Other - PG SB Custom | No | Each | 1.00 |  | NO |  | 2,307 | 2,308 | 2,146 |
|  | Process - Insulation >212 F - PG SB Custom | No | Each | 1.00 | 15.00 | NO |  | 1,612 | 1,612 | 1,499 |
|  | Steam Traps-Industrial/Process Audit | No | Each | 4.00 | 6.00 | NO | 54,992 | 6,129 | 6,413 | 5,964 |
| PTA-DAC | Boiler - HW 300-2500MBtu >88% TE | Yes | MBH | 5,663 | 25.00 | NO |  | 6,062 | 6,062 | 6,062 |
|  | Boiler Tune Up (COM) | Yes | MBH | 1,439 | 3.00 | NO |  | 702 | 702 | 702 |
|  | HW Pipe Insulation | Yes | LN FT | 200 | 15.00 | NO |  | 531 | 531 | 531 |
|  | Steam Pipe Insulation | Yes | LN FT | 360 | 15.00 | NO |  | 4,611 | 4,611 | 4,611 |
|  | Steam Pipe Insulation - Fitting | Yes | LN FT | 20.00 | 15.00 | NO |  | 323 | 323 | 323 |
|  | Steam Traps - Dry Cleaner Rep. - Audit | Yes | Each | 23.00 | 6.00 | NO | 123,820 | 27,500 | 14,904 | 14,904 |
|  | Steam Traps - HVAC Repair/Rep - Audit | Yes | Each | 110 | 6.00 | NO | 729,172 | 86,000 | 85,797 | 85,797 |
|  | Steam Traps - HVAC Repair/Rep - No Audit | Yes | Each | 74.00 | 6.00 | NO | 133,629 | 15,620 | 15,584 | 15,584 |
| Px-DAC | Boiler Reset Controls | Yes | MBH | 1,250 | 3.00 | NO |  | 1,678 | 1,678 | 1,678 |
|  | Boiler Tune Up (COM) | Yes | MBH | 3,012 | 3.00 | NO |  | 1,278 | 1,278 | 1,278 |
|  | Demand Controlled Ventilation (Gas Heating) | Yes | SQ FT | 133,203 | 6.00 | NO |  | 4,662 | 4,662 | 4,662 |
|  | Ozone Laundry Laundromat | Yes | lb-capacity | 1,995 | 10.00 | NO | 476,805 | 24,746 | 24,746 | 24,746 |
|  | Smart Thermostat | Yes | Each | 2.00 | 11.00 | NO |  | 240 | 240 | 240 |
|  | Steam Traps - HVAC Repair/Rep - No Audit | Yes | Each | 87.00 | 6.00 | NO | 581,868 | 18,364 | 18,321 | 18,321 |
|  | Tankless Water Heater 0.90 UEF | Yes | Each | 398 | 20.00 | NO |  | 282 | 282 | 282 |
| CFS-DAC | Combination Oven Gas - <15 Pans | Yes | Each | 6.00 | 12.00 | NO |  | 3,398 | 2,738 | 2,738 |
|  | Convection Oven | Yes | Each | 1.00 | 12.00 | NO |  | 540 | 209 | 209 |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) | Yes | Each | 3.00 | 12.00 | NO |  | 2,228 | 1,537 | 1,537 |
|  | Griddle Dual | Yes | Each | 1.00 | 12.00 | NO |  | 291 | 149 | 149 |
| Total or Weighted Average |  |  |  |  | 7.35 |  | 5,423,539 | 761,919 | 729,075 | 689,405 |

Source: Evaluation team analysis.

Table B-2. Verified Cost Effectiveness Inputs – NSG

| Program Path | Savings Category |  | DAC Project | Units |  | Quantity |  | Effective Useful Life |  | Early Replacement Flag† |  | Verified Gross Annual Water Savings (Gallons) |  | Ex Ante Gross Savings (Therms) |  | Verified Gross Savings (Therms) |  | Verified Net Savings (Therms) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PTA | Steam Traps - Dry Cleaner Rep. - Audit |  | No | Each |  | 214 |  | 6.00 |  | NO |  | 1,152,069 |  | 251,499 |  | 138,682 |  | 128,979 |  |
| Px | Boiler Tune Up - Process |  | No | MBH |  | 2,307 |  | 3.00 |  | NO |  |  |  | 2,359 |  | 2,359 |  | 2,194 |  |
|  | DCV - Kitchen |  | No | HP |  | 10.00 |  | 20.00 |  | NO |  |  |  | 2,133 |  | 2,133 |  | 1,983 |  |
|  | Demand Controlled Ventilation (Gas Heating) |  | No | SQ FT |  | 145,300 |  | 6.00 |  | NO |  |  |  | 5,085 |  | 5,085 |  | 4,729 |  |
|  | Energy Star Convection Oven |  | No | Each |  | 1.00 |  | 12.00 |  | NO |  |  |  | 209 |  | 209 |  | 194 |  |
|  | Energy Star Dishwasher |  | No | Each |  | 2.00 |  | 15.00 |  | NO |  | 12,602 |  | 1,222 |  | 1,222 |  | 1,136 |  |
|  | Energy Star Double Rack Oven |  | No | Double Oven |  | 1.00 |  | 12.00 |  | NO |  |  |  | 585 |  | 585 |  | 544 |  |
|  | Energy Star Fryer |  | No | Each |  | 2.00 |  | 12.00 |  | NO |  |  |  | 1,025 |  | 1,025 |  | 953 |  |
|  | Furnace > 95% AFUE (COM) |  | No | Each |  | 1.00 |  | 16.00 |  | NO |  |  |  | 235 |  | 235 |  | 219 |  |
|  | Large Gas Water Heater |  | No | MBH |  | 399 |  | 15.00 |  | NO |  |  |  | 266 |  | 266 |  | 247 |  |
|  | Makeup Air Unit |  | No | CFM |  | 3,800 |  | 15.00 |  | NO |  |  |  | 661 |  | 661 |  | 614 |  |
|  | Programmable Thermostat |  | No | Each |  | 12.00 |  | 11.00 |  | NO |  |  |  | 1,521 |  | 1,521 |  | 1,475 |  |
|  | Smart Thermostat |  | No | Each |  | 1.00 |  | 11.00 |  | NO |  |  |  | 157 |  | 157 |  | 152 |  |
|  | Steam Traps - Dry Cleaner Rep. - Audit |  | No | Each |  | 12.00 |  | 6.00 |  | NO |  | 64,602 |  | 14,348 |  | 7,776 |  | 7,231 |  |
|  | Tankless Water Heater 0.90 UEF |  | No | Each |  | 3,390 |  | 20.00 |  | NO |  |  |  | 2,819 |  | 2,682 |  | 2,494 |  |
| CFS | Combination Oven >30 Pans |  | No | Each |  | 2.00 |  | 12.00 |  | NO |  |  |  | 1,328 |  | 973 |  | 779 |  |
|  | Combination Oven Gas - <15 Pans |  | No | Each |  | 4.00 |  | 12.00 |  | NO |  |  |  | 2,143 |  | 1,825 |  | 1,460 |  |
|  | Dishwasher High Temp - Under Counter - Gas Bldg - Elec Boost |  | No | Each |  | 3.00 |  | 15.00 |  | NO |  | 18,903 |  | 562 |  | 213 |  | 170 |  |
|  | Fryer Large Vat Open Deep-Vat Fryer |  | No | Each |  | 1.00 |  | 12.00 |  | NO |  |  |  | 1,106 |  | 420 |  | 336 |  |
|  | Fryer Standard Open Deep-Vat Fryer (French Fryer) |  | No | Each |  | 1.00 |  | 12.00 |  | NO |  |  |  | 2,228 |  | 512 |  | 409 |  |
| PTA-DAC | Steam Traps - Dry Cleaner Rep. - Audit |  | Yes | Each |  | 51.00 |  | 6.00 |  | NO |  | 274,558 |  | 60,979 |  | 33,048 |  | 33,048 |  |
| Px-DAC | DCV - Kitchen |  | Yes | HP |  | 3.00 |  | 20.00 |  | NO |  |  |  | 693 |  | 693 |  | 693 |  |
|  | Energy Star Dishwasher |  | Yes | Each |  | 1.00 |  | 15.00 |  | NO |  | 6,301 |  | 676 |  | 676 |  | 676 |  |
|  | Energy Star Fryer |  | Yes | Each |  | 1.00 |  | 12.00 |  | NO |  |  |  | 512 |  | 512 |  | 512 |  |
|  | Furnace > 95% AFUE (COM) |  | Yes | Each |  | 1.00 |  | 16.00 |  | NO |  |  |  | 205 |  | 205 |  | 205 |  |
|  | Tankless Water Heater 0.90 UEF |  | Yes | Each |  | 398 |  | 20.00 |  | NO |  |  |  | 331 |  | 314 |  | 314 |  |
| CFS-DAC | Automatic Conveyer Broiler Commercial > 26" Conveyor Width |  | Yes | Each |  | 1.00 |  | 12.00 |  | NO |  |  |  | 862 |  | 1,167 |  | 1,167 |  |
| Total or Weighted Average |  |  |  |  |  |  | 6.77 |  |  |  | 1,529,035 |  | 355,749 |  | 205,156 |  | 192,913 |  |

Source: Evaluation team analysis.

The program did not offer DI measures in 2024. DI delivery path included kits for restaurant and grocery businesses.

Available on the SAG website: www.ilsag.info/technical-reference-manual/il-statewide-technical-reference-manual-version-13-0/

Available on the SAG website www.ilsag.info/evaluator-ntg-recommendations-for-2025/

www.ilsag.info/wp-content/uploads/IL_EE_Policy_Manual_Version_3.0_Final_11-3-2023