## Recip_65% base_60%eff
S fuel CHP = F grid + F thermal CHP – F total CHP
F grid = E CHP X H grid
H CHP = (F total CHP – F thermal CHP) / E CHP
S CHP Elec = S fuel CHP / H CHP
| S CHP gas = S fuel CHP / 100,000 Btu/therm |  |  |  | BASELINE | 65%
2010 - 2015
| Utility | ComEd
SWEEP Method
|  | 100 |  | 633 |  | 1121 |  | 3326 |  | 9341
Units | Assumptions
kW | CHP Capacity (kW) | 100 | 100 | 633 | 633 | 1121 | 1121 | 3326 | 3326 | 9941 | 9941
yrs | Measure Life (years) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Hrs | Operating Hours (Hrs) | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
kWh | E CHP (kWh) | 600000 | 600000 | 3798000 | 3798000 | 6726000 | 6726000 | 19956000 | 19956000 | 59646000 | 59646000
2% | Parasitic Loads (kWh) | 12000 | 12000 | 75960 | 75960 | 134520 | 134520 | 399120 | 399120 | 1192920 | 1192920 |  |  |  | Grid Heat Rate | Losses | eGrid
| Total E CHP (kWh) | 588000 | 588000 | 3722040 | 3722040 | 6591480 | 6591480 | 19556880 | 19556880 | 58453080 | 58453080 |  | >=6500 hrs | ComEd | 10.6222 | 5.82% | 10.038 | RFC West | all Fossil
kBtu/kWh | Grid heat rate (kBtu/kWh) (Hgrid) | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 |  |  | Ameren | 10.9672 | 5.82% | 10.364 | SERC Midwest | all Fossil
kBtu/yr | F grid (Fg) (kBtu/yr) | 6104616.1176 | 6104616.1176 | 38642220.0244 | 38642220.0244 | 68432746.6783 | 68432746.6783 | 203039532.0714 | 203039532.0714 | 606859888.2506 | 606859888.2506 |  | <6500 hrs | ComEd | 10.382 | 5.82% | 9.811 | RFC West | Non Baseload
kBtu/hr | Usable Waste heat from CHP (kBtu/hr) | 670 | 670 | 2780 | 2780 | 4320 | 4320 | 10670 | 10670 | 28532.0854 | 28532.0854 |  |  | Ameren | 11.1227 | 5.82% | 10.511 | SERC Midwest | Non-Baseload
| Thermal Utilization | 63.3% | 63.3% | 59% | 59% | 57.6% | 57.6% | 53.7% | 53.7% | 52.5% | 95.5%
| Displaced thermal Eff | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75%
| Electric Efficiency % (HHV) | 27% | 27% | 34.5% | 34.5% | 36.8% | 36.8% | 40.4% | 40.4% | 41.6% | 41.6%
kBtu/yr | F thermal CHP (Ft) (kBtu/yr) | 3392880 | 3392880 | 13121600 | 13121600 | 19906560 | 19906560 | 45838320 | 45838320 | 119834758.8053 | 217985132.6839
| Total CHP efficiency | 60.02% | 60.02% | 60.01% | 60.01% | 60% | 60% | 59.99% | 59.99% | 59.97% | 75.02%
kBtu/hr | Fuel Use by CHP (kBtu/hr) | 1263.7037 | 1263.7037 | 6260.2783 | 6260.2783 | 10393.6196 | 10393.6196 | 28089.8812 | 28089.8812 | 81535.3173 | 81535.3173 |  | I therm =100 kBtu
kBtu/yr | F total CHP (Fc) (kBtu/yr) | 7582222.2222 | 7582222.2222 | 37561669.5652 | 37561669.5652 | 62361717.3913 | 62361717.3913 | 168539287.1287 | 168539287.1287 | 489211903.8462 | 489211903.8462 |  | 1 kWh = 3.412 btu
kBtu/yr | S fuel CHP [ Fg+Ft-Fc ] | 1915273.8954 | 0 | 14202150.4592 | 0 | 25977589.287 | 0 | 80338564.9427 | 0 | 237482743.2097 | 98150373.8786
| Electric Savings (Claimable) | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0%
| Gas Savings (Claimable) | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
kWh | Electric Savings (Claimable) | 319212.3159 | 0 | 2367025.0765 | 0 | 4329598.2145 | 0 | 13389760.8238 | 0 | 38348056.6994 | 0
Therms | Gas Savings (Claimable) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 981503.7388
| Elec vs Gas | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 70.76% | 29.24%
% therms vs F thermal (therms)
kBtu/kWh | H CHP [ (Fc-Ft)/E ] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.1928 | 4.5473 |  | fixed at 6000 per DCEO compromise proposal
kWh | kW Savings | 95 | 95 | 601.35 | 601.35 | 1064.95 | 1064.95 | 3159.7 | 3159.7 | 9443.95 | 9443.95
$/kW | Cost/kW | 2900 | 2900 | 2737 | 2737 | 2289 | 2289 | 1822 | 1822 | 1480 | 1480
| Installation Cost | 290000 | 290000 | 1732521 | 1732521 | 2565969 | 2565969 | 6059972 | 6059972 | 14712680 | 14712680
0% | Opportunity Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Credit (@10%) | 29000 | 29000 | 173252.1 | 173252.1 | 256596.9 | 256596.9 | 605997.2 | 605997.2 | 1471268 | 1471268
| Total 1 time cost to Cust | 261000 | 261000 | 1559268.9 | 1559268.9 | 2309372.1 | 2309372.1 | 5453974.8 | 5453974.8 | 13241412 | 13241412
$/kWh | Maintenance $ | 0.024 | 0.024 | 0.021 | 0.021 | 0.019 | 0.019 | 0.016 | 0.016 | 0.0085 | 0.0085
$/ kWh/yr | yrly maintenance | 14400 | 14400 | 79758 | 79758 | 127794 | 127794 | 319296 | 319296 | 506991 | 506991
| Design | 7500 | 7500 | 47475 | 47475 | 84075 | 84075 | 195000 | 195000 | 195000 | 195000
| Contruction | 17500 | 17500 | 110775 | 110775 | 196175 | 196175 | 455000 | 455000 | 455000 | 455000
| Production | 35280 | 35280 | 223322.4 | 223322.4 | 395488.8 | 395488.8 | 1173412.8 | 1173412.8 | 1350000 | 1350000
| Total Incentives | 60280 | 60280 | 381572.4 | 381572.4 | 675738.8 | 675738.8 | 1823412.8 | 1823412.8 | 2000000 | 2000000
| CO2 tons/MMBtu from gas on-site | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489
| Avg electric T&D marginal losses | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% |  |  | Com Ed marginal loss rate
| CO2 tons/MWh from electricity | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978
| CO2 tons/yr from on-site fuel | 443.4733 |  | 2196.9283 |  | 3647.4476 |  | 9857.6217
| CO2 tons/yr displaced thermal | 198.4447 |  | 767.4636 |  | 1164.3062 |  | 2681.0177
| CO2 tons/yr displaced electric | 645.4841 |  | 4085.9141 |  | 7235.8763 |  | 21468.7998
| CO2 tons/yr net impact | -400.4554 |  | -2656.4494 |  | -4752.7349 |  | -14292.1959
| Equivalent electricity impact (kWh) | -364792.5754 |  | -2419877.3467 |  | -4329476.6023 |  | -13019393.824
| equiv elec CO2 impact as % of CHP elec output | 0.6204 |  | 0.65015 |  | 0.65683 |  | 0.66572
Check (Alternative Analysis - kWh penalty for increased on-site gas use)
| Added CO2 tons from on-site gas use | 245.0286 |  | 1429.4647 |  | 2483.1414 |  | 7176.6039
| Added CO2 lbs from on-site gas use | 490057.2599 |  | 2858929.3707 |  | 4966282.771 |  | 14353207.8664
| grid MWh equiv from added on-site gas | 247.8049 |  | 1445.661 |  | 2511.2762 |  | 7257.9172
| grid MWh equiv w/losses | 223.2074 |  | 1302.1627 |  | 2262.0034 |  | 6537.4862
| grid kWh equiv from added on-site gas | 223207.4246 |  | 1302162.6533 |  | 2262003.3977 |  | 6537486.176
| grid kWh equiv as % of CHP output | 37.96% |  | 34.99% |  | 34.32% |  | 33.43%
Key CO2 Assumptions
| natural gas CO2 emission rate | 53.06 | kg/MMBtu | From both EPA (http://www.epa.gov/climateleadership/documents/emission-factors.pdf) and EIA (http://www.eia.gov/oiaf/1605/coefficients.html#tbl1)
|  | 2.2046 | kg to lb. conversion
grid marginal CO2 emission rate (lb/MWh) - EGRID Feb 2014 tables (2010 Data)
|  | Con Ed (RFCW) | Ameren (SRMW) | Statewide Wtd Avg
| non-baseload | 1982.87 | 1964.98 | 1977.5932
| all fossil | 2040.18 | 2124.43 | 2065.03
| IL GWh Sales (2012 EIA 861 Data) | 89977 | 37642 | 127619
|  | 70.5% | 29.5% | 100%
Note on B21: raikar: From ICF draft paper, Table 3, Total Heat Recovered
Note on B24: raikar: From ICF draft paper, Table 3, Electrical Efficiency
Note on B42: raikar: $40,000/Mmbtu of steam, DOE Boiler MACT rule of thumb

## Recip_65% base_65%eff
S fuel CHP = F grid + F thermal CHP – F total CHP
F grid = E CHP X H grid
H CHP = (F total CHP – F thermal CHP) / E CHP
S CHP Elec = S fuel CHP / H CHP
| S CHP gas = S fuel CHP / 100,000 Btu/therm |  |  |  | BASELINE | 65%
2010 - 2015
| Utility | ComEd
SWEEP Method
|  | 100 |  | 633 |  | 1121 |  | 3326 |  | 9341
Units | Assumptions
kW | CHP Capacity (kW) | 100 | 100 | 633 | 633 | 1121 | 1121 | 3326 | 3326 | 9941 | 9941
yrs | Measure Life (years) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Hrs | Operating Hours (Hrs) | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
kWh | E CHP (kWh) | 600000 | 600000 | 3798000 | 3798000 | 6726000 | 6726000 | 19956000 | 19956000 | 59646000 | 59646000
2% | Parasitic Loads (kWh) | 12000 | 12000 | 75960 | 75960 | 134520 | 134520 | 399120 | 399120 | 1192920 | 1192920 |  |  | Grid Heat Rate | Losses | eGrid
| Total E CHP (kWh) | 588000 | 588000 | 3722040 | 3722040 | 6591480 | 6591480 | 19556880 | 19556880 | 58453080 | 58453080 | >=6500 hrs | ComEd | 10.6222 | 5.82% | 10.038 | RFC West | all Fossil
kBtu/kWh | Grid heat rate (kBtu/kWh) (Hgrid) | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 |  | Ameren | 10.9672 | 5.82% | 10.364 | SERC Midwest | all Fossil
kBtu/yr | F grid (Fg) (kBtu/yr) | 6104616.1176 | 6104616.1176 | 38642220.0244 | 38642220.0244 | 68432746.6783 | 68432746.6783 | 203039532.0714 | 203039532.0714 | 606859888.2506 | 606859888.2506 | <6500 hrs | ComEd | 10.382 | 5.82% | 9.811 | RFC West | Non Baseload
kBtu/hr | Usable Waste heat from CHP (kBtu/hr) | 670 | 670 | 2780 | 2780 | 4320 | 4320 | 10670 | 10670 | 28532.0854 | 28532.0854 |  | Ameren | 11.1227 | 5.82% | 10.511 | SERC Midwest | Non-Baseload
| Thermal Utilization | 72.7% | 72.7% | 70.2% | 70.2% | 69.6% | 69.6% | 66.9% | 66.9% | 52.5% | 95.5%
| Displaced thermal Eff | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75%
| Electric Efficiency % (HHV) | 27% | 27% | 34.5% | 34.5% | 36.8% | 36.8% | 40.4% | 40.4% | 41.6% | 41.6%
kBtu/yr | F thermal CHP (Ft) (kBtu/yr) | 3896720 | 3896720 | 15612480 | 15612480 | 24053760 | 24053760 | 57105840 | 57105840 | 119834758.8053 | 217985132.6839
| Total CHP efficiency | 65% | 65% | 64.98% | 64.98% | 64.99% | 64.99% | 65% | 65% | 59.97% | 75.02%
kBtu/hr | Fuel Use by CHP (kBtu/hr) | 1263.7037 | 1263.7037 | 6260.2783 | 6260.2783 | 10393.6196 | 10393.6196 | 28089.8812 | 28089.8812 | 81535.3173 | 81535.3173 | I therm =100 kBtu
kBtu/yr | F total CHP (Fc) (kBtu/yr) | 7582222.2222 | 7582222.2222 | 37561669.5652 | 37561669.5652 | 62361717.3913 | 62361717.3913 | 168539287.1287 | 168539287.1287 | 489211903.8462 | 489211903.8462 | 1 kWh = 3.412 btu
kBtu/yr | S fuel CHP [ Fg+Ft-Fc ] | 2419113.8954 | 0 | 16693030.4592 | 0 | 30124789.287 | 0 | 91606084.9427 | 0 | 237482743.2097 | 98150373.8786
| Electric Savings (Claimable) | 99.99% | 0% | 100% | 0% | 100% | 0% | 99.99% | 0% | 100% | 0%
| Gas Savings (Claimable) | 0.007133% | 100% | 0% | 100% | 0% | 100% | 0.006314% | 100% | 0% | 100%
kWh | Electric Savings (Claimable) | 403156.8913 | 0 | 2782171.7432 | 0 | 5020798.2145 | 0 | 15266716.7571 | 0 | 38348056.6994 | 0
Therms | Gas Savings (Claimable) | 1.7255 | 0 | 0 | 0 | 0 | 0 | 57.844 | 0 | 0 | 981503.7388
| Elec vs Gas | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 70.76% | 29.24%
% therms vs F thermal (therms)
kBtu/kWh | H CHP [ (Fc-Ft)/E ] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.1928 | 4.5473 | fixed at 6000 per DCEO compromise proposal
kWh | kW Savings | 95 | 95 | 601.35 | 601.35 | 1064.95 | 1064.95 | 3159.7 | 3159.7 | 9443.95 | 9443.95
$/kW | Cost/kW | 2900 | 2900 | 2737 | 2737 | 2289 | 2289 | 1822 | 1822 | 1480 | 1480
| Installation Cost | 290000 | 290000 | 1732521 | 1732521 | 2565969 | 2565969 | 6059972 | 6059972 | 14712680 | 14712680
0% | Opportunity Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Credit (@10%) | 29000 | 29000 | 173252.1 | 173252.1 | 256596.9 | 256596.9 | 605997.2 | 605997.2 | 1471268 | 1471268
| Total 1 time cost to Cust | 261000 | 261000 | 1559268.9 | 1559268.9 | 2309372.1 | 2309372.1 | 5453974.8 | 5453974.8 | 13241412 | 13241412
$/kWh | Maintenance $ | 0.024 | 0.024 | 0.021 | 0.021 | 0.019 | 0.019 | 0.016 | 0.016 | 0.0085 | 0.0085
$/ kWh/yr | yrly maintenance | 14400 | 14400 | 79758 | 79758 | 127794 | 127794 | 319296 | 319296 | 506991 | 506991
| Design | 7500 | 7500 | 47475 | 47475 | 84075 | 84075 | 195000 | 195000 | 195000 | 195000
| Contruction | 17500 | 17500 | 110775 | 110775 | 196175 | 196175 | 455000 | 455000 | 455000 | 455000
| Production | 35280 | 35280 | 223322.4 | 223322.4 | 395488.8 | 395488.8 | 1173412.8 | 1173412.8 | 1350000 | 1350000
| Total Incentives | 60280 | 60280 | 381572.4 | 381572.4 | 675738.8 | 675738.8 | 1823412.8 | 1823412.8 | 2000000 | 2000000
| CO2 tons/MMBtu from gas on-site | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489
| Avg electric T&D marginal losses | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02%
| CO2 tons/MWh from electricity | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978
| CO2 tons/yr from on-site fuel | 443.4733 |  | 2196.9283 |  | 3647.4476 |  | 9857.6217
| CO2 tons/yr displaced thermal | 227.9136 |  | 913.1516 |  | 1406.87 |  | 3340.0388
| CO2 tons/yr displaced electric | 645.4841 |  | 4085.9141 |  | 7235.8763 |  | 21468.7998
| CO2 tons/yr net impact | -429.9243 |  | -2802.1374 |  | -4995.2987 |  | -14951.217
| Equivalent electricity impact (kWh) | -391637.083 |  | -2552590.9996 |  | -4550438.6966 |  | -13619725.3288
| equiv elec CO2 impact as % of CHP elec output | 0.66605 |  | 0.6858 |  | 0.69035 |  | 0.69642
Note on B21: raikar: From ICF draft paper, Table 3, Total Heat Recovered
Note on B24: raikar: From ICF draft paper, Table 3, Electrical Efficiency
Note on B42: raikar: $40,000/Mmbtu of steam, DOE Boiler MACT rule of thumb

## Recip_65% base_70%eff
S fuel CHP = F grid + F thermal CHP – F total CHP
F grid = E CHP X H grid
H CHP = (F total CHP – F thermal CHP) / E CHP
S CHP Elec = S fuel CHP / H CHP
| S CHP gas = S fuel CHP / 100,000 Btu/therm |  |  |  | BASELINE | 65%
2010 - 2015
| Utility | ComEd
SWEEP Method
|  | 100 |  | 633 |  | 1121 |  | 3326 |  | 9341
Units | Assumptions
kW | CHP Capacity (kW) | 100 | 100 | 633 | 633 | 1121 | 1121 | 3326 | 3326 | 9941 | 9941
yrs | Measure Life (years) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Hrs | Operating Hours (Hrs) | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
kWh | E CHP (kWh) | 600000 | 600000 | 3798000 | 3798000 | 6726000 | 6726000 | 19956000 | 19956000 | 59646000 | 59646000
2% | Parasitic Loads (kWh) | 12000 | 12000 | 75960 | 75960 | 134520 | 134520 | 399120 | 399120 | 1192920 | 1192920 |  |  | Grid Heat Rate | Losses | eGrid
| Total E CHP (kWh) | 588000 | 588000 | 3722040 | 3722040 | 6591480 | 6591480 | 19556880 | 19556880 | 58453080 | 58453080 | >=6500 hrs | ComEd | 10.6222 | 5.82% | 10.038 | RFC West | all Fossil
kBtu/kWh | Grid heat rate (kBtu/kWh) (Hgrid) | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 |  | Ameren | 10.9672 | 5.82% | 10.364 | SERC Midwest | all Fossil
kBtu/yr | F grid (Fg) (kBtu/yr) | 6104616.1176 | 6104616.1176 | 38642220.0244 | 38642220.0244 | 68432746.6783 | 68432746.6783 | 203039532.0714 | 203039532.0714 | 606859888.2506 | 606859888.2506 | <6500 hrs | ComEd | 10.382 | 5.82% | 9.811 | RFC West | Non Baseload
kBtu/hr | Usable Waste heat from CHP (kBtu/hr) | 670 | 670 | 2780 | 2780 | 4320 | 4320 | 10670 | 10670 | 28532.0854 | 28532.0854 |  | Ameren | 11.1227 | 5.82% | 10.511 | SERC Midwest | Non-Baseload
| Thermal Utilization | 72.7% | 82.15% | 70.2% | 81.5% | 69.6% | 81.7% | 66.9% | 80.1% | 52.5% | 95.5%
| Displaced thermal Eff | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75%
| Electric Efficiency % (HHV) | 27% | 27% | 34.5% | 34.5% | 36.8% | 36.8% | 40.4% | 40.4% | 41.6% | 41.6%
kBtu/yr | F thermal CHP (Ft) (kBtu/yr) | 3896720 | 4403240 | 15612480 | 18125600 | 24053760 | 28235520 | 57105840 | 68373360 | 119834758.8053 | 217985132.6839
| Total CHP efficiency | 65% | 70.01% | 64.98% | 70% | 64.99% | 70.02% | 65% | 70.02% | 59.97% | 75.02%
kBtu/hr | Fuel Use by CHP (kBtu/hr) | 1263.7037 | 1263.7037 | 6260.2783 | 6260.2783 | 10393.6196 | 10393.6196 | 28089.8812 | 28089.8812 | 81535.3173 | 81535.3173 | I therm =100 kBtu
kBtu/yr | F total CHP (Fc) (kBtu/yr) | 7582222.2222 | 7582222.2222 | 37561669.5652 | 37561669.5652 | 62361717.3913 | 62361717.3913 | 168539287.1287 | 168539287.1287 | 489211903.8462 | 489211903.8462 | 1 kWh = 3.412 btu
kBtu/yr | S fuel CHP [ Fg+Ft-Fc ] | 2419113.8954 | 506520 | 16693030.4592 | 2513120 | 30124789.287 | 4181760 | 91606084.9427 | 11267520 | 237482743.2097 | 98150373.8786
| Electric Savings (Claimable) | 99.99% | 0% | 100% | 0% | 100% | 0% | 99.99% | 0% | 100% | 0%
| Gas Savings (Claimable) | 0.007133% | 100% | 0% | 100% | 0% | 100% | 0.006314% | 100% | 0% | 100%
kWh | Electric Savings (Claimable) | 403156.8913 | 0 | 2782171.7432 | 0 | 5020798.2145 | 0 | 15266716.7571 | 0 | 38348056.6994 | 0
Therms | Gas Savings (Claimable) | 1.7255 | 5065.2 | 0 | 25131.2 | 0 | 41817.6 | 57.844 | 112675.2 | 0 | 981503.7388
| Elec vs Gas | 82.69% | 17.31% | 86.92% | 13.08% | 87.81% | 12.19% | 89.05% | 10.95% | 70.76% | 29.24%
| % therms vs F thermal (therms) |  | 11.51% |  | 13.87% |  | 14.81% |  | 16.49%
kBtu/kWh | H CHP [ (Fc-Ft)/E ] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.1928 | 4.5473 | fixed at 6000 per DCEO compromise proposal
kWh | kW Savings | 95 | 95 | 601.35 | 601.35 | 1064.95 | 1064.95 | 3159.7 | 3159.7 | 9443.95 | 9443.95
$/kW | Cost/kW | 2900 | 2900 | 2737 | 2737 | 2289 | 2289 | 1822 | 1822 | 1480 | 1480
| Installation Cost | 290000 | 290000 | 1732521 | 1732521 | 2565969 | 2565969 | 6059972 | 6059972 | 14712680 | 14712680
0% | Opportunity Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Credit (@10%) | 29000 | 29000 | 173252.1 | 173252.1 | 256596.9 | 256596.9 | 605997.2 | 605997.2 | 1471268 | 1471268
| Total 1 time cost to Cust | 261000 | 261000 | 1559268.9 | 1559268.9 | 2309372.1 | 2309372.1 | 5453974.8 | 5453974.8 | 13241412 | 13241412
$/kWh | Maintenance $ | 0.024 | 0.024 | 0.021 | 0.021 | 0.019 | 0.019 | 0.016 | 0.016 | 0.0085 | 0.0085
$/ kWh/yr | yrly maintenance | 14400 | 14400 | 79758 | 79758 | 127794 | 127794 | 319296 | 319296 | 506991 | 506991
| Design | 7500 | 7500 | 47475 | 47475 | 84075 | 84075 | 195000 | 195000 | 195000 | 195000
| Contruction | 17500 | 17500 | 110775 | 110775 | 196175 | 196175 | 455000 | 455000 | 455000 | 455000
| Production | 35280 | 47040 | 223322.4 | 297763.2 | 395488.8 | 527318.4 | 1173412.8 | 1350000 | 1350000 | 1350000
| Total Incentives | 60280 | 72040 | 381572.4 | 456013.2 | 675738.8 | 807568.4 | 1823412.8 | 2000000 | 2000000 | 2000000
| CO2 tons/MMBtu from gas on-site | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489
| Avg electric T&D marginal losses | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02%
| CO2 tons/MWh from electricity | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978
| CO2 tons/yr from on-site fuel | 443.4733 | 443.4733 | 2196.9283 | 2196.9283 | 3647.4476 | 3647.4476 | 9857.6217 | 9857.6217
| CO2 tons/yr displaced thermal | 227.9136 | 257.5392 | 913.1516 | 1060.1404 | 1406.87 | 1651.4551 | 3340.0388 | 3999.06
| CO2 tons/yr displaced electric | 645.4841 | 645.4841 | 4085.9141 | 4085.9141 | 7235.8763 | 7235.8763 | 21468.7998 | 21468.7998
| CO2 tons/yr net impact | -429.9243 | -459.5499 | -2802.1374 | -2949.1262 | -4995.2987 | -5239.8839 | -14951.217 | -15610.2381
| Equivalent electricity impact (kWh) | -391637.083 | -418624.3804 | -2552590.9996 | -2686489.5959 | -4550438.6966 | -4773242.1417 | -13619725.3288 | -14220056.8336
| equiv elec CO2 impact as % of CHP elec output | 0.66605 | 0.71195 | 0.6858 | 0.72178 | 0.69035 | 0.72415 | 0.69642 | 0.72711
Note on B21: raikar: From ICF draft paper, Table 3, Total Heat Recovered
Note on B24: raikar: From ICF draft paper, Table 3, Electrical Efficiency
Note on B42: raikar: $40,000/Mmbtu of steam, DOE Boiler MACT rule of thumb

## Recip_65% base_75%eff
S fuel CHP = F grid + F thermal CHP – F total CHP
F grid = E CHP X H grid
H CHP = (F total CHP – F thermal CHP) / E CHP
S CHP Elec = S fuel CHP / H CHP
| S CHP gas = S fuel CHP / 100,000 Btu/therm |  |  |  | BASELINE | 65%
2010 - 2015
| Utility | ComEd
SWEEP Method
|  | 100 |  | 633 |  | 1121 |  | 3326 |  | 9341
Units | Assumptions
kW | CHP Capacity (kW) | 100 | 100 | 633 | 633 | 1121 | 1121 | 3326 | 3326 | 9941 | 9941
yrs | Measure Life (years) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Hrs | Operating Hours (Hrs) | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
kWh | E CHP (kWh) | 600000 | 600000 | 3798000 | 3798000 | 6726000 | 6726000 | 19956000 | 19956000 | 59646000 | 59646000
2% | Parasitic Loads (kWh) | 12000 | 12000 | 75960 | 75960 | 134520 | 134520 | 399120 | 399120 | 1192920 | 1192920 |  |  | Grid Heat Rate | Losses | eGrid
| Total E CHP (kWh) | 588000 | 588000 | 3722040 | 3722040 | 6591480 | 6591480 | 19556880 | 19556880 | 58453080 | 58453080 | >=6500 hrs | ComEd | 10.6222 | 5.82% | 10.038 | RFC West | all Fossil
kBtu/kWh | Grid heat rate (kBtu/kWh) (Hgrid) | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 |  | Ameren | 10.9672 | 5.82% | 10.364 | SERC Midwest | all Fossil
kBtu/yr | F grid (Fg) (kBtu/yr) | 6104616.1176 | 6104616.1176 | 38642220.0244 | 38642220.0244 | 68432746.6783 | 68432746.6783 | 203039532.0714 | 203039532.0714 | 606859888.2506 | 606859888.2506 | <6500 hrs | ComEd | 10.382 | 5.82% | 9.811 | RFC West | Non Baseload
kBtu/hr | Usable Waste heat from CHP (kBtu/hr) | 670 | 670 | 2780 | 2780 | 4320 | 4320 | 10670 | 10670 | 28532.0854 | 28532.0854 |  | Ameren | 11.1227 | 5.82% | 10.511 | SERC Midwest | Non-Baseload
| Thermal Utilization | 72.7% | 91.6% | 70.2% | 92.8% | 69.6% | 93.7% | 66.9% | 93.2% | 52.5% | 95.5%
| Displaced thermal Eff | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75%
| Electric Efficiency % (HHV) | 27% | 27% | 34.5% | 34.5% | 36.8% | 36.8% | 40.4% | 40.4% | 41.6% | 41.6%
kBtu/yr | F thermal CHP (Ft) (kBtu/yr) | 3896720 | 4909760 | 15612480 | 20638720 | 24053760 | 32382720 | 57105840 | 79555520 | 119834758.8053 | 217985132.6839
| Total CHP efficiency | 65% | 75.03% | 64.98% | 75.02% | 64.99% | 75.01% | 65% | 74.99% | 59.97% | 75.02%
kBtu/hr | Fuel Use by CHP (kBtu/hr) | 1263.7037 | 1263.7037 | 6260.2783 | 6260.2783 | 10393.6196 | 10393.6196 | 28089.8812 | 28089.8812 | 81535.3173 | 81535.3173 | I therm =100 kBtu
kBtu/yr | F total CHP (Fc) (kBtu/yr) | 7582222.2222 | 7582222.2222 | 37561669.5652 | 37561669.5652 | 62361717.3913 | 62361717.3913 | 168539287.1287 | 168539287.1287 | 489211903.8462 | 489211903.8462 | 1 kWh = 3.412 btu
kBtu/yr | S fuel CHP [ Fg+Ft-Fc ] | 2419113.8954 | 1013040 | 16693030.4592 | 5026240 | 30124789.287 | 8328960 | 91606084.9427 | 22449680 | 237482743.2097 | 98150373.8786
| Electric Savings (Claimable) | 99.99% | 0% | 100% | 0% | 100% | 0% | 99.99% | 0% | 100% | 0%
| Gas Savings (Claimable) | 0.007133% | 100% | 0% | 100% | 0% | 100% | 0.006314% | 100% | 0% | 100%
kWh | Electric Savings (Claimable) | 403156.8913 | 0 | 2782171.7432 | 0 | 5020798.2145 | 0 | 15266716.7571 | 0 | 38348056.6994 | 0
Therms | Gas Savings (Claimable) | 1.7255 | 10130.4 | 0 | 50262.4 | 0 | 83289.6 | 57.844 | 224496.8 | 0 | 981503.7388
| Elec vs Gas | 70.48% | 29.52% | 76.86% | 23.14% | 78.34% | 21.66% | 80.32% | 19.68% | 70.76% | 29.24%
| % therms vs F thermal (therms) |  | 20.64% |  | 24.35% |  | 25.72% |  | 28.23%
kBtu/kWh | H CHP [ (Fc-Ft)/E ] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.1928 | 4.5473 | fixed at 6000 per DCEO compromise proposal
kWh | kW Savings | 95 | 95 | 601.35 | 601.35 | 1064.95 | 1064.95 | 3159.7 | 3159.7 | 9443.95 | 9443.95
$/kW | Cost/kW | 2900 | 2900 | 2737 | 2737 | 2289 | 2289 | 1822 | 1822 | 1480 | 1480
| Installation Cost | 290000 | 290000 | 1732521 | 1732521 | 2565969 | 2565969 | 6059972 | 6059972 | 14712680 | 14712680
0% | Opportunity Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Credit (@10%) | 29000 | 29000 | 173252.1 | 173252.1 | 256596.9 | 256596.9 | 605997.2 | 605997.2 | 1471268 | 1471268
| Total 1 time cost to Cust | 261000 | 261000 | 1559268.9 | 1559268.9 | 2309372.1 | 2309372.1 | 5453974.8 | 5453974.8 | 13241412 | 13241412
$/kWh | Maintenance $ | 0.024 | 0.024 | 0.021 | 0.021 | 0.019 | 0.019 | 0.016 | 0.016 | 0.0085 | 0.0085
$/ kWh/yr | yrly maintenance | 14400 | 14400 | 79758 | 79758 | 127794 | 127794 | 319296 | 319296 | 506991 | 506991
| Design | 7500 | 7500 | 47475 | 47475 | 84075 | 84075 | 195000 | 195000 | 195000 | 195000
| Contruction | 17500 | 17500 | 110775 | 110775 | 196175 | 196175 | 455000 | 455000 | 455000 | 455000
| Production | 35280 | 47040 | 223322.4 | 297763.2 | 395488.8 | 527318.4 | 1173412.8 | 1350000 | 1350000 | 1350000
| Total Incentives | 60280 | 72040 | 381572.4 | 456013.2 | 675738.8 | 807568.4 | 1823412.8 | 2000000 | 2000000 | 2000000
| CO2 tons/MMBtu from gas on-site | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489
| Avg electric T&D marginal losses | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02%
| CO2 tons/MWh from electricity | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978
| CO2 tons/yr from on-site fuel | 443.4733 | 443.4733 | 2196.9283 | 2196.9283 | 3647.4476 | 3647.4476 | 9857.6217 | 9857.6217
| CO2 tons/yr displaced thermal | 227.9136 | 287.1648 | 913.1516 | 1207.1292 | 1406.87 | 1894.0189 | 3340.0388 | 4653.0885
| CO2 tons/yr displaced electric | 645.4841 | 645.4841 | 4085.9141 | 4085.9141 | 7235.8763 | 7235.8763 | 21468.7998 | 21468.7998
| CO2 tons/yr net impact | -429.9243 | -489.1756 | -2802.1374 | -3096.115 | -4995.2987 | -5482.4477 | -14951.217 | -16264.2666
| Equivalent electricity impact (kWh) | -391637.083 | -445611.6779 | -2552590.9996 | -2820388.1921 | -4550438.6966 | -4994204.236 | -13619725.3288 | -14815840.3725
| equiv elec CO2 impact as % of CHP elec output | 0.66605 | 0.75784 | 0.6858 | 0.75775 | 0.69035 | 0.75768 | 0.69642 | 0.75758
Note on B21: raikar: From ICF draft paper, Table 3, Total Heat Recovered
Note on B24: raikar: From ICF draft paper, Table 3, Electrical Efficiency
Note on B42: raikar: $40,000/Mmbtu of steam, DOE Boiler MACT rule of thumb

## Recip_65% base_MaxEff
S fuel CHP = F grid + F thermal CHP – F total CHP
F grid = E CHP X H grid
H CHP = (F total CHP – F thermal CHP) / E CHP
S CHP Elec = S fuel CHP / H CHP
| S CHP gas = S fuel CHP / 100,000 Btu/therm |  |  |  | BASELINE | 65%
2010 - 2015
| Utility | ComEd
SWEEP Method
|  | 100 |  | 633 |  | 1121 |  | 3326 |  | 9341
Units | Assumptions
kW | CHP Capacity (kW) | 100 | 100 | 633 | 633 | 1121 | 1121 | 3326 | 3326 | 9941 | 9941
yrs | Measure Life (years) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Hrs | Operating Hours (Hrs) | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
kWh | E CHP (kWh) | 600000 | 600000 | 3798000 | 3798000 | 6726000 | 6726000 | 19956000 | 19956000 | 59646000 | 59646000
2% | Parasitic Loads (kWh) | 12000 | 12000 | 75960 | 75960 | 134520 | 134520 | 399120 | 399120 | 1192920 | 1192920 |  |  | Grid Heat Rate | Losses | eGrid
| Total E CHP (kWh) | 588000 | 588000 | 3722040 | 3722040 | 6591480 | 6591480 | 19556880 | 19556880 | 58453080 | 58453080 | >=6500 hrs | ComEd | 10.6222 | 5.82% | 10.038 | RFC West | all Fossil
kBtu/kWh | Grid heat rate (kBtu/kWh) (Hgrid) | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 | 10.382 |  | Ameren | 10.9672 | 5.82% | 10.364 | SERC Midwest | all Fossil
kBtu/yr | F grid (Fg) (kBtu/yr) | 6104616.1176 | 6104616.1176 | 38642220.0244 | 38642220.0244 | 68432746.6783 | 68432746.6783 | 203039532.0714 | 203039532.0714 | 606859888.2506 | 606859888.2506 | <6500 hrs | ComEd | 10.382 | 5.82% | 9.811 | RFC West | Non Baseload
kBtu/hr | Usable Waste heat from CHP (kBtu/hr) | 670 | 670 | 2780 | 2780 | 4320 | 4320 | 10670 | 10670 | 28532.0854 | 28532.0854 |  | Ameren | 11.1227 | 5.82% | 10.511 | SERC Midwest | Non-Baseload
| Thermal Utilization | 72.7% | 100% | 70.2% | 100% | 69.6% | 100% | 66.9% | 100% | 52.5% | 95.5% | [9 empty] | Electric Avoided Costs ($/kWh) | 0.02917 | 0.029937 | 0.030725 | 0.031533 | 0.032362 | 0.033213 | 0.034086 | 0.034983 | 0.035903 | 0.036847 | 0.037816 | 0.038811 | 0.039832 | 0.040879 | 0.041954 | 0.043058 | 0.04419 | 0.045352 | 0.046545 | 0.047769 | 0.049026 | 0.050315 | 0.051638 | 0.052996 | 0.05439
| Displaced thermal Eff | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | [9 empty] | Avoided Electric Capacity ($/kW) | 35.16 | 36.039 | 36.94 | 37.8635 | 38.8101 | 39.7803 | 40.7748 | 41.7942 | 42.839 | 43.91 | 45.0078 | 46.133 | 47.2863 | 48.4684 | 49.6802 | 50.9222 | 52.1952 | 53.5001 | 54.8376 | 56.2085 | 57.6138 | 59.0541 | 60.5305 | 62.0437 | 63.5948
| Electric Efficiency % (HHV) | 27% | 27% | 34.5% | 34.5% | 36.8% | 36.8% | 40.4% | 40.4% | 41.6% | 41.6%
kBtu/yr | F thermal CHP (Ft) (kBtu/yr) | 3896720 | 5360000 | 15612480 | 22240000 | 24053760 | 34560000 | 57105840 | 85360000 | 119834758.8053 | 217985132.6839 | [13 empty] | 1.0263 | 1.0533 | 1.081 | 1.1094 | 1.1386 | 1.1685 | 1.1993 | 1.2308 | 1.2632 | 1.2964 | 1.3305 | 1.3655 | 1.4014 | 1.4383 | 1.4761 | 1.5149 | 1.5548 | 1.5957 | 1.6376 | 1.6807 | 1.7249 | 1.7703
| Total CHP efficiency | 65% | 79.48% | 64.98% | 78.22% | 64.99% | 77.63% | 65% | 77.58% | 59.97% | 75.02% | [13 empty] | 1.025 | 1.0506 | 1.0769 | 1.1038 | 1.1314 | 1.1597 | 1.1887 | 1.2184 | 1.2489 | 1.2801 | 1.3121 | 1.3449 | 1.3785 | 1.413 | 1.4483 | 1.4845 | 1.5216 | 1.5597 | 1.5987 | 1.6386 | 1.6796 | 1.7216
kBtu/hr | Fuel Use by CHP (kBtu/hr) | 1263.7037 | 1263.7037 | 6260.2783 | 6260.2783 | 10393.6196 | 10393.6196 | 28089.8812 | 28089.8812 | 81535.3173 | 81535.3173 | I therm =100 kBtu
kBtu/yr | F total CHP (Fc) (kBtu/yr) | 7582222.2222 | 7582222.2222 | 37561669.5652 | 37561669.5652 | 62361717.3913 | 62361717.3913 | 168539287.1287 | 168539287.1287 | 489211903.8462 | 489211903.8462 | 1 kWh = 3.412 btu
kBtu/yr | S fuel CHP [ Fg+Ft-Fc ] | 2419113.8954 | 1463280 | 16693030.4592 | 6627520 | 30124789.287 | 10506240 | 91606084.9427 | 28254160 | 237482743.2097 | 98150373.8786 | [10 empty] | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
| Electric Savings (Claimable) | 99.99% | 0% | 100% | 0% | 100% | 0% | 99.99% | 0% | 100% | 0%
| Gas Savings (Claimable) | 0.007133% | 100% | 0% | 100% | 0% | 100% | 0.006314% | 100% | 0% | 100%
kWh | Electric Savings (Claimable) | 403156.8913 | 0 | 2782171.7432 | 0 | 5020798.2145 | 0 | 15266716.7571 | 0 | 38348056.6994 | 0
Therms | Gas Savings (Claimable) | 1.7255 | 14632.8 | 0 | 66275.2 | 0 | 105062.4 | 57.844 | 282541.6 | 0 | 981503.7388
| Elec vs Gas | 62.31% | 37.69% | 71.58% | 28.42% | 74.14% | 25.86% | 76.43% | 23.57% | 70.76% | 29.24%
| % therms vs F thermal (therms) |  | 27.3% |  | 29.8% |  | 30.4% |  | 33.11%
kBtu/kWh | H CHP [ (Fc-Ft)/E ] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.1928 | 4.5473 | fixed at 6000 per DCEO compromise proposal | [9 empty] | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25
kWh | kW Savings | 95 | 95 | 601.35 | 601.35 | 1064.95 | 1064.95 | 3159.7 | 3159.7 | 9443.95 | 9443.95 | [8 empty] | Avoided Electric Capacity ($/kW) |  | 1 | 4.5435 | 4.9044 | 2.141 | 1.1275 | 1.1613 | 1.1829 | 1.1882 | 1.2037 | 1.2165 | 1.2558 | 1.2975 | 1.3313 | 1.3636 | 1.391 | 1.4304 | 1.4703 | 1.5106 | 1.5576 | 1.6115 | 1.6735 | 1.7346 | 1.7878 | 1.8439 | 1.898
[20 empty] | Avoided Ancillary ($/kW/Mth) |  | 1.0488 | 1.0379 | 1.0603 | 1.1906 | 1.2539 | 1.2915 | 1.3155 | 1.3214 | 1.3386 | 1.3528 | 1.3966 | 1.4429 | 1.4805 | 1.5164 | 1.5469 | 1.5908 | 1.6351 | 1.6799 | 1.7322 | 1.7921 | 1.861 | 1.929 | 1.9881 | 2.0506 | 2.1107
$/kW | Cost/kW | 2900 | 2900 | 2737 | 2737 | 2289 | 2289 | 1822 | 1822 | 1480 | 1480 | [7 empty] | Electric Avoided Costs ($/kWh) | 0.031166 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Installation Cost | 290000 | 290000 | 1732521 | 1732521 | 2565969 | 2565969 | 6059972 | 6059972 | 14712680 | 14712680 | [7 empty] | Avoided Electric Capacity ($/kW) | 6.18 |  | 6.18 | 28.0786 | 30.3094 | 13.2314 | 6.9679 | 7.1771 | 7.3102 | 7.3431 | 7.4387 | 7.5177 | 7.761 | 8.0184 | 8.2276 | 8.4269 | 8.5961 | 8.8402 | 9.0868 | 9.3352 | 9.626 | 9.9592 | 10.342 | 10.7199 | 11.0483 | 11.3956 | 11.7295
0% | Opportunity Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | Avoided Electric T&D ($/kW) | 42 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Tax Credit (@10%) | 29000 | 29000 | 173252.1 | 173252.1 | 256596.9 | 256596.9 | 605997.2 | 605997.2 | 1471268 | 1471268 | [7 empty] | Avoided Ancillary ($/kW/Mth) | 0.84345 |  | 0.88458 | 0.87538 | 0.89432 | 1.0042 | 1.0576 | 1.0893 | 1.1095 | 1.1145 | 1.129 | 1.141 | 1.178 | 1.217 | 1.2488 | 1.279 | 1.3047 | 1.3417 | 1.3792 | 1.4169 | 1.461 | 1.5116 | 1.5697 | 1.627 | 1.6769 | 1.7296 | 1.7803
| Total 1 time cost to Cust | 261000 | 261000 | 1559268.9 | 1559268.9 | 2309372.1 | 2309372.1 | 5453974.8 | 5453974.8 | 13241412 | 13241412
$/kWh | Maintenance $ | 0.024 | 0.024 | 0.021 | 0.021 | 0.019 | 0.019 | 0.016 | 0.016 | 0.0085 | 0.0085
$/ kWh/yr | yrly maintenance | 14400 | 14400 | 79758 | 79758 | 127794 | 127794 | 319296 | 319296 | 506991 | 506991
[22 empty] | Electric Avoided Costs ($/kWh) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Design | 7500 | 7500 | 47475 | 47475 | 84075 | 84075 | 195000 | 195000 | 195000 | 195000 | [10 empty] | Avoided Electric Capacity ($/kW) |  |  | 0.43654 | 0.22989 | 0.23679 | 0.24119 | 0.24227 | 0.24543 | 0.24803 | 0.25606 | 0.26455 | 0.27145 | 0.27803 | 0.28361 | 0.29166 | 0.2998 | 0.308 | 0.31759 | 0.32858 | 0.34121 | 0.35368 | 0.36452 | 0.37597 | 0.38699
| Contruction | 17500 | 17500 | 110775 | 110775 | 196175 | 196175 | 455000 | 455000 | 455000 | 455000 | [10 empty] | Avoided Electric T&D ($/kW) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Production | 35280 | 47040 | 223322.4 | 297763.2 | 395488.8 | 527318.4 | 1173412.8 | 1350000 | 1350000 | 1350000 | [10 empty] | Avoided Ancillary ($/kW/Mth) |  |  | 1.1229 | 1.1825 | 1.218 | 1.2406 | 1.2462 | 1.2624 | 1.2758 | 1.3171 | 1.3608 | 1.3963 | 1.4301 | 1.4589 | 1.5003 | 1.5421 | 1.5843 | 1.6336 | 1.6902 | 1.7552 | 1.8193 | 1.875 | 1.934 | 1.9906
| Total Incentives | 60280 | 72040 | 381572.4 | 456013.2 | 675738.8 | 807568.4 | 1823412.8 | 2000000 | 2000000 | 2000000
| CO2 tons/MMBtu from gas on-site | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489 | 0.058489
| Avg electric T&D marginal losses | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02% | 11.02%
| CO2 tons/MWh from electricity | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 1.0978
| CO2 tons/yr from on-site fuel | 443.4733 | 443.4733 | 2196.9283 | 2196.9283 | 3647.4476 | 3647.4476 | 9857.6217 | 9857.6217
| CO2 tons/yr displaced thermal | 227.9136 | 313.4987 | 913.1516 | 1300.7858 | 1406.87 | 2021.3649 | 3340.0388 | 4992.5842
| CO2 tons/yr displaced electric | 645.4841 | 645.4841 | 4085.9141 | 4085.9141 | 7235.8763 | 7235.8763 | 21468.7998 | 21468.7998
| CO2 tons/yr net impact | -429.9243 | -515.5095 | -2802.1374 | -3189.7716 | -4995.2987 | -5609.7936 | -14951.217 | -16603.7624
| Equivalent electricity impact (kWh) | -391637.083 | -469600.3867 | -2552590.9996 | -2905704.1119 | -4550438.6966 | -5110209.3355 | -13619725.3288 | -15125102.0568
| equiv elec CO2 impact as % of CHP elec output | 0.66605 | 0.79864 | 0.6858 | 0.78068 | 0.69035 | 0.77527 | 0.69642 | 0.77339
Egrid 2010 RFCW (Com Ed)
Note on B21: raikar: From ICF draft paper, Table 3, Total Heat Recovered
Note on B24: raikar: From ICF draft paper, Table 3, Electrical Efficiency
Note on B42: raikar: $40,000/Mmbtu of steam, DOE Boiler MACT rule of thumb