## Assumptions
Chapter 49, Service Water Heating, 2007 ASHRAE Handbook, HVAC Applications |  |  |  | Based on CA study -1 | Based on Plumbing code, CA study or estimate -2 |  | Based on CA study -1 |  |  | See-3 | Estimate
| Building Type | Gallons hot water per unit per day | Unit | Estimated % hot water from Faucets | Multiplier | Unit | Days per year | Annual gallons per faucet | kWh using TRM defaults | Annual Recovery Hours | % usage in peak period (1-5) | Hours of Recovery during peak (65 days in summer peak) | CF (260 hours in peak period) | Summer Coincident Peak Demand savings using default TRM assumptions
| Small Office | 1 | person | 100% | 10 | employees per faucet | 250 | 2500 | 46.0037 | 18.6644 | 50% | 1.6619 | 0.0063919 | 0.015755
| Large Office | 1 | person | 100% | 45 | employees per faucet | 250 | 11250 | 207.0169 | 83.9897 | 50% | 7.4785 | 0.028764 | 0.070896
| Fast Food Rest | 0.7 | meal/day | 50% | 75 | meals per faucet | 365 | 6562.5 | 120.7598 | 48.994 | 25% | 2.1812 | 0.0083894 | 0.020678
| Sit-Down Rest | 2.4 | meal/day | 50% | 36 | meals per faucet | 365 | 10800 | 198.7362 | 80.6301 | 33.33% | 4.7863 | 0.018409 | 0.045374
| Retail | 2 | employee | 100% | 5 | employees per faucet | 365 | 2500 | 46.0037 | 18.6644 | 33.33% | 1.1079 | 0.0042613 | 0.010503
| Grocery | 2 | employee | 100% | 5 | employees per faucet | 365 | 2500 | 46.0037 | 18.6644 | 33.33% | 1.1079 | 0.0042613 | 0.010503
| Warehouse | 2 | employee | 100% | 5 | employees per faucet | 250 | 2500 | 46.0037 | 18.6644 | 50% | 1.6619 | 0.0063919 | 0.015755
| Elementary School | 0.6 | person | 50% | 50 | students per faucet | 200 | 3750 | 69.0056 | 27.9966 | 50% | 2.4928 | 0.0095879 | 0.023632
| Jr High/High School | 1.8 | person | 50% | 50 | students per faucet | 200 | 11250 | 207.0169 | 83.9897 | 50% | 7.4785 | 0.028764 | 0.070896
| Health | 90 | patient | 25% | 2 | Patients per faucet | 365 | 11250 | 207.0169 | 83.9897 | 25% | 3.7393 | 0.014382 | 0.035448
| Motel | 20 | room | 25% | 1 | faucet per room | 365 | 1250 | 23.0019 | 9.3322 | 10% | 0.16619 | 0.00063919 | 0.0015755
| Hotel | 14 | room | 25% | 1 | faucet per room | 365 | 875 | 16.1013 | 6.5325 | 10% | 0.11633 | 0.00044743 | 0.0011028
| Other | 1 | employee | 100% | 20 | employees per faucet | 250 | 5000 | 92.0075 | 37.3288 | 50% | 3.3238 | 0.012784 | 0.031509
1. Appendix E; “Waste Not, Want Not: The Potential for Urban Water Conservation in California”; http://www.pacinst.org/reports/urban_usage/appendix_e.pdf
2- Based on review of the Illinois plumbing code (Employees and students per faucet). Retail, grocery, warehouse and health are estimates. Meals per faucet estimated as 4 bathroom and 3 kitchen faucets and average meals per day of 250 (based on California study above) – 250/7 = 36. Fast food assumption estimated.
3- 54.5% is the proportion of hot 120F water mixed with 54.1F supply water to give 90F mixed faucet water. 73 is Gallons per hour recovery calculated for 65.9F temp rise (120-54.1), 98% recovery efficiency, and typical 12kW electric resistance storage tank.

## Plumbing Code
# faucets | Mid point # people | People per faucet
1 | 8 | 8
2 | 26 | 13
3 | 48 | 16
4 | 76 | 19
5 | 108 | 21.6
1 | 13 | 13
2 | 38 | 19