Work Paper PGECOFST116

#### Demand Ventilation Controls

Revision # 1

Pacific Gas & Electric Company

Customer Energy Efficiency Department

Commercial Kitchen Demand Ventilation Controls

Measure Codes F150, F151

# At a Glance Summary

| Applicable Measure Codes: | F150 | F151 |
| --- | --- | --- |
| Measure Description: | Commercial Kitchen Ventilation Control—Retrofit | Commercial Kitchen Ventilation Control—New Hood |
| Energy Impact Common Units: | Source: PG&E Calculations Per nameplate exhaust fan horsepower | Source: PG&E Calculations Per nameplate exhaust fan horsepower |
| Base Case Description: | Source: PG&E Calculations. Single-speed commercial kitchen exhaust system | Source: PG&E Calculations. Single-speed commercial kitchen exhaust system |
| Base Case Energy Consumption: | Source: PG&E Calculations. 7,640 kWh/yr/exh HP | Source: PG&E Calculations. 7,640 kWh/yr/exh HP |
| Measure Energy Consumption: | Source: PG&E Calculations. 3,154 kWh/yr/exh HP | Source: PG&E Calculations. 3,154 kWh/yr/exh HP |
| Energy Savings (Base Case – Measure) | Source: PG&E Calculations. 4,486 kWh/yr/exh HP | Source: PG&E Calculations. 4,486 kWh/yr/exh HP |
| Costs Common Units: | Source: PG&E Calculations Per nameplate exhaust fan horsepower | Source: PG&E Calculations Per nameplate exhaust fan horsepower |
| Base Case Equipment Cost ($/unit): | Source: PG&E Calculations. $0 | Source: PG&E Calculations. $0 |
| Measure Equipment Cost ($/unit): | Source: PG&E Calculations. $1,988/exh HP | Source: PG&E Calculations. $994/exh HP |
| Measure Incremental Cost ($/unit): | Source: PG&E Calculations. $1,988/exh HP | Source: PG&E Calculations. $994/exh HP |
| Effective Useful Life (years): | Source: PG&E. EUL = 15 years | Source: PG&E. EUL = 15 years |
| Program Type: | Retrofit | Retrofit |
| Net-to-Gross Ratios: | 0.8 -- Source: www.Deeresources.com - NTG table | 0.8 -- Source: www.Deeresources.com - NTG table |
| Important Comments: |  |  |

# At-A-Glance Measure List

| Measure Code | DEER RunID | Measure Description | Unit Type | Building Type | Building Vintage | Climate Zone | Peak Electric Demand Reduction (kW/unit) | Electric Savings (kWh/unit) | Gas Savings (therms/unit) | Base Case Cost ($/unit) | Measure Cost ($/unit) | Measure Incremental Cost ($/unit) | Effective Useful Life (years) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| F150 |  | DVC Control Retrofit | Exhaust HP | BCR | AV | ALL | 0.76 | 4,486 | 0 | 0 | 1,988 | 1,988 | 15 |
| F151 |  | DVC Control New Hood | Exhaust HP | BCR | AV | ALL | 0.76 | 4,486 | 0 | 0 | 994 | 994 | 15 |

Unit: HP

# Work Paper Approvals

| Ed Mah Manager, Forecast, Analysis, and Product Performance | Date |
| --- | --- |
| Grant Brohard Manager, Technical Product Support | Date |
| Keith Reed or Greydon Hicks Manager, Mass Market or Target Market | Date |

# Document Revision History

Revision # 		Date 		         Description		         Author (Company)

| Revision 0 | 12/21/2007 | Original work paper : Demand Ventilation Controls PGECOFST116 R0.doc | David Zabrowski (Fisher-Nickel, Inc.) |
| --- | --- | --- | --- |
| Revision 1 | 6/1/09 | Changes to EUL, NTG language and references, costs updated | David Zabrowski, Lauren Mills (Fisher-Nickel, inc.), Steve Blanc PG&E |

# Table of Contents

At a Glance Summary	ii

At-A-Glance Measure List	iii

Work Paper Approvals	iv

Document Revision History	v

Table of Contents	vi

List of Tables	vi

Section 1. General Measure & Baseline Data	1

1.1 Measure Description & Background	1

1.2 DEER Differences Analysis	2

1.3 Codes & Standards Requirements Analysis	2

1.4 EM&V, Market Potential, and Other Studies	2

1.5 Base Cases for Savings Estimates: Existing & Above Code	2

1.6 Base Cases & Measure Effective Useful Lives	2

1.7 Net-to-Gross Ratios for Different Program Strategies	3

Section 2. Calculation Methods	4

2.1 Electric Energy Savings Estimation Methodologies	4

2.2. Demand Reduction Estimation Methodologies	6

2.3. Gas Energy Savings Estimation Methodologies	6

Section 3. Load Shapes	6

3.1 Base Cases Load Shapes	6

3.2 Measure Load Shapes	6

Section 4. Base Case & Measure Costs	7

4.1 Base Cases Costs	7

4.2 Measure Costs	7

4.3 Incremental & Full Measure Costs	7

References	9

# List of Tables

Table 1. Commercial Demand Ventilation Control Cost Effectiveness Example	5

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper documents the rationale for the Commercial Kitchen Demand Ventilation Control measures as listed in the Commercial Food Service Catalog. The Commercial Food Service Catalog is part of Pacific Gas and Electric Company’s Customer Energy Efficiency Program. PG&E offers incentives to non-residential customers for installing qualifying lighting, refrigeration, air-conditioning, food service, and agricultural equipment.

Catalog Description –

F150: This incentive applies towards the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing dedicated commercial kitchen exhaust hood and make-up air system. The control system must be used in conjunction with variable speed fan motor controls. Project Installation Worksheet must be submitted with rebate application. Only pre-approved control systems will qualify for an incentive.

F151: This incentive applies towards the purchase and installation of a new commercial kitchen exhaust hood control system installed in a new dedicated commercial kitchen exhaust hood and make-up air system. The control system must be used in conjunction with variable speed fan motor controls. Project Installation Worksheet must be submitted with rebate application. Only pre-approved control systems will qualify for an incentive.

Program Restrictions and Guidelines

Terms and Conditions

This incentive applies towards the purchase of new or retrofit demand ventilation controls for dedicated commercial kitchen exhaust and make-up air systems. The control system must be used in conjunction with variable speed fan motor controls.

Market Applicability

This measure is applicable to any commercial cooking application, including (but not limited to) casual dining and quick service restaurants, hotels, motels, schools, colleges and recreational facilities.

Technical Description

There are over 90,000 restaurants in the State of California. Most food service operations that cook food require an exhaust ventilation hood to remove grease and effluent from the kitchen space. Modern commercial kitchen ventilation systems are about more than heat and smoke removal at the lowest first cost. Food-service establishment owners and operators have become more sophisticated, demanding systems that are more energy efficient and require less maintenance. In addition, there is a greater emphasis on comfort, kitchen indoor air quality, reduced noise levels and improved fire safety.

Until recently, kitchen ventilation controls mainly consisted of a manual on/off switch and a magnetic relay or motor starter for each fan. Exhaust and makeup fans operated either at 100% speed or not at all. The occasional independent operator has upgraded to a manual two-speed system that relies on cooks to switch from low to high-speed and vice versa, which is an improvement but not a global solution for the lack of control over kitchen exhaust. Today’s state-of-the-art system is equipped with microprocessor-based controls with sensors that automatically vary fan speed based on cooking load and/or time of day.

The control system varies the exhaust rate based on the energy and effluent output from the cooking appliances (i.e., the more heat and smoke/vapors generated, the more ventilation needed). This involves installing a temperature sensor in the hood exhaust collar and/or an optic sensor on the end of the hood that sense cooking conditions which allows the system to automatically vary the rate of exhaust to what is needed by adjusting the fan speed accordingly.

There have been at least 5 monitored installations of this technology with an average annual savings of nearly 4,500 kWh per exhaust fan H.P. Typical exhaust system H.P. of monitored systems has ranged from 3 H.P. to 15 H.P.

## 1.2 DEER Differences Analysis

The DEER database does not contain a commercial kitchen demand ventilation control measure.

## 1.3 Codes & Standards Requirements Analysis

State Standards: These measures do not fall under Title 20 or Title 24 of the California Energy Regulations.

Federal Standards: These measures do not fall under Federal DOE or EPA Energy Regulations.

## 1.4 EM&V, Market Potential, and Other Studies

There were no specific EM&V studies identified that addressed commercial kitchen demand ventilation control measures in the commercial sector.

## 1.5 Base Cases for Savings Estimates: Existing & Above Code

The base case for both existing units and above code savings was the pre-existing single-speed exhaust and makeup air fans with standard on/off controls used in each of the five monitored locations. 1-5

## 1.6 Base Cases & Measure Effective Useful Lives

The DEER Measure Cost Data Users Guide, version 2.01, defines the following terms:

- Retrofit (RET) – replacing a working technology prior to failure.

- Replace on Burnout (ROB) – replacing a technology at the end of its useful life.

- New Construction (NEW) – installing a technology in a new construction or major renovation project.

2008 DEER, version 2008.2.05 database shows a EUL of 15 years for variable frequency drives6. Demand ventilation controls are classed as suitable for RET and NEW installations.

## 1.7 Net-to-Gross Ratios for Different Program Strategies

NTGR Values for Residential and Nonresidential Measure/Delivery Strategy Combinations

| Sector | Market Segment | End-Use | Type | Measure Name(s) | NTG Values Recommended for 2006-07 update |
| --- | --- | --- | --- | --- | --- |
| Non Residential | All | All | Default Value | New Measures or New Delivery Methods Where no Previous NTG results are Available in the 2008 DEER Update | 80% |

The assumed Net-to-Gross (NTG)7 ratio for commercial food service equipment is 0.8, a default value due to a lack of studies on this issue in the food Service Sector.

However, we are convinced that this default value underestimates the actual importance of the rebate programs in motivating FS operators to purchase EE equipment.

Commercial food service facility operators place a high importance on the first cost of commercial food service equipment.  In addition to the low-first-cost economic pressure on the food service operator to purchase less efficient equipment, the general lack of objective performance data has placed a greater emphasis on initial equipment cost. If the buyer is not exposed to accurate bench-mark performance data and recommendations from a trusted source (i.e., the energy utility), there is less incentive on the part of the manufacturers to improve equipment performance and offer energy-efficient models.  The very existence of energy-efficiency incentives has been the major driving force in motivating manufacturers to develop and promote more efficient commercial food service appliances to an industry historically interested only in first cost.

In fact, the initial cost of the appliances is often the primary metric for choosing new or replacement appliances. A study published by the U.S. Department of Energy, Characterization of Commercial Building Appliances8, effectively summarizes the industry:

“The largest impact on the future efficiency of the installed base of cooking equipment will depend more on factors that influence the purchase decision criteria for the equipment than on technology developments. Quite simply, the installed base of [commercial cooking] equipment efficiencies could be significantly increased if customers purchased more efficient models. However, the cost premium associated with the high efficiency cooking equipment does not always justify the resultant savings.”

“As a result, projecting future efficiencies, we need to consider customer trends and driving forces behind the more energy efficient system. Often times, the higher efficiency systems also provide better cooking performance which is extremely important to the fast food chains.”

# Section 2. Calculation Methods

## 2.1 Electric Energy Savings Estimation Methodologies

Measure data for cost effectiveness modeling are based on average equipment characteristics for California utility customer participants for the Food Service Equipment program. The energy savings were based on five separate monitored sites that represent the range of demand ventilation control installations. 1-5 Unitized cost effectiveness determinants are summarized in Table 1. Measure unit of measure is based on energy savings per total exhaust fan rated horsepower.

Table 1. Commercial Demand Ventilation Control Cost Effectiveness Example

| Food Service Facility Type | Institutional Cafeteria1 | Casual Dining Restaurant2 | Hotel Main Kitchen3 | Super Market4 | University Campus Dining Facility5 | Average |
| --- | --- | --- | --- | --- | --- | --- |
| Location | San Ramon | Rancho Cucamonga | San Francisco | Brentwood | Berkeley |  |
| Exhaust Capacity (cfm) | 9,600 | 6,400 | 22,500 | 23,800 | 12,000 | 14,860 |
| Rated Exhaust Fan Power (HP) | 6.0 | 3.0 | 15 | NA | 7.0 | 7.75 |
| Measured Exhaust Fan Power (kW) | 4.2 | 2.3 | 7.6 | 6.3 | 6.22 | 5.32 |
| Exhaust kW/HP Ratio | 0.70 | 0.77 | 0.51 | NA | 0.89 | 0.72 |
| Rated MUA Fan Power (HP) | NA | 5.0 | 20 | NA | NA | 12.5 |
| Measured MUA Fan Power (kW) | 3.1 | 1.5 | 6.4 | NA | 6.52 | 4.38 |
| Measured Total Fan Power (kW) | 7.3 | 3.9 | 14 | 6.29 | 12.47 | 8.79 |
| Avg Power with DVC (kW) | 1.9 | 2.1 | 5.3 | 1.23 | 5.6 | 3.23 |
| Fan Power Reduction (kW) | 5.4 | 1.8 | 8.7 | 5.1 | 6.8 | 5.56 |
| Fan Power Reduction (%) | 74 | 46 | 62 | 80 | 55 | 64 |
| Fan Speed Reduction (%) | 36 | 19 | 28 | 42 | 23 | 30 |
| Effective CFM Reduction (cfm) | 3,471 | 1,200 | 6,223 | 9,986 | 2,791 | 4,734 |
| Operating Time (h) | 19 | 17 | 24 | 12 | 17 | 17.8 |
| Baseline Energy Use (w/o DVC, kWh/d) | 137.9 | 58.9 | 336 | 75.5 | 216.6 | 165.0 |
| Measure Energy Use (w/ DVC, kWh/d) | 34.8 | 31.6 | 127 | 17.5 | 97.9 | 61.8 |
| Energy Savings (kWh/d) | 103.1 | 27.3 | 209 | 58 | 118.7 | 103.2 |
| Energy savings (%) | 75 | 46 | 62 | 77 | 55 | 63 |
| Operating Days Per Year | 260 | 363 | 365 | 360 | 300 | 330 |
| Annual Energy Savings (kWh) | 26,806 | 9,910 | 76,285 | 20,880 | 35,610 | 33,898 |
| Applied Rate ($/kWh) | $0.13 | $0.13 | $0.13 | $0.13 | $0.13 | $0.13 |
| Annual Cost Savings ($) | $3,485 | $1,288 | $9,917 | $2,714 | $4,629 | $4,407 |
| Incremental Measure Cost ($) | $12,000 | $8,000 | $15,000 | $18,000 | $16,000 | $13,800 |
| Estimated Useful Life (EUL) a | 15 years | 15 years | 15 years | 15 years | 15 years | 15 years |
| Estimated Payback (yr) | 3.4 | 6.2 | 1.5 | 6.6 | 3.5 | 3.1 |
| Normalized Baseline Annual Energy Consumption (kWh/exh HP) |  |  |  |  |  | 7,640 |
| Normalized Measure Case Annual Energy Consumption (kWh/exh HP) |  |  |  |  |  | 3,154 |
| Normalized Annual Energy Savings (kWh/exh HP) |  |  |  |  |  | 4,486 |
| Normalized Demand Savings (kW/exh HP) |  |  |  |  |  | 0.76 |
| Normalized Measure Cost ($/exh HP)b |  |  |  |  |  | $1,988 |
| Normalized Annual Energy Cost Savings ($/exh HP) |  |  |  |  |  | $583 |

a The estimated useful life for variable frequency drives is listed in 2008 DEER EUL Summary6

b Incremental cost for retrofit is based on normalized cost derived from the above Emerging Technology project costs where available. The incremental cost of installing kitchen ventilation control as an integral component of a new ventilation system is approximately half the cost of a retrofit installation.

## 2.2. Demand Reduction Estimation Methodologies

The demand reduction estimation is based on end-use monitored data for five separate sites. 1-5 Measure unit of measure is based on energy savings per total exhaust fan rated horsepower. The normalized demand savings for the five sites was 0.76 kW per rated exhaust fan horsepower.

## 2.3. Gas Energy Savings Estimation Methodologies

There were no gas energy savings associated with this measure.

# Section 3. Load Shapes

Load Shapes are an important part of the life-cycle cost analysis of any energy efficiency program portfolio.  The net benefits associated with a measure are based on the amount of energy saved and the avoided cost per unit of energy saved.  For electricity, the avoided cost varies hourly over an entire year.  Thus, the net benefits calculation for a measure requires both the total annual energy savings (kWh) of the measure and the distribution of that savings over the year.  The distribution of savings over the year is represented by the measure’s load shape.  The measure’s load shape indicates what fraction of annual energy savings occurs in each time period of the year.  An hourly load shape indicates what fraction of annual savings occurs for each hour of the year.  A Time-of-Use (TOU) load shape indicates what fraction occurs within five or six broad time-of-use periods, typically defined by a specific utility rate tariff.  Formally, a load shape is a set of fractions summing to unity, one fraction for each hour or for each TOU period.  Multiplying the measure load shape with the hourly avoided cost stream determines the average avoided cost per kWh for use in the life cycle cost analysis that determines a measure’s Total Resource Cost (TRC) benefit.

## 3.1 Base Cases Load Shapes

The base case load shape would be expected to follow a typical nonresidential foodservice end use load shape.

Commercial kitchen ventilation exhaust and makeup air fan load shapes  differ among food service facilities (quick service, casual dining, hotels, college, schools, hospitals etc) depending on daily menu variations, hours of operation, serving periods, day-of-week, and facility location (city downtown, suburban mall, access to interstate highways, etc.). Consequently, applicable average TOU and hourly load shapes for commercial kitchen exhaust and make-up air fans are unavailable. The Base Case Load Shape  for commercial kitchen exhaust and makeup air fans would be relatively flat during operating hours, with the fans running at their maximum speed.

## 3.2 Measure Load Shapes

For purposes of the net benefits estimates in the E3 calculator, what is required is the load shape that ideally represents the difference between the base equipment and the installed energy efficiency measure.  This difference load profile is what is called the Measure Load Shape and would be the preferred load shape for use in the net benefits calculations.

The measure load shape for this measure is determined by the E3 calculator based on the nonresidential market sector and the foodservice end-use.

Commercial kitchen demand ventilation controlled exhaust and makeup air fan load shapes  differ among food service facilities (quick service, casual dining, hotels, college, schools, hospitals etc) depending on daily menu variations, hours of operation, serving periods, day-of-week, and facility location (city downtown, suburban mall, access to interstate highways, etc.). Consequently, applicable average TOU and hourly load shapes for demand ventilation controlled kitchen exhaust and make-up air fans are unavailable. The Measure Load Shape for demand ventilation controlled exhaust and makeup air fans are operated all day long, and would operate at maximum speed during regular meal periods (breakfast, lunch, and dinner). Between meal periods the demand ventilation controlled exhaust and makeup air fans would tend to run at less than maximum speed.

# Section 4. Base Case & Measure Costs

## 4.1 Base Cases Costs

The Base Case is a standard commercial kitchen ventilation system with single speed exhaust and makeup air fans and a simple on/off control. Since the commercial kitchen ventilation system is required for both standard systems and demand ventilation controlled systems, the Base Case cost for these measures is zero.

## 4.2 Measure Costs

Incremental cost for retrofit is based on normalized cost derived from the above Emerging Technology project costs, where available, and published manufacturer prices1-5, 9.  These costs include both the equipment costs and the full installation costs of the demand ventilation control system.

The costs of the retrofit include the control system, and the fan and variable speed fan control upgrades and the sensor arrays. Installation costs include the cost of installing the demand ventilation control system, running sensor array wiring between the sensors, the control system and the rooftop fan equipment.

The incremental cost of installing kitchen demand ventilation control system as an integral component of a new ventilation system is approximately half the cost of a retrofit installation. The reduction in costs is entirely due to the simpler installation of a prefabricated system where wiring is already a component of the kitchen ventilation system.

## 4.3 Incremental & Full Measure Costs

Full measure costs are used in this analysis.

Index

Base Case Load Shape, 6

DEER Measure Cost Data Users Guide, 2

load shape, 6, 7

Measure Load Shape, 7

New Construction, 2

Replace on Burnout, 2

Retrofit, ii, 2

# References

- Fisher-Nickel, inc., Unpublished. Melink Intelli-Hood™ Operator, Fan Motor Speed Controller: In-Kitchen Appliance Performance Report.

- Architectural Energy Corporation, 2004. Demand Ventilation in Commercial Kitchens—An Emerging Technologies Case Study for Applebee’s Neighborhood Grill, Rancho Cucamonga and El Cajon, California.

- Fisher-Nickel, inc., 2004. Demand Ventilation in Commercial Kitchens—An Emerging Technology Case Study. Melink Intelli-Hood® Controls—Commercial Kitchen Ventilation System Intercontinental Mark Hopkins Hotel.

- Fisher-Nickel, inc., 2006. Demand Ventilation in Commercial Kitchens—An Emerging Technology Case Study. Melink Intelli-Hood® Controls—Supermarket Application.

- California Energy Commission (CEC), 2006. Public Interest Energy Research (PIER) Program Report: Demand Ventilation Control in Commercial Kitchens.

- 2008 Database for Energy-Efficient Resources Version 2008.2.05  December 16, 2008; www.deeresources.com – EUL/RUL (Effective/Remaining Useful Life) Values --EUL/RUL Values and Summary Documentation (Updated 10 October 2008) Excel Spreadsheet --http://www.deeresources.com/deer0911planning/downloads/EUL_Summary_10-1-08.xls (Non-Residential/Cooking )

- 2008 Database for Energy-Efficient Resources Version 2008.2.05  December 16, 2008; www.deeresources.com-- /  NTG Values / To be used for 2009 Bridge Funding period reporting (same as 2006-2007 Ex Ante update values) CPUC DEER NTFR Update Process for 2006-2007 Programs(posted 14 October 2008) / Table 3-2--Recommended NFTR Values, pg 3-4, Excel spreadsheet -- Updated DEER NTG Values for 2006-07 final 2008-10-10.xls

- Arthur D. Little, Inc., Characterization of Commercial Building Appliances. Prepared for U.S. Department of Energy, ADL Reference No. 4520, August, 1993.

- Melink 2007. Intelli-Hood 2007 Price List.