# Measure 10: Commercial Kitchen Demand Ventilation Controls-Electric

Measure Code: F150 (Retrofit) / F151 (Integral New Hood)

### Measure Description

There are over 90,000 restaurants in the State of California. Most food service operations that cook food require an exhaust ventilation hood to remove grease and effluent from the kitchen space. Modern commercial kitchen ventilation systems are about more than heat and smoke removal at the lowest first cost. Food-service establishment owners and operators have become more sophisticated, demanding systems that are more energy efficient and require less maintenance. In addition, there is a greater emphasis on comfort, kitchen indoor air quality, reduced noise levels and improved fire safety.

Until recently, kitchen ventilation controls mainly consisted of a manual on/off switch and a magnetic relay or motor starter for each fan. Exhaust and makeup fans operated either at 100% speed or not at all. The occasional independent operator has upgraded to a manual two-speed system that relies on cooks to switch from low to high-speed and vice versa, which is an improvement but not a global solution for the lack of control over kitchen exhaust. Today’s state-of-the-art system is equipped with microprocessor-based controls with sensors that automatically vary fan speed based on cooking load and/or time of day.

The control system varies the exhaust rate based on the energy and effluent output from the cooking appliances (i.e., the more heat and smoke/vapors generated, the more ventilation needed). This involves installing a temperature sensor in the hood exhaust collar and/or an optic sensor on the end of the hood that sense cooking conditions which allows the system to automatically vary the rate of exhaust to what is needed by adjusting the fan speed accordingly.

There have been at least 5 monitored installations of this technology with an average annual savings of nearly 2,000 kWh per H.P. Total system H.P. (Exhaust and Make up Fans) of monitored systems has ranged from 8 H.P. to 35 H.P.

Market Applicability

This measure is applicable to commercial cooking applications. Includes (but not limited to) casual dining, hotels, motels, schools, colleges and recreational facilities.

# Terms and Conditions:

This incentive applies towards the purchase of new or retrofit demand ventilation controls for dedicated commercial kitchen exhaust and make-up air systems. The control system must be used in conjunction with variable speed fan motor controls.

### Cost Effectiveness Modeling Measure Data

Measure data for cost effectiveness modeling are based on average equipment characteristics for California utility customer participants for the Food Service Equipment program. Unitized cost effectiveness determinants are summarized in Table 10.1. Annual energy use was monitoring five different types of sites, as summarized in Table 10.1. The assumed price for electricity is $0.13 per kWh. Measure unit of measure is based on energy savings per total exhaust fan rated horsepower.

# Table 10.1 Commercial Demand Ventilation Control Cost Effectiveness Example

| Food Service Facility | Institutional Cafeteria | Casual Dining Restaurant | Hotel Main Kitchen | Supermarket | University Campus Dining Facility | Average |
| --- | --- | --- | --- | --- | --- | --- |
| Location | San Ramon | Rancho Cucamonga | San Francisco | Brentwood | Berkeley |  |
| Exhaust Capacity (cfm) | 9,600 | 6,400 | 22,500 | 23,800 | 12,000 | 14,860 |
| Rated Exhaust Fan Power (HP) | 6.0 | 3.0 | 15 | NA | 7.0 | 7.75 |
| Measured Exhaust Fan Power (kW) | 4.2 | 2.3 | 7.6 | 6.3 | 6.22 | 5.32 |
| Exhaust kW/HP Ratio | 0.70 | 0.77 | 0.51 | NA | 0.89 | 0.72 |
| Rated MUA Fan Power (HP) | NA | 5.0 | 20 | NA | NA | 12.5 |
| Measured MUA Fan Power (kW) | 3.1 | 1.5 | 6.4 | NA | 6.52 | 4.38 |
| Measured Total Fan Power (kW) | 7.3 | 3.9 | 14 | 6.29 | 12.47 | 8.79 |
| Avg Power with DVC (kW) | 1.9 | 2.1 | 5.3 | 1.23 | 5.6 | 3.23 |
| Fan Power Reduction (kW) | 5.4 | 1.8 | 8.7 | 5.1 | 6.8 | 5.56 |
| Fan Power Reduction (%) | 74 | 46 | 62 | 80 | 55 | 64 |
| Fan Speed Reduction (%) | 36 | 19 | 28 | 42 | 23 | 30 |
| Effective CFM Reduction (cfm) | 3,471 | 1,200 | 6,223 | 9,986 | 2,791 | 4,734 |
| Operating Time (h) | 19 | 17 | 24 | 12 | 17 | 17.8 |
| Energy Use w/o DVC (kWh/d) | 137.9 | 58.9 | 336 | 75.5 | 216.6 | 165.0 |
| Energy Use w/ DVC (kWh/d) | 34.8 | 31.6 | 127 | 17.5 | 97.9 | 61.8 |
| Energy Savings (kWh/d) | 103.1 | 27.3 | 209 | 58 | 118.7 | 103.2 |
| Energy savings (%) | 75 | 46 | 62 | 77 | 55 | 63 |
| Operating Days Per Year | 260 | 363 | 365 | 360 | 300 | 330 |
| Annual Energy Savings (kWh) | 26,806 | 9,910 | 76,285 | 20,880 | 35,610 | 33,898 |
| Applied Rate ($/kWh) | $0.13 | $0.13 | $0.13 | $0.13 | $0.13 | $0.13 |
| Annual Cost Savings ($) | $3,485 | $1,288 | $9,917 | $2,714 | $4,629 | $4,407 |
| Incremental Measure Cost ($) | $12,000 | $8,000 | $15,000 | $18,000 | $16,000 | $13,800 |
| Estimated Useful Life (EUL) a | 15 years | 15 years | 15 years | 15 years | 15 years | 15 years |
| Estimated Payback (yr) | 3.4 | 6.2 | 1.5 | 6.6 | 3.5 | 3.1 |
| Normalized Measure Cost ($/exh HP)b |  |  |  |  |  | $1,988 |
| Normalized Energy Savings (kWh/exh HP) |  |  |  |  |  | 4,486 |
| Normalized Demand Savings (kW/exh HP) |  |  |  |  |  | 0.76 |
| Normalized Energy Cost Savings ($/exh HP) |  |  |  |  |  | $583 |

a The estimated useful life for variable frequency drives is listed in the Energy Efficiency Policy Manual Table 4.1.

b Incremental cost for retrofit is based on normalized cost derived from the above Emerging Technology project costs where available. The incremental cost of installing kitchen ventilation control as an integral component of a new ventilation system is approximately half the cost of a retrofit installation.

MDSS Review Table

| Measure Name | Measure Code | Unit Type | Bldg Type | Bldg Vintage | Climate Zone | Coincident Peak Demand Reduction (kW) | Annual Energy Savings Per Unit (kWh) | Annual Savings Per Unit (Therms) | Increment Measure Cost | EUL (Yrs) | Net to Gross |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DVC Control Retrofit | F150 | Exhaust HP | BCR | AV | ALL | 0.76 | 4,486 | 0 | $1,988 | 15 | 1a |
| DVC Control New | F151 | Exhaust HP | BCR | AV | ALL | 0.76 | 4,486 | 0 | $1,000 | 15 | 1a |

a The Net-to-Gross Ratio is based on August 2003 Energy Efficiency Policy Manual Table 4.2. for Food Services Equipment

| Measure Name | Measure Code | Rebate |
| --- | --- | --- |
| DVC Control Retrofit Existing Hood | F150 | $350.00/Ex hp |
| DVC Control Integral New Hood | F151 | $300.00/Ex hp |