## Introduction
Introduction:
The load profile data in the "Compressor Factors" tab was collected from 50 facilities on Long Island, NY employing air compressors less than or equal to 40 hp as part of the Long Island Power Authority's Clean Energy Initiative. The data was collected from 2002 to 2005 in the process of performing custom compressed air system projects as part of their Commercial Construction Program. The number of compressor run hours at a given capacity from a typical work day were recorded and tabulated in the following sheet. These load profiles were weighted by compressor motor bhp and used to determine the average percent capacity for a small air compressor. DOE part load curves for various compressor types were used in conjunction with the collected data to develop "compressor factors." The percent full load compressor kW from DOE data was multiplied against the percent total compressor operating hours for each percent capacity bin. The results were then added to obtain the "compressor factors" for each of the given compressor types. Therefore, the "compressor factors" incorporate average demand curves and part load curves. When multiplied against total operating hours and full load kW for a given compressor, the result is a reliable estimate of a small compressor's annual kWh consumption.

## Compressor Factors
% Capacity
Compressor ID # | Flowrate (CFM) | Pressure (psi) | BHP | Full Load kW | Control Scheme | 100% | 95% | 90% | 85% | 80% | 75% | 70% | 65% | 60% | 55% | 50% | 45% | 40% | 35% | 30% | 25% | 20% | 15% | 10% | 5% | 0% | TOTAL HOURS
1 | 123 | 100 | 29.4 | 23.5832 | 1 |  |  |  |  | 0.5 | 0.5 | 0.5 | 1 |  |  |  | 0.5 | 1 | 1 | 1 | 1 | 2.5 | 1 |  |  |  | 10.5
2 | 123 | 100 | 29.4 | 23.5832 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 2 | 1 | 2 | 0 | 2 | 0 | 2 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 16
3 | 81 | 100 | 21.8 | 17.677 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18
4 | 123 | 100 | 29.4 | 23.5832 | 1 |  | 1 | 2 | 1 | 1 | 1 |  |  | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 1 | [5 empty] | 20
5 | 123 | 100 | 29.4 | 23.5832 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1.5 | 0 | 0 | 0 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 10
6 | 123 | 100 | 29.4 | 23.5832 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 4 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
7 | 106 | 100 | 27 | 22.1341 | 1 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 4.5 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
8 | 127 | 100 | 25 | 20.3381 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.5 | 0 | 5 | 1.5 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5
9 | 127 | 100 | 25 | 20.3381 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.5 | 0 | 5 | 1.5 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5
10 | 115 | 125 | 27.6 | 22.6259 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11
11 | 115 | 125 | 27.6 | 22.6259 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.5 | 0 | 0 | 4 | 0 | 0 | 0.5 | 0 | 4 | 0 | 0 | 0 | 0 | 13
12 | 115 | 125 | 27.6 | 22.6259 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.5 | 0 | 0 | 4 | 0 | 0 | 0.5 | 0 | 4 | 0 | 0 | 0 | 0 | 13
13 | 103 | 125 | 24.9 | 19.7611 | 1 | 0 | 0 | 0 | 14 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16
14 | 103 | 125 | 27.5 | 23.1808 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
15 | 123 | 100 | 29.4 | 23.5832 | 1 |  |  |  |  | 1 | 1 | [8 empty] | 2 | 3 | 2 |  |  |  |  | 9
16 | 43 | 100 | 10.1 | 8.4185 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2.5 | 1 | 0 | 1 | 2 | 1.5 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 14
17 | 93 | 125 | 25.3 | 20.4262 | 1 | 0 | 1.5 | 1.5 | 1 | 2 | 0 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 14
18 | 123 | 100 | 29.4 | 23.5832 | 1 | [5 empty] | 0.75 | 1.5 | 1.25 | 1.5 | 1.5 | 1.5 | 1 | 2 |  |  | 2 | 1 |  |  |  |  | 14
19 | 125 | 125 | 30 | 24.2208 | 1 |  |  | 10 |  |  |  |  | 2 | [13 empty] | 12
20 | 125 | 125 | 30 | 24.2208 | 1 |  |  | 10 |  |  |  |  | 2 | [13 empty] | 12
21 | 125 | 125 | 30 | 24.2208 | 1 |  |  | 10 |  |  |  |  | 2 | [13 empty] | 12
22 | 125 | 125 | 30 | 24.2208 | 1 |  |  | 10 |  |  |  |  | 2 | [13 empty] | 12
23 | 125 | 125 | 30 | 24.2208 | 1 |  |  | 10 |  |  |  |  | 2 | [13 empty] | 12
24 | 127 | 100 | 27 | 22.1341 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 5 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
25 | 127 | 100 | 27 | 22.1341 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 5 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
26 | 127 | 100 | 27 | 22.1341 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 5 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
27 | 106 | 100 | 27 | 22.1341 | 1 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 3.5 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
28 | 81 | 100 | 21.8 | 17.677 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.5 | 0.5 | 1 | 1 | 1 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
29 | 40 | 150 | 11 | 8.9196 | 1 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 11
30 | 43 | 100 | 10.1 | 8.4185 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
31 | 52 | 125 | 15.2 | 12.5991 | 2 | 0 | 8 | 0 | 8 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24
32 | 123 | 100 | 29.4 | 23.5832 | 1 | 0 | 0 | 0 | 4 | 4 | 2 | 0 | 4 | 3 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24
33 | 55 | 125 | 16.5 | 13.7531 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
34 | 123 | 100 | 29.4 | 23.5832 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1.5 | 0 | 0 | 0 | 1.5 | 1 | 1.5 | 0 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 9
35 | 123 | 100 | 29.4 | 23.5832 | 1 |  |  |  |  | 1 |  | 0.5 | 0.5 |  |  |  | 1 | 1.5 | 2.5 | 1.5 | 1.5 | [5 empty] | 10
36 | 123 | 100 | 29.4 | 23.5832 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 3 | 1 | 1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 12.5
37 | 123 | 100 | 29.4 | 23.5832 | 1 | 0 | 0 | 0 | 2 | 5 | 5 | 2 | 0 | 1 | 3 | 0 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24
38 | 123 | 100 | 33 | 26.471 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5
39 | 106 | 100 | 27 | 22.1341 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 4.5 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5
40 | 131 | 100 | 33.4 | 26.9658 | 1 | 0 | 4 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8
41 | 131 | 100 | 33.4 | 26.9658 | 1 | 0 | 4 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8
42 | 115 | 125 | 27.6 | 22.6259 | 1 | 2 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16
43 | 100.7 | 125 | 25.7 | 21.0684 | 2 | 0 | 2.5 | 0 | 0 | 0 | 2.5 | 4 | 0 | 5 | 1.25 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5
44 | 55 | 125 | 16.5 | 13.6463 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11
45 | 115 | 125 | 26.4 | 21.6422 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 8.5
46 | 134 | 125 | 32.6 | 26.5208 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 8.5
47 | 51 | 125 | 15.2 | 12.4607 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
48 | 112 | 100 | 27.9 | 22.6973 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10
49 | 140 | 175 | 40 | 35.1059 | 1 | 8 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
50 | 43 | 100 | 10.1 | 8.4185 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 1.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5
51 | 81 | 100 | 21.8 | 17.677 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 3 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
52 | 43 | 100 | 10.1 | 8.4185 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 10
53 | 127 | 100 | 27 | 22.1341 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
54 | 43 | 100 | 10.1 | 8.4185 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 1 | 2 | 2.5 | 2 | 0 | 0 | 0 | 0 | 0 | 9
55 | 123 | 100 | 29.4 | 23.5832 | 1 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 1 | 4 | 1.5 | 2.5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 13
56 | 145 | 125 | 28.7 | 23.3481 | 1 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
57 | 106 | 100 | 27 | 22.1341 | 2 | 0 | 12 | 8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24
58 | 106 | 100 | 27 | 22.1341 | 2 | 0 | 12 | 8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24
59 | 55 | 125 | 16.5 | 13.7531 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
60 | 105 | 125 | 20.7 | 16.8399 | 1 | 0 | 0 | 6 | 0 | 2 | 0 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17
61 | 96 | 125 | 27.6 | 22.6259 | 2 | 0 | 0 | 6 | 0 | 2 | 0 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17
62 | 96 | 125 | 27.6 | 22.6259 | 2 | 0 | 0 | 6 | 0 | 2 | 0 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17
63 | 50.5 | 125 | 15.2 | 12.4607 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
64 | 99.3 | 125 | 28 | 22.6061 | 1 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24
65 | 98 | 125 | 26.8 | 21.8024 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 7
66 | 173 | 100 | 38.1 | 30.9827 | 1 | 1 | 2 | 2 |  |  |  |  | 2 | 6 |  | 2 |  | 1 | [8 empty] | 16
67 | 127 | 100 | 27 | 22.1341 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
68 | 106 | 100 | 27 | 21.9651 | 2 | 0 | 5 | 5 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 24
69 | 134 | 125 | 31.1 | 25.3005 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
70 | 134 | 125 | 31.057 | 25.2656 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
71 | 134 | 125 | 31.057 | 25.2656 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
72 | 134 | 125 | 31.1 | 25.3005 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
[5 empty] | Total BHP * HOURS: | 1458.54 | 1379.6 | 2794.35 | 976.1 | 1204.1 | 2166 | 1242.9 | 1996.3 | 1240.05 | 2184.275 | 1486.375 | 1254.2 | 1072.65 | 1517.1 | 1055.7 | 506.9 | 422.1 | 29.4 | 0 | 0 | 0 | 23986.64
[5 empty] | Composite Load Distribution: | 6.081% | 5.752% | 11.65% | 4.069% | 5.02% | 9.03% | 5.182% | 8.323% | 5.17% | 9.106% | 6.197% | 5.229% | 4.472% | 6.325% | 4.401% | 2.113% | 1.76% | 0.1226% | 0% | 0% | 0% | 1
[5 empty] | Smoothed Composite Load Distribution (3-point rolling average): | 5.916% | 7.827% | 7.157% | 6.913% | 6.04% | 6.411% | 7.511% | 6.225% | 7.533% | 6.824% | 6.844% | 5.299% | 5.342% | 5.066% | 4.28% | 2.758% | 1.332% | 0.6274% | 0.04086% | 0% | 0% | 0.99945
Example Compressor Annual kWh Consumption
[28 empty] | Full Load kW: | 28.3
Air Compressor Part Load Power Curves (% Full Load kW vs. % Capacity) |  |  |  |  | Modulating w/ BD | 100% | 99% | 98% | 97% | 96% | 94.5% | 93% | 91.5% | 90% | 88% | 86% | 84% | 82% | 76% | 70% | 62% | 54% | 47% | 40% | 32.5% | 25% |  | # of Shifts: | 1
Source: DOE |  |  |  |  | Load/No Load w/ 1 gal/CFM | 100% | 100% | 100% | 99% | 98% | 96.5% | 95% | 93.5% | 92% | 89.5% | 87% | 84.5% | 82% | 78% | 74% | 69% | 64% | 55.5% | 47% | 36.5% | 26% |  | Operating Hours: | 2080
| = Green cells denote interpolated values |  |  |  | Load/No Load w/ 3 gal/CFM | 100% | 99% | 98% | 96% | 94% | 91% | 88% | 85.5% | 83% | 79.5% | 76% | 72% | 68% | 63% | 58% | 53% | 48% | 43% | 38% | 32% | 26%
[5 empty] | Variable Speed w/ Unloading | 100% | 95% | 90% | 85% | 80% | 75% | 70% | 66.5% | 63% | 58.5% | 54% | 50% | 46% | 42% | 38% | 34% | 30% | 25.5% | 21% | 18% | 15%
[5 empty] | Load/No Load w/ 5 gal/CFM | 100% | 99% | 98% | 94.5% | 91% | 88.5% | 86% | 82% | 78% | 74.5% | 71% | 69% | 67% | 60.5% | 54% | 49.5% | 45% | 40.5% | 36% | 31% | 26%
[27 empty] | "Compressor Factors" |  | Annual kWh
[5 empty] | Modulating w/ BD | 0.059161 | 0.07749 | 0.070137 | 0.067056 | 0.057982 | 0.060579 | 0.069856 | 0.056956 | 0.067796 | 0.060053 | 0.058857 | 0.044512 | 0.043803 | 0.038501 | 0.029958 | 0.0171 | 0.007192 | 0.0029489 | 0.00016342 | 0 | 0 | 0.8901 | Modulating w/ BD | 52394.8824
[5 empty] | Load/No Load w/ 1 gal/CFM | 0.059161 | 0.078273 | 0.071568 | 0.068438 | 0.05919 | 0.061861 | 0.071358 | 0.0582 | 0.069302 | 0.061077 | 0.059542 | 0.044777 | 0.043803 | 0.039514 | 0.03167 | 0.019031 | 0.0085239 | 0.0034823 | 0.00019202 | 0 | 0 | 0.90896 | Load/No Load w/ 1 gal/CFM | 53505.2333
[5 empty] | Load/No Load w/ 3 gal/CFM | 0.059161 | 0.07749 | 0.070137 | 0.066364 | 0.056774 | 0.058336 | 0.0661 | 0.053221 | 0.062523 | 0.054253 | 0.052013 | 0.038153 | 0.036324 | 0.031915 | 0.024823 | 0.014618 | 0.0063929 | 0.002698 | 0.00015525 | 0 | 0 | 0.83145 | Load/No Load w/ 3 gal/CFM | 48942.4958
[5 empty] | Variable Speed w/ Unloading | 0.059161 | 0.074359 | 0.064411 | 0.05876 | 0.048318 | 0.048079 | 0.05258 | 0.041394 | 0.047457 | 0.039922 | 0.036957 | 0.026495 | 0.024572 | 0.021277 | 0.016263 | 0.0093774 | 0.0039956 | 0.0016 | 8.5798e-05 | 0 | 0 | 0.67506 | Variable Speed w/ Unloading | 39736.9584
[5 empty] | Load/No Load w/ 5 gal/CFM | 0.059161 | 0.07749 | 0.070137 | 0.065327 | 0.054962 | 0.056733 | 0.064598 | 0.051042 | 0.058756 | 0.05084 | 0.048592 | 0.036564 | 0.03579 | 0.030649 | 0.023111 | 0.013652 | 0.0059933 | 0.0025411 | 0.00014708 | 0 | 0 | 0.80609 | Load/No Load w/ 5 gal/CFM | 47449.4064
[5 empty] | Average % Compressor Capacity | 64.94%
[5 empty] | Modulating w/BD %Full Load kWh/%Capacity | 1 | 1.0421 | 1.0889 | 1.1412 | 1.2 | 1.26 | 1.3286 | 1.4077 | 1.5 | 1.6 | 1.72 | 1.8667 | 2.05 | 2.1714 | 2.3333 | 2.48 | 2.7 | 3.1333 | 4 | 6.5 | #DIV/0!