## Summary
Source | Install VFD on Evaporative Condenser Fan | Install VFD on Cooling Tower Fan | Install VFD on Process Cooling Pump | Install VFD on Evaporator Fans | Install High-Efficiency Air Nozzles
Deemed Savings (kWh/yr/hp) | 860 | 1380 | 800 | 1870
Deemed Savings (kW/hp) | 0.16 | 0.14 | -0.03 | 0.24 | Using PJM method at 84F
Implementation Cost ($/unit) | 370 | 370 | 270 | 600
Measure Life | 15 years | 15 years | 15 years | 15 years
Confidence (1-10, 10 highest) | 8 | 6 | 2 | 7
Conficence description |  | Part load relations at constant load for a cooling tower could be developed. | What is the process and how does it vary?
| Install High-Efficiency Air Nozzles |  | Application | Number of nozzles installed
Deemed Savings (kWh/yr/nozzle) | 1070 |  |  | Make and model
Deemed Savings (kW/nozzle) | 0.17 |  |  | Manufacturer's spec sheet identifying CFM of air consumption
Implementation Cost ($/unit) | 100
Measure Life | 10 Years
Confidence (1-10, 10 highest) | 3
Conficence description | There are a lot of variables that come into play. Savings could be MUCH more or much less.
| Install No-loss Condensate Drains |  | Application | Number of drains installed
Deemed Savings (kWh/yr/drain) | 1610 |  |  | Is a VFD compressor installed at the facility? Y/N
Deemed Savings (kW/drain) | 0.26 |  |  | Make and model
Implementation Cost ($/unit) | 700 |  |  | Manufacturer's spec sheet
Measure Life | 15 years
Confidence (1-10, 10 highest) | 6
Conficence description | Some uncertainty about actual timer settings and ratio of cracked to timer valves.
| Install Low Pressure Drop Filter | …And reduce system pressure
Deemed Savings (kWh/yr/Compressor hp) | 50 |  | Application | Quantity of filters
Deemed Savings (kW/Compressor hp) | 0.01 |  |  | Compressor HP
Implementation Cost ($/unit) | 1000 |  |  | hp of compressors that feed air through filter
Measure Life | 5 years |  |  | Make and model
Confidence (1-10, 10 highest) | 6 |  |  | Manufacturer's spec sheet
Conficence description | Some uncertainty about pressure loss through filters.
Install a Refrigerated Cycling Dryer
Deemed Savings (kWh/yr/Dryer CFM) | 40 |  | Application | Equipment ID/Location
Deemed Savings (kW/Dryer CFM) | 0.0003 |  |  | Dryer Rated CFM
Implementation Cost ($/unit) | 28.603 |  |  | Need make and model of new dryer
Measure Life | 15 years |  |  | State that noncycling dryers do not meet requirements
Confidence (1-10, 10 highest) | 6 |  |  | State that only refrigerated dryers meet requirements
Conficence description | Some uncertainty about how we want to present cost, also seasonal factor |  |  | 50% project cost 100% incremental
Manufacturer's spec sheet

## VFD Evap Condenser
Data for Appendix Summary
ECM Name | Install Variable Speed Drives on Evaporative Condenser Fans |  | Key Assumptions for Deemed Savings Calculations
Peak Summer kW | 1.5899 |  | The evaporative condenser baseline condition has a single-speed fan with on-off operation to maintain condensing temperature
Electricity [kWh] | 8632.9107 |  | The condenser is designed for 95F peak condensing temperature
Natural Gas [therms] | 0 |  | The refrigeration system operates 24/7
Electricity [$] | 690.6329 |  | The load somewhat varies based on outdoor temperature, although there is significant base load due to the freezers or processes in the space
Natural Gas [$] | 0 |  | The distribution of fan sizes is equal across all considered fan sizes (for cost purposes) | [27 empty] | Reference Evaporative Condenser fan size versus rated heat rejection. From Baltimore AirCoil for the VCA models.
Estimated Installed Cost | 3375
Prescriptive Rebate (Leave Blank if N/A) | #REF! | [25 empty] | Lookup Table
MBH Base
R-717 Rated Tons
|  | Measure: | Install Variable Speed Drives on Evaporative Condenser Fans
|  | Description: | Change from on-off cycling of fan for capacity control to VFD drive | [23 empty] | Cost Data
2012 RS Means Mechanical
|  | Specifications, Assumptions, and Formulas | [6 empty] | Weather Data |  |  |  |  | Tons of Cooling (tons) | SCT (F) | Heat Rejection Cap. Factor | Cooling Tower Capacity (tons) | Tower Part Load Ratio | Existing On-off Operation |  |  | Proposed VFD Operation |  |  |  |  | VFD HP | Cost (Incl O&P) | $/hp
Warning - if they currently have two-speed fan control, savings may be significantly less. VFD savings can be very low if they already have 2-speed operation. Calculation heat rejection factors are based on R717 (ammonia). If other refrigerants are used, a different lookup table will be required. |  | Evaporative Condenser Fan Inventory | Horsepower | Estimated Load Factor | Efficiency | MBH Base | Power (kW) |  | TMY3 Dry Bulb BIN Data for CHICAGO OHARE INTL AP | [9 empty] | On-off Power Ratio | Avg. kW | Consumption (kWh) | VFD Power Ratio | Avg. kW | Consumption (kWh) | kW Reduction |  | 3 | 2000 | 666.6667
|  | Generic Evaporative Condenser | 10 | 80% | 93% | 3529.6389 | 6.4172 |  | DB Temperature BIN | Occupied | Unoccupied | Total | MCWB | [12 empty] | OA | 5 | 2150 | 430
[9 empty] | 107.5 | 0 | 0 | 0 | - | [12 empty] | 107.5 | 7.5 | 2575 | 343.3333
[9 empty] | 102.5 | 0 | 0 | 0 | - | [12 empty] | 102.5 | 10 | 2875 | 287.5
[9 empty] | 97.5 | 1 | 0 | 1 | 79.11 | 125 | 92.11 | 1.82 | 129.2908 | 0.96681 | 0.96316 | 6.1808 | 6.1808 | 0.90371 | 6.1045 | 6.1045 | 0.076318 | 97.5 | 15 | 3700 | 246.6667
[9 empty] | 92.5 | 26 | 0 | 26 | 78.3408 | 121.875 | 91.3408 | 1.96 | 120.0557 | 1.0152 | 1 | 6.4172 | 166.8473 | 1 | 6.755 | 175.6287 | -0.33775 | 92.5 | 20 | 4150 | 207.5
[9 empty] | 87.5 | 160 | 0 | 160 | 72.4176 | 115.625 | 85.4176 | 2.14 | 109.9576 | 1.0515 | 1 | 6.4172 | 1026.7527 | 1 | 6.755 | 1080.7923 | -0.33775 | 87.5 | 25 | 5300 | 212
[5 empty] | Total: | 3529.6389 | 6.4172 |  | 82.5 | 428 | 0 | 428 | 69.5289 | 109.375 | 85 | 1.7 | 138.4172 | 0.79018 | 0.7671 | 4.9227 | 2106.899 | 0.49338 | 3.3328 | 1426.4283 | 1.5899 | 82.5 | 30 | 6100 | 203.3333
[9 empty] | 77.5 | 531 | 0 | 531 | 67.5934 | 103.125 | 85 | 1.55 | 151.8124 | 0.67929 | 0.64401 | 4.1328 | 2194.5018 | 0.31345 | 2.1173 | 1124.3116 | 2.0154 | 77.5 | 40 | 6925 | NA
[5 empty] | Total Evaporative Condenser Base Heat Rejection (MBH) | 3529.6389 |  |  | 72.5 | 538 | 0 | 538 | 65.1905 | 96.875 | 85 | 1.43 | 164.5519 | 0.58872 | 0.54348 | 3.4876 | 1876.3377 | 0.20405 | 1.3783 | 741.5334 | 2.1093 | 72.5 | 50 | 8675
|  | Current Operation | [6 empty] | 67.5 | 767 | 0 | 767 | 61.5641 | 90.625 | 85 | 1.25 | 188.2474 | 0.48141 | 0.42437 | 2.7233 | 2088.7469 | 0.11157 | 0.75367 | 578.0623 | 1.9696 | 67.5 | 60 | 10600
|  | Estimated cooling load varies linearly with outside air temperature as follows: | [6 empty] | 62.5 | 848 | 0 | 848 | 57.2744 | 84.375 | 85 | 1.11 | 211.9903 | 0.39801 | 0.33179 | 2.1292 | 1805.5581 | 0.1 | 0.6755 | 572.8199 | 1.4537 | 62.5 | 75 | 11700
You can enter either MBH Base or R-717 Rated Tons for the evaporative condenser size. Calculations assume a 75% adiabatic efficiency compressors. This is fairly accurate - most will be between 65% (reciprocating) and 80% (fully loaded screw). |  |  | 125 | tons of cooling load at |  | 95 | °F and higher |  | 57.5 | 677 | 0 | 677 | 52.6552 | 78.125 | 85 | 1.01 | 232.9795 | 0.33533 | 0.26222 | 1.6827 | 1139.1848 | 0.1 | 0.6755 | 457.3102 | 1.0072 | 57.5 | 100 | 13500
|  |  | 62.5 | tons of cooling load at |  | 45 | °F and lower |  | 52.5 | 641 | 0 | 641 | 47.771 | 71.875 | 85 | 0.97 | 242.5869 | 0.29629 | 0.21888 | 1.4046 | 900.3349 | 0.1 | 0.6755 | 432.9924 | 0.72908 | 52.5 | 125 | 14700
[9 empty] | 47.5 | 408 | 0 | 408 | 43.5612 | 65.625 | 85 | 0.97 | 242.5869 | 0.27052 | 0.19028 | 1.2211 | 498.1923 | 0.1 | 0.6755 | 275.602 | 0.54556 | 47.5 | 150 | 16300
|  | Cooling Tower Approach Temperature (F) | 13 | Estimate |  |  |  |  | 42.5 | 595 | 0 | 595 | 38.9135 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 671.9334 | 0.1 | 0.6755 | 401.9196 | 0.4538 | 42.5 | 200 | 20900
|  | Minimum Condensing Temperature (F) | 85 | Approximate based on existing pressure setpoint of about 150 psig |  |  |  |  | 37.5 | 865 | 0 | 865 | 34.1746 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 976.8444 | 0.1 | 0.6755 | 584.3033 | 0.4538 | 37.5 | Only reviewing costs through 30 hp. Larger cooling towers likely have multiple fans of this size unless dealing with very large industrial or power plant systems not applicable to this measure.
[9 empty] | 32.5 | 759 | 0 | 759 | 29.7523 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 857.1386 | 0.1 | 0.6755 | 512.7008 | 0.4538 | 32.5 | Average $/hp |  | 324.625
|  | VFD Efficiency | 95% | Assumed value |  |  |  |  | 27.5 | 402 | 0 | 402 | 25.2031 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 453.9785 | 0.1 | 0.6755 | 271.5491 | 0.4538 | 27.5 | StDev |  | 159.0222
[9 empty] | 22.5 | 320 | 0 | 320 | 20.2956 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 361.3759 | 0.1 | 0.6755 | 216.1585 | 0.4538 | 22.5
[9 empty] | 17.5 | 382 | 0 | 382 | 15.5614 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 431.3925 | 0.1 | 0.6755 | 258.0392 | 0.4538 | 17.5
|  | Cost Estimate | [6 empty] | 12.5 | 157 | 0 | 157 | 10.6288 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 177.3001 | 0.1 | 0.6755 | 106.0527 | 0.4538 | 12.5
|  |  | VFD hp | Each | Total Cost |  |  |  | 7.5 | 108 | 0 | 108 | 6.0472 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 121.9644 | 0.1 | 0.6755 | 72.9535 | 0.4538 | 7.5
|  | Generic Evaporative Condenser VFD | 10 | 2875 | 2875 | RS Means |  |  | 2.5 | 68 | 0 | 68 | 1.2043 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 76.7924 | 0.1 | 0.6755 | 45.9337 | 0.4538 | 2.5 | Base Heat Rejection Method (MBH) | Fan hp | MBH/hp
|  | Programming Cost |  |  | 500 | Assumed |  |  | -2.5 | 54 | 0 | 54 | -3.6882 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 60.9822 | 0.1 | 0.6755 | 36.4767 | 0.4538 | -2.5 | 1793 | 3 | 597.6667
[9 empty] | -7.5 | 25 | 0 | 25 | -8.3832 | 62.5 | 85 | 0.97 | 242.5869 | 0.25764 | 0.17598 | 1.1293 | 28.2325 | 0.1 | 0.6755 | 16.8874 | 0.4538 | -7.5 | 2029 | 5 | 405.8
[9 empty] | -12.5 | 0 | 0 | 0 | - | [12 empty] | -12.5 | 2205 | 7.5 | 294
[9 empty] | -17.5 | 0 | 0 | 0 | - | [12 empty] | -17.5 | 2367 | 10 | 236.7
[9 empty] | -22.5 | 0 | 0 | 0 | - | [12 empty] | -22.5 | 2264 | 5 | 452.8
|  | Total Estimated Equipment and Installation Cost: |  |  | 3375 |  |  |  | -27.5 | 0 | 0 | 0 | - | [12 empty] | -27.5 | 2499 | 7.5 | 333.2
[9 empty] | -32.5 | 0 | 0 | 0 | - | [12 empty] | -32.5 | 2675 | 10 | 267.5
|  | Summary | [6 empty] | Total Hours | 8760 | 0 | 8760 | [8 empty] | 18027.4712 |  |  | 9394.5604 |  |  | 2617 | 7.5 | 348.9333
|  | VFD Savings | 47.89% | [5 empty] | Occ. Hours: 0:00-24:00 M-F 0:00-24:00 Sat., and 0:00-24:00 Sun. | [17 empty] | 2808 | 10 | 280.8
|  | Peak kW Reduction | 1.5899 | PJM Method at 84F | [22 empty] | 2558 | 5 | 511.6
|  | Annual kWh Reduction | 8632.9107 | [23 empty] | 2822 | 7.5 | 376.2667
|  | Annual Cost Reduction | 690.6329 | [23 empty] | 3028 | 10 | 302.8
|  | Total Installed Cost | 3375 | [23 empty] | 3337 | 15 | 222.4667
|  | Simple Payback | 4.8868 | [23 empty] | 2867 | 5 | 573.4
[27 empty] | 3161 | 7.5 | 421.4667
|  | See Industrial Refrigeration Energy Efficiency Guidebook for formulas and relations | [24 empty] | 3455 | 10 | 345.5
[27 empty] | 3807 | 15 | 253.8
|  | Deemed Savings (kWh/yr/hp) | 860 | [23 empty] | 3837 | 10 | 383.7
|  | Deemed Savings (kW/hp) | 0.16 | PJM Method at 84F | [22 empty] | 4234 | 15 | 282.2667
|  | Implementation Cost ($/unit) | 370 | [23 empty] | 4528 | 20 | 226.4
|  | Measure Life | 15 years | [23 empty] | 4013 | 10 | 401.3
[27 empty] | 4425 | 15 | 295
[27 empty] | 4733 | 20 | 236.65
[27 empty] | 4748 | 10 | 474.8
[27 empty] | 5233 | 15 | 348.8667
|  | Paste these cells into the Bill Calculator: | [24 empty] | 5601 | 20 | 280.05
|  | Month | kWh Reduction | kW Reduction | % On Peak |  | weighting | 35.71% | [18 empty] | 5821 | 15 | 388.0667
|  | Jan | [24 empty] | 6233 | 20 | 311.65
|  | Feb | [24 empty] | 6115 | 15 | 407.6667
|  | Mar | [24 empty] | 6556 | 20 | 327.8
Apr
|  | May | [6 empty] | Note, the peak is set for the max temperature in the month. At cooler temperatures, the refrigeration facility won't be at peak load. | [17 empty] | Average MBH/hp |  | 352.9639
|  | Jun | [24 empty] | StDev |  | 98.0688
Jul
Aug
Sep
Oct
Nov
Dec
Table is based on standard evaporator capacity factors. This particular table is from the BAC Product and Application Handbook, Volume III , page G28. All condensers have very similar curves. The specific curve for the tower would be best, but the error in approximating existing loads is far more significant than the error in this table. This also assumes no scale and "like new" performance, which may not be the case.
[27 empty] | Condensing Pressure (psig) | Condensing Temp (F) | Entering Wet Bulb Temperature (F)
[27 empty] | R-717 |  | 50 | 52 | 54 | 56 | 58 | 60 | 62 | 64 | 66 | 68 | 70 | 72 | 74 | 76 | 78 | 80 | 82
[27 empty] | Lookup Column |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
[28 empty] | -30 | 0.97 | 1.01 | 1.06 | 1.11 | 1.17 | 1.25 | 1.33 | 1.43 | 1.55 | 1.7 | 1.89 | 2.14 | 2.47 | 2.97 | 3.73 | - | - | Added column - basically if the condensing temp is below 80, assume the tower performs like it is 80 (conservative)
[27 empty] | 151.3 | 85 | 0.97 | 1.01 | 1.06 | 1.11 | 1.17 | 1.25 | 1.33 | 1.43 | 1.55 | 1.7 | 1.89 | 2.14 | 2.47 | 2.97 | 3.73 | - | -
[27 empty] | 154.1 | 86 | 0.94 | 0.98 | 1.02 | 1.07 | 1.13 | 1.19 | 1.27 | 1.36 | 1.46 | 1.6 | 1.76 | 1.97 | 2.26 | 2.66 | 3.26 | 4.25 | -
[27 empty] | 156.9 | 87 | 0.91 | 0.95 | 0.99 | 1.03 | 1.08 | 1.14 | 1.21 | 1.29 | 1.39 | 1.51 | 1.65 | 1.83 | 2.08 | 2.4 | 2.88 | 3.63 | -
[27 empty] | 159.8 | 88 | 0.88 | 0.91 | 0.95 | 0.99 | 1.04 | 1.1 | 1.16 | 1.23 | 1.32 | 1.42 | 1.55 | 1.71 | 1.92 | 2.2 | 2.58 | 3.16 | 4.13
[27 empty] | 162.6 | 89 | 0.85 | 0.89 | 0.92 | 0.96 | 1 | 1.05 | 1.11 | 1.18 | 1.26 | 1.35 | 1.46 | 1.6 | 1.78 | 2.02 | 2.34 | 2.8 | 3.53
[27 empty] | 165.5 | 90 | 0.83 | 0.86 | 0.89 | 0.93 | 0.97 | 1.01 | 1.07 | 1.13 | 1.2 | 1.28 | 1.38 | 1.51 | 1.67 | 1.87 | 2.13 | 2.51 | 3.08
[27 empty] | 168.5 | 91 | 0.8 | 0.83 | 0.86 | 0.9 | 0.93 | 0.98 | 1.02 | 1.08 | 1.14 | 1.22 | 1.31 | 1.42 | 1.56 | 1.73 | 1.96 | 2.27 | 2.72
[27 empty] | 171.5 | 92 | 0.78 | 0.81 | 0.83 | 0.87 | 0.9 | 0.94 | 0.99 | 1.04 | 1.1 | 1.17 | 1.25 | 1.35 | 1.47 | 1.62 | 1.82 | 2.08 | 2.44
[27 empty] | 174.5 | 93 | 0.76 | 0.78 | 0.81 | 0.84 | 0.87 | 0.91 | 0.95 | 1 | 1.05 | 1.11 | 1.19 | 1.28 | 1.38 | 1.52 | 1.69 | 1.91 | 2.21
[27 empty] | 177.6 | 94 | 0.74 | 0.76 | 0.79 | 0.81 | 0.84 | 0.88 | 0.92 | 0.96 | 1.01 | 1.07 | 1.13 | 1.21 | 1.31 | 1.43 | 1.58 | 1.77 | 2.02
[27 empty] | 180.7 | 95 | 0.72 | 0.74 | 0.76 | 0.79 | 0.82 | 0.85 | 0.88 | 0.92 | 0.97 | 1.02 | 1.08 | 1.16 | 1.24 | 1.35 | 1.48 | 1.64 | 1.86
[27 empty] | 185 | 96.3 | 0.69 | 0.71 | 0.73 | 0.76 | 0.78 | 0.81 | 0.84 | 0.88 | 0.92 | 0.97 | 1.02 | 1.09 | 1.16 | 1.25 | 1.36 | 1.51 | 1.68
[27 empty] | 187 | 97 | 0.68 | 0.7 | 0.72 | 0.74 | 0.77 | 0.79 | 0.83 | 0.86 | 0.9 | 0.94 | 0.99 | 1.05 | 1.13 | 1.21 | 1.31 | 1.44 | 1.6
[27 empty] | 190.2 | 98 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.77 | 0.8 | 0.83 | 0.87 | 0.91 | 0.96 | 1.01 | 1.07 | 1.15 | 1.24 | 1.35 | 1.49
[27 empty] | 193.4 | 99 | 0.65 | 0.66 | 0.68 | 0.7 | 0.72 | 0.75 | 0.77 | 0.8 | 0.84 | 0.87 | 0.92 | 0.97 | 1.03 | 1.1 | 1.18 | 1.28 | 1.4
[27 empty] | 196.7 | 100 | 0.63 | 0.65 | 0.66 | 0.68 | 0.7 | 0.72 | 0.75 | 0.78 | 0.81 | 0.84 | 0.88 | 0.93 | 0.98 | 1.05 | 1.12 | 1.21 | 1.32
[27 empty] | 213.7 | 105 | 0.56 | 0.57 | 0.58 | 0.6 | 0.61 | 0.63 | 0.65 | 0.67 | 0.69 | 0.71 | 0.74 | 0.77 | 0.81 | 0.85 | 0.89 | 0.95 | 1.01
[27 empty] | 231.8 | 110 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.57 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.71 | 0.74 | 0.78 | 0.82
Rated R717 Conditions, 20F Suction
Note on U16: Bartels, Jeff: Based on IRC Energy Efficiency Guidebook. Tower has 10% capacity with no fan power due to natural convection.
Note on X16: Bartels, Jeff: Based on IRC Energy Efficiency Guidebook. Tower has a heat rejection to the 0.76 power of fan speed. Fan speed is related to hp to the 3 power. Combined, part load ratio to the 3.95 power = fan power. For a more conservative calculation, a cubic relation is used instead. Also, a minimum power of 10% is also used to prevent significantly overstating savings.
Note on F17: Bartels, Jeff: Assume 93%, premium efficiency 20 hp motor. All motors of smaller size will have a lower efficiency, making this calculation more conservative.
Note on G17: Bartels, Jeff: Based on scaling for average ratio of MBH/hp.
Note on D28: Bartels, Jeff: Given the heat rejection of the evaporative condenser and design conditions, the tonnage has been set such that the evaporative condenser is at full load at 95F ambient conditions (design conditions).
Note on C29: Bartels, Jeff: Any standard cooling profiles?
Note on D29: Bartels, Jeff: Cooling load half of the design conditions at lower outdoor temperatures.
Note on D31: Bartels, Jeff: 10-15F is typically a good value.
Note on D32: Bartels, Jeff: Low temperature is limited by defrost or other system factors. This should be a value you obtain on-site.
Note on F40: Bartels, Jeff: Any better sources? I can see this beeing $500-$2000 max.

## VFD Cooling Tower
Data for Appendix Summary
ECM Name | Install Variable Speed Drives on Cooling Tower Fans |  | Key Assumptions for Deemed Savings Calculations | [6 empty] | A cooling tower has a capacity exponent of 0.95, meaning at part load it has more cooling surface per ton of cooling, allowing for more efficient operation.
Peak Summer kW | 1.3764 |  | The evaporative cooling tower baseline condition has a single-speed fan with on-off operation to maintain condensing temperature | [6 empty] | A fan has a capacity exponent of 3 from the affinity laws. The affinity laws work closely here since the system curve changes with varying flow
Electricity [kWh] | 13761.9307 |  | The cooling load occurs 24/7 | [6 empty] | The industrial refrigeration guidebook gives a capacity exponent of 3.95 for fan power.
Natural Gas [therms] | 0 |  | The cooling tower load varies based on outdoor temperature since the tower has a higher differential between cooling water and ambient temperature during cold periods | [6 empty] | As a more conservative estimate, an exponent of 3 is used in this calculator.
Electricity [$] | 1100.9545 |  | The distribution of fan sizes is equal across all considered fan sizes (for cost purposes)
Natural Gas [$] | 0
Estimated Installed Cost | 3375
Prescriptive Rebate (Leave Blank if N/A) | #REF!
|  | Measure: | Install Variable Speed Drives on Cooling Tower Fans
|  | Description: | Change from on-off cycling of fan for capacity control to VFD drive | [16 empty] | Cost Data
2012 RS Means Mechanical
|  | Specifications, Assumptions, and Formulas | [5 empty] | Weather Data |  |  |  |  | % Capacity | Existing |  | Proposed |  |  |  | VFD HP | Cost (Incl O&P) | $/hp
|  | Cooling Tower Fan Inventory | Horsepower | Estimated Load Factor | Efficiency | Power (kW) |  | TMY3 Dry Bulb BIN Data for CHICAGO OHARE INTL AP | [5 empty] | Avg. kW | Consumption (kWh) | Avg. kW | Consumption (kWh) |  |  | 3 | 2000 | 666.6667
|  | Generic Cooling Tower | 10 | 80% | 93% | 6.4172 |  | DB Temperature BIN | Occupied | Unoccupied | Total | MCWB | [5 empty] | kW Reduction |  | 5 | 2150 | 430
[8 empty] | 107.5 | 0 | 0 | 0 | - | 100% | 6.4172 | 0 | 6.755 | 0 | -0.33775 | 107.5 | 7.5 | 2575 | 343.3333
[8 empty] | 102.5 | 0 | 0 | 0 | - | 100% | 6.4172 | 0 | 6.755 | 0 | -0.33775 | 102.5 | 10 | 2875 | 287.5
[8 empty] | 97.5 | 1 | 0 | 1 | 79.11 | 100% | 6.4172 | 6.4172 | 6.755 | 6.755 | -0.33775 | 97.5 | 15 | 3700 | 246.6667
[8 empty] | 92.5 | 26 | 0 | 26 | 78.3408 | 96.5% | 6.1676 | 160.3588 | 6.0702 | 157.8256 | 0.09743 | 92.5 | 20 | 4150 | 207.5
[8 empty] | 87.5 | 160 | 0 | 160 | 72.4176 | 89.5% | 5.6685 | 906.9649 | 4.8427 | 774.8388 | 0.82579 | 87.5 | 25 | 5300 | 212
[5 empty] | Total: | 6.4172 |  | 82.5 | 428 | 0 | 428 | 69.5289 | 82.5% | 5.1694 | 2212.5094 | 3.793 | 1623.4087 | 1.3764 | 82.5 | 30 | 6100 | 203.3333
[8 empty] | 77.5 | 531 | 0 | 531 | 67.5934 | 75.5% | 4.6703 | 2479.9286 | 2.9071 | 1543.6813 | 1.7632 | 77.5 | 40 | 6925 | NA
|  | Current Operation | Cooling tower fans are turned off below: |  |  | -10 | °F | 72.5 | 538 | 0 | 538 | 65.1905 | 68.5% | 4.1712 | 2244.0963 | 2.1712 | 1168.0899 | 2 | 72.5 | 50 | 8675
[8 empty] | 67.5 | 767 | 0 | 767 | 61.5641 | 61.5% | 3.6721 | 2816.4753 | 1.5713 | 1205.1552 | 2.1008 | 67.5 | 60 | 10600
|  | Estimated cooling tower load varies linearly with outside air temperature as follows: | [5 empty] | 62.5 | 848 | 0 | 848 | 57.2744 | 54.5% | 3.173 | 2690.6625 | 1.0935 | 927.273 | 2.0795 | 62.5 | 75 | 11700
|  |  | 100% | of design demand, at |  | 95 | °F and higher | 57.5 | 677 | 0 | 677 | 52.6552 | 47.5% | 2.6738 | 1810.1864 | 0.72394 | 490.108 | 1.9499 | 57.5 | 100 | 13500
|  |  | 30% | of design demand, at |  | 45 | °F and lower | 52.5 | 641 | 0 | 641 | 47.771 | 40.5% | 2.1747 | 1393.995 | 0.44873 | 287.6374 | 1.726 | 52.5 | 125 | 14700
[8 empty] | 47.5 | 408 | 0 | 408 | 43.5612 | 33.5% | 1.6756 | 683.6462 | 0.25395 | 103.6136 | 1.4216 | 47.5 | 150 | 16300
|  | VFD Efficiency | 95% |  |  |  |  | 42.5 | 595 | 0 | 595 | 38.9135 | 30% | 1.426 | 848.497 | 0.18238 | 108.5183 | 1.2437 | 42.5 | 200 | 20900
[8 empty] | 37.5 | 865 | 0 | 865 | 34.1746 | 30% | 1.426 | 1233.5293 | 0.18238 | 157.7619 | 1.2437 | 37.5 | Only reviewing costs through 30 hp. Larger cooling towers likely have multiple fans of this size unless dealing with very large industrial or power plant systems not applicable to this measure.
[8 empty] | 32.5 | 759 | 0 | 759 | 29.7523 | 30% | 1.426 | 1082.3685 | 0.18238 | 138.4292 | 1.2437 | 32.5 | Average $/hp |  | 324.625
|  | Cost Estimate | [5 empty] | 27.5 | 402 | 0 | 402 | 25.2031 | 30% | 1.426 | 573.2703 | 0.18238 | 73.3182 | 1.2437 | 27.5 | StDev |  | 159.0222
|  |  | VFD hp | Each | Total Cost |  |  | 22.5 | 320 | 0 | 320 | 20.2956 | 30% | 1.426 | 456.3345 | 0.18238 | 58.3628 | 1.2437 | 22.5
|  | Generic Cooling Tower VFD | 10 | 2875 | 2875 | RS Means |  | 17.5 | 382 | 0 | 382 | 15.5614 | 30% | 1.426 | 544.7493 | 0.18238 | 69.6706 | 1.2437 | 17.5
|  | Programming Cost |  |  | 500 | Assumed |  | 12.5 | 157 | 0 | 157 | 10.6288 | 30% | 1.426 | 223.8891 | 0.18238 | 28.6342 | 1.2437 | 12.5
[8 empty] | 7.5 | 108 | 0 | 108 | 6.0472 | 30% | 1.426 | 154.0129 | 0.18238 | 19.6974 | 1.2437 | 7.5
[8 empty] | 2.5 | 68 | 0 | 68 | 1.2043 | 30% | 1.426 | 96.9711 | 0.18238 | 12.4021 | 1.2437 | 2.5
[8 empty] | -2.5 | 54 | 0 | 54 | -3.6882 | 30% | 1.426 | 77.0065 | 0.18238 | 9.8487 | 1.2437 | -2.5
[8 empty] | -7.5 | 25 | 0 | 25 | -8.3832 | 30% | 1.426 | 35.6511 | 0.18238 | 4.5596 | 1.2437 | -7.5
|  | Total Estimated Equipment and Installation Cost: |  |  | 3375 |  |  | -12.5 | 0 | 0 | 0 | - | 0% | 0 | 0 | 0 | 0 | 0 | -12.5
[8 empty] | -17.5 | 0 | 0 | 0 | - | 0% | 0 | 0 | 0 | 0 | 0 | -17.5
|  | Summary | [5 empty] | -22.5 | 0 | 0 | 0 | - | 0% | 0 | 0 | 0 | 0 | 0 | -22.5
|  | VFD Savings | 60.54% |  |  |  |  | -27.5 | 0 | 0 | 0 | - | 0% | 0 | 0 | 0 | 0 | 0 | -27.5
|  | Peak kW Reduction | 1.3764 | PJM Method at 84F |  |  |  | -32.5 | 0 | 0 | 0 | - | 0% | 0 | 0 | 0 | 0 | 0 | -32.5
|  | Annual kWh Reduction | 13761.9307 |  |  |  |  | Total Hours | 8760 | 0 | 8760 |  |  |  | 22731.5202 |  | 8969.5895
|  | Annual Cost Reduction | 1100.9545 |  |  |  |  | Occ. Hours: 0:00-24:00 M-F 0:00-24:00 Sat., and 0:00-24:00 Sun.
|  | Total Installed Cost | 3375
|  | Simple Payback | 3.0655
See Industrial Refrigeration Energy Efficiency Guidebook for formulas and relations
|  | Deemed Savings (kWh/yr/hp) | 1380
|  | Deemed Savings (kW/hp) | 0.14 | PJM Method at 84F
|  | Implementation Cost ($/unit) | 370
|  | Measure Life | 15 years
Paste these cells into the Bill Calculator:
|  | Month | kWh Reduction | kW Reduction | % On Peak | weighting | 35.71%
|  | Jan |  |  |  | 0.2
|  | Feb |  |  |  | 0.2
|  | Mar |  |  |  | 0.2
|  | Apr |  |  |  | 0.5
|  | May |  |  |  | 1
|  | Jun |  |  |  | 1
|  | Jul |  |  |  | 1
|  | Aug |  |  |  | 1
|  | Sep |  |  |  | 1
|  | Oct |  |  |  | 0.5
|  | Nov |  |  |  | 0.2
|  | Dec |  |  |  | 0.2
Measure Text
Note on F17: Bartels, Jeff: Assume 93%, premium efficiency 20 hp motor. All motors of smaller size will have a lower efficiency, making this calculation more conservative.
Note on C29: Bartels, Jeff: Any standard profiles?

## VFD Process Pumps
Data for Appendix Summary
ECM Name | Install Variable Speed Drives on Process Pumps |  | Key Assumptions for Deemed Savings Calculations
Peak Summer kW | -1.0025 |  | The evaporative condenser currently has a single-speed fan with on-off operation to maintain condensing temperature
Electricity [kWh] | 24059.1265 |  | The condenser is designed for 95F peak condensing temperature
Natural Gas [therms] | 0 |  | The refrigeration system operates 24/7
Electricity [$] | 1924.7301 |  | The load somewhat varies based on outdoor temperature, although there is significant base load due to the freezers or processes in the space
Natural Gas [$] | 0 |  | The distribution of fan sizes is equal across all considered fan sizes (for cost purposes)
Estimated Installed Cost | 7100
Prescriptive Rebate (Leave Blank if N/A) | #REF!
Measure: Install Variable Speed Drives on Process Pumps
|  | Pump | Generic Process Pump |  |  |  | Totals | 2012 RS Means Mechanical
|  | Pump hp | 30 |  |  |  | 30 | VFD HP | Cost (Incl O&P) | $/hp
|  | Load Factor | 80% |  |  |  |  | 3 | 2000 | 666.6667
|  | Motor Efficiency | 94% |  |  |  |  | 5 | 2150 | 430
|  | Pump kW | 19.0468 |  |  |  | 19.0468 | 7.5 | 2575 | 343.3333
|  | Annual Hours | 6000 |  |  |  |  | 10 | 2875 | 287.5
[8 empty] | 15 | 3700 | 246.6667
|  | VFD Pump Operation | [5 empty] | 20 | 4150 | 207.5
|  | Peak kW | 20.0493 |  |  |  | 20.0493 | 25 | 5300 | 212
|  | Average kW | 15.037 |  |  |  | 15.037 | 30 | 6100 | 203.3333
|  | Peak kW Reduction | -1.0025 |  |  |  | -1.0025 | 40 | 6925 | 173.125
|  | Average kW Reduction | 4.0099 |  |  |  | 4.0099 | 50 | 8675 | 173.5
|  | Annual kWh Reduction | 24059.1265 |  |  |  | 24059.1265 | 60 | 10600 | 176.6667
[8 empty] | 75 | 11700 | 156
|  | VFD Cost (RS Means) | 6100 |  |  |  | 6100 | 100 | 13500 | 135
|  | Programming Cost | 1000 |  |  |  | 1000
|  | Total Installed Cost | 7100 |  |  |  | 7100 | 125 | 14700 | 117.6
[8 empty] | 150 | 16300 | 108.6667
|  | VFD Operation Estimates and Calculations | [5 empty] | 200 | 20900 | 104.5
|  | VFD Efficiency | 95%
|  | % of Full Flow | 100% | 75% | 50% | Operates between 40% and 90% throughout year |  | Average $/hp |  | 233.8786
|  | Hours @ Speed | 2000 | 2000 | 2000 | Assumed to be equally distributed |  | StDev |  | 144.9793
|  | VFD kW Fraction | 1.0526 | 0.78947 | 0.52632 | Linear relation due to process pumping and pressure requirements
|  | Weighted VFD kW Power | 0.78947
Summary
|  | Total kW Reduction | -1.0025 | Penalty assuming peak flow during peak demand conditions (conservative)
|  | Total kWh Reduction | 24059.1265
|  | Estimated Cost | 7100
|  | Annual Cost Savings | 1924.7301
|  | Simple Payback | 3.6888
|  | Deemed Savings (kWh/yr/hp) | 800
|  | Deemed Savings (kW/hp) | -0.03
|  | Implementation Cost ($/unit) | 270
|  | Measure Life | 15 years
|  | Month | kWh Reduction | kW Reduction
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Measure Text
Note on D15: Bartels, Jeff: Selected as a standard size for calculation purposes
Note on D17: Bartels, Jeff: Assumed premium at roughly 40 hp. In general, for process pumps the value will fall between 91 and 96.2% for premium efficiency motors. If they use an existing motor, the efficiency will be less.
Note on D19: Bartels, Jeff: based on a 5 day, 24 hour workweek with 2 weeks shutdown/year.
Note on E19: Bartels, Jeff: hours?
Note on F34: Bartels, Jeff: what should this profile look like? We don't have a good source. Every site is different!

## VFD Evaporator Fans
Data for Appendix Summary
ECM Name | Install Variable Speed Drives on Ventilation Fans |  | Key Assumptions for Deemed Savings Calculations
Peak Summer kW | 0.71228 |  | The evaporator baseline is assumed to be a single speed evaporator motor with on-off thermostat control for the space
Electricity [kWh] | 5622.5654 |  | The condenser is designed for 95F peak condensing temperature
Natural Gas [therms] | 0 |  | The refrigeration system operates 24/7
Electricity [$] | 449.8052 |  | The load somewhat varies based on outdoor temperature, although there is significant base load due to the freezers or processes in the space
Natural Gas [$] | 0 |  | The distribution of fan sizes is equal across all considered fan sizes (for cost purposes)
Estimated Installed Cost | 2500
Prescriptive Rebate (Leave Blank if N/A) | #REF!
|  | Measure: | Install Variable Speed Drives on Ventilation Fans
Specifications, Assumptions, and Formulas
|  | Fan Inventory | Horsepower | Estimated Load Factor | Efficiency | Power (kW) |  | TMY3 Dry Bulb BIN Data for CHICAGO OHARE INTL AP |  |  |  |  | Existing Evaporator Load | Existing Peak kW | Existing Average kW | Existing Annual kWh | VFD % Power | VFD Peak & Avg. kW | Proposed Annual kWh | kW Reduction | kWh Reduction | 2012 RS Means Mechanical
|  | Generic Evap Fan VFD | 3 | 80% | 91% | 1.9675 |  | DB Temperature BIN | Occupied | Unoccupied | Total | MCWB | [9 empty] | VFD HP | Cost (Incl O&P) | $/hp
For help on input variables, please see the help files located here: | [7 empty] | 107.5 | 0 | 0 | 0 | - | 100% | 1.9675 | 1.9675 | 0 | 100% | 2.071 | 0 | -0.10355 | 0 | 3 | 2000 | 666.6667
Q:\Common Files\Tech Resources\Calculators\00 Calculation Guides | [7 empty] | 102.5 | 0 | 0 | 0 | - | 100% | 1.9675 | 1.9675 | 0 | 100% | 2.071 | 0 | -0.10355 | 0 | 5 | 2150 | 430
[8 empty] | 97.5 | 1 | 0 | 1 | 79.11 | 100% | 1.9675 | 1.9675 | 1.9675 | 100% | 2.071 | 2.071 | -0.10355 | -0.10355 | 7.5 | 2575 | 343.3333
[8 empty] | 92.5 | 26 | 0 | 26 | 78.3408 | 96.82% | 1.9675 | 1.9049 | 49.5266 | 86.33% | 1.7879 | 46.4864 | 0.11693 | 3.0402 | 10 | 2875 | 287.5
[8 empty] | 87.5 | 160 | 0 | 160 | 72.4176 | 90.45% | 1.9675 | 1.7797 | 284.7469 | 63.38% | 1.3126 | 210.0204 | 0.46704 | 74.7266 | 15 | 3700 | NA
[8 empty] | 82.5 | 428 | 0 | 428 | 69.5289 | 84.09% | 1.9675 | 1.6545 | 708.1112 | 45.49% | 0.94218 | 403.2543 | 0.71228 | 304.8569 | 20 | 4150
[5 empty] | Total: | 1.9675 |  | 77.5 | 531 | 0 | 531 | 67.5934 | 77.73% | 1.9675 | 1.5293 | 812.0385 | 31.81% | 0.65886 | 349.8534 | 0.87041 | 462.1851 | 25 | 5300
[8 empty] | 72.5 | 538 | 0 | 538 | 65.1905 | 71.36% | 1.9675 | 1.4041 | 755.3842 | 21.58% | 0.44686 | 240.4106 | 0.9572 | 514.9737 | 30 | 6100
|  | Esisting Operation: | On-off Control |  |  |  |  | 67.5 | 767 | 0 | 767 | 61.5641 | 65% | 1.9675 | 1.2789 | 980.8834 | 14.11% | 0.29227 | 224.1747 | 0.98658 | 756.7087 | 40 | 6925
|  | Recommended Operation: | Variable Speed Drive |  |  |  |  | 62.5 | 848 | 0 | 848 | 57.2744 | 58.64% | 1.9675 | 1.1537 | 978.2989 | 10% | 0.2071 | 175.6228 | 0.94655 | 802.6761 | 50 | 8675
|  | VFD Efficiency: | 95% |  |  |  |  | 57.5 | 677 | 0 | 677 | 52.6552 | 52.27% | 1.9675 | 1.0285 | 696.2617 | 10% | 0.2071 | 140.2083 | 0.82135 | 556.0534 | 60 | 10600
[8 empty] | 52.5 | 641 | 0 | 641 | 47.771 | 45.91% | 1.9675 | 0.90325 | 578.9824 | 10% | 0.2071 | 132.7526 | 0.69615 | 446.2298 | 75 | 11700
|  | System Operation: | Space Refrigerated at all times |  |  |  |  | 47.5 | 408 | 0 | 408 | 43.5612 | 39.55% | 1.9675 | 0.77805 | 317.4427 | 10% | 0.2071 | 84.4978 | 0.57094 | 232.945 | 100 | 13500
[8 empty] | 42.5 | 595 | 0 | 595 | 38.9135 | 33.18% | 1.9675 | 0.65284 | 388.4417 | 10% | 0.2071 | 123.2259 | 0.44574 | 265.2158
|  | Estimate evaporator load varies linearly with outside air temperature as follows: | [5 empty] | 37.5 | 865 | 0 | 865 | 34.1746 | 30% | 1.9675 | 0.59024 | 510.5591 | 10% | 0.2071 | 179.1436 | 0.38314 | 331.4156 | 125 | 14700
|  |  | 100% | of design demand, at |  | 95 | °F and higher | 32.5 | 759 | 0 | 759 | 29.7523 | 30% | 1.9675 | 0.59024 | 447.9935 | 10% | 0.2071 | 157.1907 | 0.38314 | 290.8028 | 150 | 16300
|  |  | 30% | of design demand, at |  | 40 | °F and lower | 27.5 | 402 | 0 | 402 | 25.2031 | 30% | 1.9675 | 0.59024 | 237.2772 | 10% | 0.2071 | 83.2552 | 0.38314 | 154.022 | 200 | 20900
[8 empty] | 22.5 | 320 | 0 | 320 | 20.2956 | 30% | 1.9675 | 0.59024 | 188.8774 | 10% | 0.2071 | 66.2728 | 0.38314 | 122.6046 | Only reviewing costs through 10 hp. Most larger evaporators have multiple fans, not larger motors.
|  | Existing and proposed operation are based on relations given in the Industrial Refrigeration Energy Efficiency Guidebook. | [5 empty] | 17.5 | 382 | 0 | 382 | 15.5614 | 30% | 1.9675 | 0.59024 | 225.4724 | 10% | 0.2071 | 79.1131 | 0.38314 | 146.3592 | Average $/hp |  | 431.875
[8 empty] | 12.5 | 157 | 0 | 157 | 10.6288 | 30% | 1.9675 | 0.59024 | 92.668 | 10% | 0.2071 | 32.5151 | 0.38314 | 60.1529 | StDev |  | 167.1471
[8 empty] | 7.5 | 108 | 0 | 108 | 6.0472 | 30% | 1.9675 | 0.59024 | 63.7461 | 10% | 0.2071 | 22.3671 | 0.38314 | 41.3791
[8 empty] | 2.5 | 68 | 0 | 68 | 1.2043 | 30% | 1.9675 | 0.59024 | 40.1364 | 10% | 0.2071 | 14.083 | 0.38314 | 26.0535
|  | Cost Estimate | [5 empty] | -2.5 | 54 | 0 | 54 | -3.6882 | 30% | 1.9675 | 0.59024 | 31.8731 | 10% | 0.2071 | 11.1835 | 0.38314 | 20.6895
|  |  | VFD hp | VFD Installed Cost |  |  |  | -7.5 | 25 | 0 | 25 | -8.3832 | 30% | 1.9675 | 0.59024 | 14.756 | 10% | 0.2071 | 5.1776 | 0.38314 | 9.5785
|  | Generic Evap Fan VFD VFD | 3 | 2000 | RS Means |  |  | -12.5 | 0 | 0 | 0 | - | 30% | 1.9675 | 0.59024 | 0 | 10% | 0.2071 | 0 | 0.38314 | 0
[8 empty] | -17.5 | 0 | 0 | 0 | - | 30% | 1.9675 | 0.59024 | 0 | 10% | 0.2071 | 0 | 0.38314 | 0
[8 empty] | -22.5 | 0 | 0 | 0 | - | 30% | 1.9675 | 0.59024 | 0 | 10% | 0.2071 | 0 | 0.38314 | 0
[8 empty] | -27.5 | 0 | 0 | 0 | - | 30% | 1.9675 | 0.59024 | 0 | 10% | 0.2071 | 0 | 0.38314 | 0
[8 empty] | -32.5 | 0 | 0 | 0 | - | 30% | 1.9675 | 0.59024 | 0 | 10% | 0.2071 | 0 | 0.38314 | 0
[8 empty] | Total Hours | 8760 | 0 | 8760 |  |  |  |  | 8405.4451 |  |  | 2782.8797 |  | 5622.5654
Occ. Hours: 0:00-24:00 M-F 0:00-24:00 Sat., and 0:00-24:00 Sun.
|  | Programming | NA | 500 | Assumed
|  | Total Estimated Equipment and Installation Cost: |  | 2500
Summary
|  | VFD Savings | 66.89%
|  | Peak kW Reduction | 0.71228 | PJM Method at 84F
|  | Annual kWh Reduction | 5622.5654
|  | Annual Cost Reduction | 449.8052
|  | Total Installed Cost | 2500
|  | Simple Payback | 5.558
|  | Deemed Savings (kWh/yr/hp) | 1870
|  | Deemed Savings (kW/hp) | 0.24
|  | Implementation Cost ($/unit) | 600
|  | Measure Life | 15 years
Paste these cells into the Bill Calculator:
|  | Month | kWh Reduction | kW Reduction | kWh weighting
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Measure Text
Note on S15: Bartels, Jeff: Equation is based on the Industrial Refrigeration Energy Efficiency Guidebook. Fan speed to the 0.55 power is equivalent to % capacity. A 2.5 exponent relates fan speed to power. A minimum % power of 10% is applied to not overstate savings. Note that these fans have very low static pressure requirements with no static pressure setpoint, simply a coil that has a squared relationship between flow and pressure loss. The fan can go to very low speed and still have flow.
Note on D16: Bartels, Jeff: Evaporators will have 1 to 10 fans ranging in size from <1 hp to maybe 10 hp. If more airflow is required, the number of fans increases, not necessarily the hp.
Note on F16: Bartels, Jeff: For a 1-10 hp motor, efficiency will range from 85.5 to 91.7% for premium. Assumed 91% as a conservative estimate.

## Install High Efficiency Nozzles
Data for Appendix Summary
ECM Name | Install High-Efficiency Air Nozzles
Peak Summer kW | 0.17358
Electricity [kWh] | 1065.0838
Natural Gas [therms] | 0
Electricity [$] | 85.2067
Natural Gas [$] | 0
Estimated Installed Cost | 100
Prescriptive Rebate (Leave Blank if N/A) | 0
|  | Measure: | Install High-Efficiency Air Nozzles
|  |  | Compressor Information | Notes
The compressor entered here should be the compressor that sees the reduction in demand. For example, if there are 3 compressors base-loaded and 1 compressor that is trim, you would enter the trim compressor since the other compressors would not be impacted by changes in use. |  | Compressor Name/Description | Generic Compressor | Compressor is based on a 100 hp nominal, oil flooded, single-stage, air-cooled, rotary screw machine | [5 empty] | Operation curves and load/unload penalty are from the Compressed Air Challenge
|  | Manufacturer | Generic Compressor
|  | Model | 100 hp nominal
|  | Type - Control | Screw - Inlet Modulation w/ Unloading | Inlet modulation with unloading as a conservative estimate. A VFD compressor would provide more savings for such an application |  |  |  | Compressor Operation Curves | [5 empty] | Load Unload Penalty
|  |  |  | Notes |  |  |  |  | 0-40% Load Curve (y=mx+b) |  | 40-100% Load Curve (y=mx+b) |  |  | % Load | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
|  | Nominal Compressor hp | 100 | Compressor performance based on CAGI datasheets. Ingersoll Rand R75I-A110 used for reference. |  |  |  |  | m | b | m | b |  | Row | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Note that for extremely large reductions in demand that result in a compressor being turned off, a different calculation method would be required. For such a measures, consider the actual pre and post loading of all compressors involved in a separate calculator. |  | Rated Flow (CFM) | 478 |  |  |  |  | Reciprocating - On/off Control | 1 | 0 | 1 | 0 |  | Gal/CFM
|  | Compressor Shaft bhp | [5 empty] | Reciprocating - Load/Unload | 0.74 | 0.26 | 0.74 | 0.26 |  | 0 | 0% | 11% | 20% | 22% | 22% | 20% | 16% | 11% | 8% | 3% | 0% | same as ratio of 1
|  | Pressure at Rated Flow (psig) | 100 |  |  |  |  | Screw - Load/Unload | 0.74 | 0.26 | 0.74 | 0.26 | & penalty | 1 | 0% | 11% | 20% | 22% | 22% | 20% | 16% | 11% | 8% | 3% | 0%
|  | Motor Efficiency | 95.4% |  |  |  |  | Screw - Inlet Modulation | 0.3 | 0.7 | 0.3 | 0.7 |  | 2 | 0% | 7% | 12.5% | 14.5% | 15% | 14% | 11.5% | 8.5% | 6% | 2.5% | 0% | average
|  | VFD Efficiency (if applicable) | [5 empty] | Screw - Inlet Modulation w/ Unloading | 1.4 | 0.26 | 0.3 | 0.7 |  | 3 | 0% | 3% | 5% | 7% | 8% | 8% | 7% | 6% | 4% | 2% | 0%
|  | Motor Load Factor | [5 empty] | Screw - Variable Displacement | 0.6 | 0.26 | 0.83333 | 0.16667 |  | 4 | 0% | 2% | 3.5% | 5% | 5.5% | 5.5% | 5% | 4.5% | 3% | 1.5% | 0% | average
Package input power is a key parameter. It is either calculated from the compressor shaft bhp, or calculated based on the estimated load factor of the compressor. Many times compressor manufacturers will indicated package input power for new compressors, in which case the package input power can be overwritten with the manufacturer supplied value (with notes to the side). |  | Package Input Power (kW) | 87.8 |  |  |  |  | Screw - VFD | 0.8 | 0.1 | 0.96667 | 0.033333 |  | 5 | 0% | 1% | 2% | 3% | 3% | 3% | 3% | 3% | 2% | 1% | 0%
|  | System Storage (gallons) | 956 | Assumed 2 gal/CFM, although this value is not relevant unless load-unload compressor control is selected. | [9 empty] | 7.5 | 0% | 0.5% | 1% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1% | 0.5% | 0% | average
|  | System Pressure | 100 | Assumed 100 psig. 90 psig required by most end uses, so the compressor is at least 5-10 psig higher to account for pressure losses and to allow a storage buffer for demand events. |  |  |  | For the above compressors, Screw - Inlet Modulation machines are assumed to have no peak impact. These machines have little variance. | [5 empty] | 10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Compressor Design Efficacy (CFM/kW) | 5.4442 | For reference
|  | Compressor Operating Efficacy (CFM/kW) | 5.4442 | Adjusted from rated conditions based on actual operating pressure.
|  | System Power Reduction per Reduced Air Demand (kW/CFM) | 0.055105 | Calculated based on the type of compressor control. This assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. |  |  |  | Compressor Adjusted Capacity (CFM) | 478 | http://www.chreed.com/help_pages/quincy_sizing_formulas.htm | [7 empty] | Gal/CFM | 2
[8 empty] | Compressor Adjusted Power (kW) | 87.8 | Based on 1% savings per 2 psig reduction in CA pressure | [7 empty] | Penalty | 0%
If possible, try to look up the CAGI data sheets for the compressor(s). They are usually available and contain many key parameters useful for this analysis. They are available here: |  | Compressed Air System Pressurized Hours | 6136 | From DOE's Evaluation of the Compressed Air Challenge
[8 empty] | Type of Opening | Coefficient of Flow
|  | Existing Air Nozzle Operation | [5 empty] | Well Rounded | 0.97
|  | Location/Process | Generic Blowoff |  |  |  |  | Sharp Edged | 0.61
|  | Annual Operating Hours | 6136
|  | Blow-off Pressure (psig) | 90
|  | Blow-off Type | Intermittent
|  | Cycle Time (seconds) | 100
|  | Blow-off Time per Cycle (seconds) | 30
http://www.cagi.org/verification/ea_sheets.htm |  | Number of Nozzles | 1
|  | Nozzle Inside Diameter (inches) | 0.125
|  | Type of Opening | Sharp Edged |  |  |  |  | Calculation assumes an atmospheric pressure of 14.5 psia. This should be reasonable for most applications. Also, the equation has other inaccuracies that are more significant.
|  | Air Flow through Each Nozzle (CFM) | 21
|  | Air Flow through All Nozzles (CFM) | 21
See this guide to estimate flow through an orifice. |  | Average Flow of Air Loss (CFM) | 6.3
http://www.energystar.gov/ia/business/industry/compressed_air3.pdf
High-Efficiency Air Nozzle Operation
|  | Energy Savings (%) | 50%
|  | Reduced Air Consumption (CFM) | 3.15
|  | Reduced Peak Demand (kW) | 0.17358
|  | Reduced Energy Consumption (kWh) | 1065.0838
|  | Cost per Nozzle | 100
|  | Total Installed Cost | 100 | 0 | 0 | 0 | 0
|  | Description of Input Parameters | Assumed 30% utilization factor for the blowoff application. This will vary since hand-operated blow-off applications could have a very low percentage, and continuous applications on an assembly line may be at 100% utilization. Compressed air nozzle flow conservatively estimated at 15 CFM. Many generic nozzles have flow of such rating. Savings are roughly 50% for an upgrade, although the value varies depending on the actual application.
|  | Summary |  | Notes
|  | Annual Energy Savings (kWh) | 1065.0838
|  | Peak Demand Savings (kW) | 0.17358
|  | Annual Cost Reduction | 85.2067
|  | Total Installed Cost | 100 | Cost is approximate
|  | Simple Payback | 1.1736
|  | Deemed Savings (kWh/yr/nozzle) | 1070
|  | Deemed Savings (kW/nozzle) | 0.17
|  | Implementation Cost ($/unit) | 100
|  | Measure Life | 10 Years
Paste these cells into the Bill Calculator:
|  | Month | kWh Reduction | kW Reduction | % on peak
|  | Jan | 88.757 | 0.17358
|  | Feb | 88.757 | 0.17358
|  | Mar | 88.757 | 0.17358
|  | Apr | 88.757 | 0.17358
|  | May | 88.757 | 0.17358
|  | Jun | 88.757 | 0.17358
|  | Jul | 88.757 | 0.17358
|  | Aug | 88.757 | 0.17358
|  | Sep | 88.757 | 0.17358
|  | Oct | 88.757 | 0.17358
|  | Nov | 88.757 | 0.17358
|  | Dec | 88.757 | 0.17358
1065.0838
Measure Text
Note on F18: Bartels, Jeff: any statistics on what fraction of systems have a VFD for trim? If so, we could apply some weighting to the type of compressor. This applies to all CA calculators. Diana: Accorind to the CAC program (http://www.compressedairchallenge.org/library/evaluation/Evaluation.pdf), maybe 4 out of 100 program participants had improved compressor controls (which could include VSDs), so I say no weighting is necessary.
Note on F42: Bartels, Jeff: see if any other programs have any values for % operating. This is pretty safe, but maybe others are claiming continuous blowoff.
Note on F45: dhusmann: New York TRM confirms this number
Note on F47: Bartels, Jeff: Compare this to other programs. 15 is very conservative, but I can see applications with as high as Diana: NY TRM uses 21.
Note on F52: Bartels, Jeff: Savings from this measure vary depending on the application and selected nozzle. Are the sources below good enough? Sources: Compressed Air Challenge Tipsheet #2 http://www.compressedairchallenge.org/library/tipsheets/tipsheet02.pdf File shows a savings of 75% for installing nozzles on open blow guns. Energy Savings in Compressed Air Systems (Book) Air Power USA, Inc. Page 8-3, Book states that compressed air consumption can be reduced by 50% or more. Scales Industrial Technologies http://www.scalesair.com/equipment/otherproducts/airknives/index.php Website shows savings up to 70% Exair Air Nozzles and Jets http://airnozzles.info/jets_and_nozzles/ajan_page.htm Website shows savings as much as 80% Phase To Inc. http://www.phaseto.com/Noise%20Control%20Spotlight%20-%20Acoustical%20Nozzles.htm Website shows savings up to 50% Diana: I think these are good enough.
Note on F56: Bartels, Jeff: Any sources. I know these cost $100, and $100 is really safe. But there are exceptions really cheap and expensive. Decent source: http://www.airtx.com/ plus $20-$50 installation.

## Install NoLoss CondDrainValves
Data for Appendix Summary
ECM Name | Install No-loss Condensate Drain Valves
Peak Summer kW | 1.047
Electricity [kWh] | 6424.315
Natural Gas [therms] | 0
Electricity [$] | 513.9452
Natural Gas [$] | 0
Estimated Installed Cost | 2800
Prescriptive Rebate (Leave Blank if N/A) | 0
|  | Measure: | Install No-loss Condensate Drain Valves
|  |  | Compressor Information | Notes
The compressor entered here should be the compressor that sees the reduction in demand. For example, if there are 3 compressors base-loaded and 1 compressor that is trim, you would enter the trim compressor since the other compressors would not be impacted by changes in use. |  | Compressor Name/Description | Generic Compressor | Compressor is based on a 100 hp nominal, oil flooded, single-stage, air-cooled, rotary screw machine | [5 empty] | Operation curves and load/unload penalty are from the Compressed Air Challenge
|  | Manufacturer | Generic Compressor
|  | Model | 100 hp nominal
|  | Type - Control | Screw - Inlet Modulation w/ Unloading | Inlet modulation with unloading as a conservative estimate. A VFD compressor would provide more savings for such an application |  |  |  | Compressor Operation Curves | [5 empty] | Load Unload Penalty
|  |  |  | Notes |  |  |  |  | 0-40% Load Curve (y=mx+b) |  | 40-100% Load Curve (y=mx+b) |  |  | % Load | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
|  | Nominal Compressor hp | 100 | Compressor performance based on CAGI datasheets. Ingersoll Rand R75I-A110 used for reference. |  |  |  |  | m | b | m | b |  | Row | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Note that for extremely large reductions in demand that result in a compressor being turned off, a different calculation method would be required. For such a measures, consider the actual pre and post loading of all compressors involved in a separate calculator. |  | Rated Flow (CFM) | 478 |  |  |  |  | Reciprocating - On/off Control | 1 | 0 | 1 | 0 |  | Gal/CFM
|  | Compressor Shaft bhp | [5 empty] | Reciprocating - Load/Unload | 0.74 | 0.26 | 0.74 | 0.26 |  | 0 | 0% | 11% | 20% | 22% | 22% | 20% | 16% | 11% | 8% | 3% | 0% | same as ratio of 1
|  | Pressure at Rated Flow (psig) | 100 |  |  |  |  | Screw - Load/Unload | 0.74 | 0.26 | 0.74 | 0.26 | & penalty | 1 | 0% | 11% | 20% | 22% | 22% | 20% | 16% | 11% | 8% | 3% | 0%
|  | Motor Efficiency | 95.4% |  |  |  |  | Screw - Inlet Modulation | 0.3 | 0.7 | 0.3 | 0.7 |  | 2 | 0% | 7% | 12.5% | 14.5% | 15% | 14% | 11.5% | 8.5% | 6% | 2.5% | 0% | average
|  | VFD Efficiency (if applicable) | [5 empty] | Screw - Inlet Modulation w/ Unloading | 1.4 | 0.26 | 0.3 | 0.7 |  | 3 | 0% | 3% | 5% | 7% | 8% | 8% | 7% | 6% | 4% | 2% | 0%
|  | Motor Load Factor | [5 empty] | Screw - Variable Displacement | 0.6 | 0.26 | 0.83333 | 0.16667 |  | 4 | 0% | 2% | 3.5% | 5% | 5.5% | 5.5% | 5% | 4.5% | 3% | 1.5% | 0% | average
Package input power is a key parameter. It is either calculated from the compressor shaft bhp, or calculated based on the estimated load factor of the compressor. Many times compressor manufacturers will indicated package input power for new compressors, in which case the package input power can be overwritten with the manufacturer supplied value (with notes to the side). |  | Package Input Power (kW) | 87.8 |  |  |  |  | Screw - VFD | 0.8 | 0.1 | 0.96667 | 0.033333 |  | 5 | 0% | 1% | 2% | 3% | 3% | 3% | 3% | 3% | 2% | 1% | 0%
|  | System Storage (gallons) | 956 | Assumed 2 gal/CFM, although this value is not relevant unless load-unload compressor control is selected. | [9 empty] | 7.5 | 0% | 0.5% | 1% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1% | 0.5% | 0% | average
|  | System Pressure | 100 | Assumed 100 psig. 90 psig required by most end uses, so the compressor is at least 5-10 psig higher to account for pressure losses and to allow a storage buffer for demand events. |  |  |  | For the above compressors, Screw - Inlet Modulation machines are assumed to have no peak impact. These machines have little variance. | [5 empty] | 10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Compressor Design Efficacy (CFM/kW) | 5.4442 | For reference
|  | Compressor Operating Efficacy (CFM/kW) | 5.4442 | Adjusted from rated conditions based on actual operating pressure.
|  | System Power Reduction per Reduced Air Demand (kW/CFM) | 0.055105 | Calculated based on the type of compressor control. This assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. |  |  |  | Compressor Adjusted Capacity (CFM) | 478 | http://www.chreed.com/help_pages/quincy_sizing_formulas.htm | [7 empty] | Gal/CFM | 2
[8 empty] | Compressor Adjusted Power (kW) | 87.8 | Based on 1% savings per 2 psig reduction in CA pressure | [7 empty] | Penalty | 0%
If possible, try to look up the CAGI data sheets for the compressor(s). They are usually available and contain many key parameters useful for this analysis. They are available here: |  | Compressed Air System Pressurized Hours | 6136 | From DOE's Evaluation of the Compressed Air Challenge
Existing Condensate Drains
|  | Location | Cracked Open Valve | Timer Drain Valve
|  | Type | Continuous | Timer Drain
http://www.cagi.org/verification/ea_sheets.htm |  | Quantity | 1 | 3
|  | Time Between Valve Cycling (seconds) | NA | 300
|  | Valve Open Time (seconds) | NA | 10
|  | Flow through Open Drain (CFM) | 10 | 90
|  | Average CFM Flow per Drain | 10 | 3 | 0 | 0 | 0
See this guide to estimate flow through an orifice. |  | Total Air Consumption (CFM) | 10 | 9 | 0 | 0 | 0
http://www.energystar.gov/ia/business/industry/compressed_air3.pdf
Proposed No-loss Condensate Drains
|  | Total Air Consumption (CFM) | 0 | 0 | 0 | 0 | 0
|  | Reduced Air Consumption (CFM) | 10 | 9 | 0 | 0 | 0
|  | Reduced Peak Demand (kW) | 0.55105 | 0.49594 | 0 | 0 | 0
|  | Reduced Energy Consumption (kWh) | 3381.2184 | 3043.0966 | 0 | 0 | 0
|  | Cost per No-loss Drain | 700 | 700 | 0 | 0 | 0
|  | Total Installed Cost | 700 | 2100 | 0 | 0 | 0
|  | Description of Input Parameters | Cost based on example projects from ComEd CA program. Savings based on a 3 to 1 ratio of timer drains to cracked valves
|  | Summary |  | Notes
|  | Annual Energy Savings (kWh) | 6424.315
|  | Peak Demand Savings (kW) | 1.047
|  | Annual Cost Reduction | 513.9452
|  | Total Installed Cost | 2800
|  | Simple Payback | 5.4481
|  | Deemed Savings (kWh/yr/drain) | 1610
|  | Deemed Savings (kW/drain) | 0.26
|  | Implementation Cost ($/unit) | 700
|  | Measure Life | 15 years
Paste these cells into the Bill Calculator:
|  | Month | kWh Reduction | kW Reduction | % on peak
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
0
Measure Text
Note on G42: Bartels, Jeff: Valve will open for 5-30 seconds to push the moisture and water out of the line.
Note on F43: Bartels, Jeff: Estimate based on cracked open valve.
Note on G43: Bartels, Jeff: The valve will have an orifice of 1/4 to 3/8 inch in diameter, corresponding to a flow of 60-150 CFM @ 100 psig. 90 used for an approximation.
Note on F55: Bartels, Jeff: is this truly the ratio? From what I see in the field, it's pretty close

## Install Low P Filter
Data for Appendix Summary
ECM Name | Reduce Compressed Air System Pressure
Peak Summer kW | 0.82532
Electricity [kWh] | 5064.1635
Natural Gas [therms] | 0
Electricity [$] | 405.1331
Natural Gas [$] | 0
Estimated Installed Cost | 1000
Prescriptive Rebate (Leave Blank if N/A) | 0
|  | Measure: | Reduce Compressed Air System Pressure
|  |  | Compressor Information |  |  |  | Notes
|  | Compressor Name/Description | Generic Compressor |  |  |  | Compressor is based on a 100 hp nominal, oil flooded, single-stage, air-cooled, rotary screw machine |  |  | Operation curves and load/unload penalty are from the Compressed Air Challenge
|  | Manufacturer | Generic Compressor
|  | Model | 100 hp nominal
|  | Type - Control | Screw - Inlet Modulation w/ Unloading |  |  |  | Inlet modulation with unloading as a conservative estimate. A VFD compressor would provide more savings for such an application | Compressor Operation Curves | [5 empty] | Load Unload Penalty
[9 empty] | 0-40% Load Curve (y=mx+b) |  | 40-100% Load Curve (y=mx+b) |  |  | % Load | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
|  | Nominal Compressor hp | 100 |  |  |  | Compressor performance based on CAGI datasheets. Ingersoll Rand R75I-A110 used for reference. |  | m | b | m | b |  | Row | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
|  | Rated Flow (CFM) | 478 |  |  |  |  | Reciprocating - On/off Control | 1 | 0 | 1 | 0 |  | Gal/CFM
|  | Compressor Shaft bhp | [5 empty] | Reciprocating - Load/Unload | 0.74 | 0.26 | 0.74 | 0.26 |  | 0 | 0% | 11% | 20% | 22% | 22% | 20% | 16% | 11% | 8% | 3% | 0% | same as ratio of 1
|  | Pressure at Rated Flow (psig) | 100 |  |  |  |  | Screw - Load/Unload | 0.74 | 0.26 | 0.74 | 0.26 | & penalty | 1 | 0% | 11% | 20% | 22% | 22% | 20% | 16% | 11% | 8% | 3% | 0%
|  | Motor Efficiency | 95.4% |  |  |  |  | Screw - Inlet Modulation | 0.3 | 0.7 | 0.3 | 0.7 |  | 2 | 0% | 7% | 12.5% | 14.5% | 15% | 14% | 11.5% | 8.5% | 6% | 2.5% | 0% | average
|  | VFD Efficiency (if applicable) | [5 empty] | Screw - Inlet Modulation w/ Unloading | 1.4 | 0.26 | 0.3 | 0.7 |  | 3 | 0% | 3% | 5% | 7% | 8% | 8% | 7% | 6% | 4% | 2% | 0%
|  | Motor Load Factor | [5 empty] | Screw - Variable Displacement | 0.6 | 0.26 | 0.83333 | 0.16667 |  | 4 | 0% | 2% | 3.5% | 5% | 5.5% | 5.5% | 5% | 4.5% | 3% | 1.5% | 0% | average
Package input power is a key parameter. It is either calculated from the compressor shaft bhp, or calculated based on the estimated load factor of the compressor. Many times compressor manufacturers will indicated package input power for new compressors, in which case the package input power can be overwritten with the manufacturer supplied value (with notes to the side). |  | Package Input Power (kW) | 87.8 | 0 | 0 | 0 |  | Screw - VFD | 0.8 | 0.1 | 0.96667 | 0.033333 |  | 5 | 0% | 1% | 2% | 3% | 3% | 3% | 3% | 3% | 2% | 1% | 0%
|  | System Storage (gallons) | 956 | NA | NA | NA | Assumed 2 gal/CFM, although this value is not relevant unless load-unload compressor control is selected. | [6 empty] | 7.5 | 0% | 0.5% | 1% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1% | 0.5% | 0% | average
|  | System Pressure | 100 |  |  |  | Assumed 100 psig. 90 psig required by most end uses, so the compressor is at least 5-10 psig higher to account for pressure losses and to allow a storage buffer for demand events. | For the above compressors, Screw - Inlet Modulation machines are assumed to have no peak impact. These machines have little variance. | [5 empty] | 10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Compressor Operating Hours | 6136 |  |  |  | From DOE's Evaluation of the Compressed Air Challenge
|  | Peak Demand Operation | Operates On-peak
|  | Compressor % Capacity | 80% |  |  |  | Assumed not at full load all of the time | Compressor Adjusted Capacity (CFM) | 478 | http://www.chreed.com/help_pages/quincy_sizing_formulas.htm | [7 empty] | Gal/CFM | 2
|  | Compressor Power (kW) | 82.532 | 0 | 0 | 0 | Adjusted based on compressor loading and operating pressure | Compressor Adjusted Power (kW) | 87.8 | Based on 1% savings per 2 psig reduction in CA pressure | [7 empty] | Penalty | 0%
If possible, try to look up the CAGI data sheets for the compressor(s). They are usually available and contain many key parameters useful for this analysis. They are available here: |  | Compressor Energy Use (kWh) | 506416.352 | 0 | 0 | 0 | Calculated
Existing System Operation
|  | System Pressure (psig) | 100 | Current operation with high pressure loss filter
|  | Peak Demand (kW) | 82.532 | Calculated from entries above
http://www.cagi.org/verification/ea_sheets.htm |  | Annual Energy Use (kWh) | 506416.352 | Calculated from entries above
Proposed Operation
|  | Reduced Filter Loss (psi) | 2 | Pressure will be reduced from a roughly 3 psi pressure drop through a filter to less than 1 psi, for a 2 psi savings.
|  | New System Pressure (psig) | 98 | Calc.
See this guide to estimate flow through an orifice. |  | Peak Demand (kW) | 81.7067 | Calculated based on 1% reduction in power per 2 psi reduction in system pressure
http://www.energystar.gov/ia/business/industry/compressed_air3.pdf |  | Annual Energy Use (kWh) | 501352.1885 | Calculated based on 1% reduction in energy consumption per 2 psi reduction in system pressure
Description of Input Parameters
|  | Summary |  | Notes
|  | Baseline Energy Use (kWh) | 506416.352
|  | Upgrade Energy Use (kWh) | 501352.1885
|  | Annual Energy Savings (kWh) | 5064.1635
|  | Savings % | 1%
|  | Peak Demand Savings (kW) | 0.82532
|  | Annual Cost Reduction | 405.1331
|  | Total Installed Cost | 1000 | No source - simply an estimate based on knowledge of systems
|  | Simple Payback | 2.4683
|  | Deemed Savings (kWh/yr/Compressor hp) | 50
|  | Deemed Savings (kW/Compressor hp) | 0.01
|  | Implementation Cost ($/unit) | 1000
|  | Measure Life | 5 years
Element should be replaced as required to sustain low pressure drop. New type of filter will remain in place for many years.
Paste these cells into the Bill Calculator:
|  | Month | kWh Reduction | kW Reduction | % on peak
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Measure Text
Note on G43: Bartels, Jeff: investigate this comment Diana: The DOE (http://www1.eere.energy.gov/manufacturing/tech_deployment/pdfs/compressed_air14.pdf) says no more than 3 psi. The CAC says no more than 2-3 psi. Washington State, Rhode Island, and Connecticut require the low pressure drop filter to be 1 psi or less.

## Install Cycling Dryer
Cycling Dryer Calculations
Calculations are based on Zeks cycling dryer savings calculations and factors
Reference calculations based on 1,000 CFM cycling dryer (air cooled) assuming it is properly sized with the correct adjustments for operating conditions
Refrigerated dryers are rarely shut off.
Compressed Air Load Description
Compressed Air System Operating Hours | 6136 | From DOE's Evaluation of the Compressed Air Challenge
Average % Flow | 70% | Assumed dryer is not at full flow at all times, although near full flow for a conservative estimate
Dryer Inlet Pressure (psig) | 100 | Assumed 100 psig. 90 psig required by most end uses, so the compressor is at least 5-10 psig higher to account for pressure losses and to allow a storage buffer for demand events.
Non Cycling Dryer Operation
Rated Capacity (CFM) | 1000
Dryer Rated kW | 6.5 | Zeks 1000 NCF
Operating Hours | 8760 | Dryer operates continuously
Peak Demand (kW) | 6.5
Annual Energy Consumption (kWh/yr) | 56940
Cycling Dryer Operation
Rated Capacity (CFM) | 1000
Dryer Rated kW | 8.9 | Zeks 1000 HSF
Operating Hours | 8760 | Dryer operates continuously
Flow Factor | 0.7 | Based on operating at 70% flow
Operating Hours Factor | 0.70046 | Based on only operating loaded 6,000 out of 8,760 hours
Ambient Temperature Factor | 0.5 | Based on AirPower USA book "Energy Savings in Compressed Air Systems." pg 2-15. Monitored operation in the northern US has the refrigeration compressor loaded about 50% of the time. This conservatively agrees with the Zeks value of 0.31, and also agrees with Nexant measured values of less than 25% load on a cycling dryer.
Dryer Utilization Factor | 0.24516
Average Dryer kW | 2.1819
Annual Energy Consumption (kWh/yr) | 19113.64
Summary
Average Demand Reduction (kW) | 4.3181 | Average
Peak Demand Reduction (kW) | 0.27 | Average assuming the unit is at a higher moisture load in the summer months and peak occurs during operation hours
Annual Energy Use Reduction (kWh/yr) | 37826.36
1000 CFM Cycling Dryer Cost | 15000 | Based on an installed project
Installation Cost | 13603 | Based on an installed project
Total Installed Cost | 28603
Deemed Savings (kWh/yr/Dryer CFM) | 40
Deemed Savings (kW/Dryer CFM) | 0.0003
Implementation Cost ($/unit) | 28.603
Measure Life | 15 years
Note on D15: Bartels, Jeff: look into average size dryers, etc. Diana: This seems large, because the CLC has calculations for air dryers rangine from less than 100 CFM to more than 400. Consumers Energy has prescriptive incentives up to 600 CFM only. Jeff and I think that having the incentive/CFM will make this a non-issue.
Note on E27: Bartels, Jeff: any other sources, studies? Diana: HeatSink (http://www.glauber.com/Products/Compressors/zeks/zeks1/zeks2) recommends 0.24. I feel like these sites are inclined to report lower numbers though.
Note on D38: Bartels, Jeff: Is this cost okay? I know it is real. The incremental cost is a LOT less, more like $3,000 for this size machine. Are we doing incremental or full?