Memorandum

To:	Technical Advisory Committee

FROM:	KEITH CRONIN, PROJECT LEAD, and SAM DENT, TECHNICAL LEAD - VEIC

subject:	v13.0 Errata Measures effective 01/01/2025

Date:	08/01/2025

Cc:	CELIA JOHNSON, SAG

This memo documents errata changes to Version 13.0 of the Illinois Technical Reference Manual (TRM) that the Technical Advisory Committee (TAC) recommends be made effective 01/01/2025.

VEIC has provided a summary table below showing the errata measures and a brief summary of what was changed, followed by the v13.0 measures themselves.

TRM Policy Document, Section 3.2.1, states that,

“TAC participants should notify the TAC when a TRM mistake or omission is found. If a significant mistake or omission is found in the TRM that results in an unreasonable savings estimate, the Program Administrators, Evaluators, TRM Administrator, and TAC will strive to reach consensus on a solution that will result in a reasonable savings estimate. For example, an unreasonable savings estimate may result from an error or omission in the TRM.

“In these limited cases where consensus is reached, the TRM Administrator shall inform the Evaluators to use corrected TRM algorithms and inputs to calculate energy and capacity savings, in addition to using the Commission-approved TRM algorithms and inputs to calculate savings. If the corrected TRM algorithms and inputs are stipulated for acceptance by all the parties in the Program Administrator’s savings docket, then the corrected TRM savings verification values may be used for the purpose of measuring savings toward compliance with the Program Administrator’s energy savings goals. Errors and omissions found in the TRM will be officially corrected through the annual TRM Update proceeding and will be identified as ‘Errata’.”

It is our belief and understanding that the following measures have been determined to be consensus errata by the Program Administrators, Evaluators, and the entire TAC. The term ‘errata’ is used to describe these measures, and in accordance with the TRM Policy Document, the Evaluators may use this version of the measures during evaluation of the current program year (in addition to the measures currently in Version 13.0 of the TRM).

Summary of Errata Measures

| Section | Measure Name | Measure Code | Brief Summary of Change | TAC Reviewed and Approved As of |
| --- | --- | --- | --- | --- |
| 4.4.9 | Air and Water Source Heat Pump Systems (Centrally Ducted and Ductless) | CI-HVC-HPSY-V13-250101 | Error in ASHPSiteHeatingImpact algorithm for non-fuel switch measures >60kBtuh. A 3412 btu/kWh factor is provided since calculation uses COP for efficiency, however it was erroneously only applied to the baseline heatload. Edits to unit conversions when using COP efficiency ratings. | 01/01/2025 |
| 4.4.15 | Single-Package and Split System Unitary Air Conditioners | CI-HVC-SPUA-V11-250101 | Corrected code baseline SEER2 value for split systems <65,000 Btu/h. Value was incorrectly transcribed from code. The compliance date for these baseline systems was also incorrect, updated that as well. Also made minor adjustments/updates, transitioning the SEER/EER metrics for systems <65,000 Btu/h to SEER2/EER2 | 01/01/2025 |
| 4.4.58 | Steam Trap Monitoring System | CI-HVC-STMS-V2-250101 | Correct deemed table values for process heating based on variable inputs provided. | 07/07/2025 |
| 4.4.60 | Variable Refrigerant Flow HVAC System | CI-HVC-VFFY-V4-250101 | Energy saving algorithm for units >65 kBtu/hr should use IEER rather than EER. | 01/01/2025 |
| 4.8.8 | Commercial Secondary Windows | CI-SHL-CSW-V02-250101 | Fixing Fossil Fuel algorithm to divide by heating efficiency, not multiply. | New |
| 5.6.3 | Floor Insulation Above Crawlspace | RS-SHL-FINS-V17-250101 | CDD and HDD fixed to reflect Conditioned spaces since measure will be between conditioned space and vented crawlspace. | New |

### 4.4.9	Air and Water Source Heat Pump Systems (Centrally Ducted and Ductless)

###### Description

This measure applies to the installation of high-efficiency air cooled and water source heat pump systems with conditioned air delivered to the building via ductwork, ductless systems and “hybrid” systems that work in conjunction with fuel-fired heating systems. This measure could apply to replacing an existing unit at the end of its useful life, or installation of a new unit in a new or existing building.

This measure was developed to be applicable to the following program types: TOS, NC, EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

In order for this characterization to apply, the efficient equipment is assumed to be a high-efficiency air cooled or water source, heat pump system that exceeds the baseline and meets program requirements.

###### Definition of Baseline Equipment

New construction / Time of Sale: To calculate savings with an electric baseline, the baseline equipment is assumed to be a standard-efficiency air cooled or water source heat pump system that meets the Code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher) in effect on the date of equipment purchase (if date unknown assume current Code minimum).  The rating conditions for the baseline and efficient equipment efficiencies must be equivalent.

To calculate savings with a furnace/ AC baseline, the baseline equipment is assumed to meet the Code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher).

Where unknown, the baseline should be determined via EM&V and the algorithms are provided to allow savings to be calculated from any baseline condition.

In order for this characterization to apply, the baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit. As code requirements and adoption can differ from municipality to municipality, the user should verify which version of code is applicable given these constraints.

Note, IECC 2021 is became effective statewide on 1/1/2024. IECC 2018 is the requisite code for any projects with permitting dates spanning July 1, 2019 to 12/31/2023. Prior to July 1, 2019, IECC 2015 is the applicable code. If evaluation determines the applicable version of code, given location and timing, isn’t an appropriate baseline due to supply constraints, low compliance, or other issues, the previous iteration of code may be used through 2023.

IECC 2021 leverages new DOE testing methods and associated metrics. The following conversion factors are recommended for use if the efficient equipment is not rated under the new testing procedure but the stipulated baseline is:

SEER2 = X * SEER

EER2 = X * EER

HSPF2 = X * HSPF

Where:

| X | SEER2 | EER2 | HSPF2 |
| --- | --- | --- | --- |
| Ducted | 0.95 | 0.95 | 0.85 |
| Ductless | 1.00 | 1.00 | 0.90 |
| Packaged | 0.95 | 0.95 | 0.84 |

Note: new Federal Standards affecting heat pumps and air conditioning equipment became effective January 1, 2023.

Early replacement / Retrofit: The baseline for this measure is the efficiency of the existing heating and cooling equipment for the assumed remaining useful life of the existing unit and a new baseline heating and cooling system meeting the code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher) for the remainder of the measure life.

A weighted average early replacement rate is provided for use in programs when the actual baseline early replacement rates are unknown.

Deemed Early Replacement Rates For ASHP

| Equipment Type | Full System Displacement | Partial System Displacement |
| --- | --- | --- |
| Cooling | 30% | 30% |
| Heating | 30% | 100% |

Note to apply these deemed early replacement rates, an assumption of the percentage of replacements that are full displacement v partial displacement is required. This should be determined through evaluation, or a deemed ratio of 100% Full Displacement for ducted ASHPs and 50% Full: 50% Partial for Ductless ASHPs can be used. Savings should be calculated following both the full and partial displacement methodology and then this ratio should be used to weight the savings accordingly.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 16 years.

Remaining life of existing equipment is assumed to be 6 years for ASHP and Central AC, 6 years for furnace, 8 years for boilers and 16 years for electric resistance.

###### Deemed Measure Cost

Ducted Air Source Heat Pumps:

New Construction and Time of Sale: For analysis purposes, the incremental capital cost for this measure is assumed as $100 per ton for air-cooled units. The incremental cost for all other equipment types should be determined on a site-specific basis.

Early Replacement: The actual full installation cost of the Heat Pump (including any necessary electrical or distribution upgrades required) should be used. The assumed deferred cost of replacing existing equipment with a new baseline unit should also be incorporated.

Ductless Minisplit Heat Pumps:

New Construction and Time of Sale: The actual installed cost of the DMSHP (including any necessary electrical or distribution upgrades required) should be used (defaults are provided below), minus the assumed installation cost of the baseline equipment ($6,562 + $600 per ton for ASHP, or $2,011 for a new baseline 80% AFUE furnace, or $4,053 for a new 84% AFUE boiler, and $952 per ton for new baseline Central AC replacement ).

Default full cost of the DMSHP is provided below. Note, for smaller units a minimum cost of $2,000 should be applied:

| Unit Size | Full Install Cost ($/ton) |
| --- | --- |
| 9-9.9 | $1,443 |
| 10-10.9 | $1,605 |
| 11-12.9 | $1,715 |
| 13+ | $2,041 |

The incremental cost of the DSMHP compared to a baseline minimum efficiency DSMHP is provided in the table below:

| Efficiency (HSPF2) | Incremental Cost ($/ton) over an HSPF2 7.5 DHP |
| --- | --- |
| 8.1-8.9 | $62 |
| 9-9.8 | $224 |
| 9.9-11.6 | $334 |
| 11.7+ | $660 |

Early Replacement/retrofit (replacing existing equipment): The actual full installation cost of the DMSHP (including any necessary electrical or distribution upgrades required) should be used. The assumed deferred cost (after 8 years) of replacing existing equipment with a new baseline unit is assumed to be $7,527 + $688 per ton for a new baseline Air Source Heat Pump, or $2,296 for a new baseline 80% AFUE furnace or $4,627 for a new 84% AFUE boiler and $1,047 per ton for new baseline Central AC replacement. If replacing electric resistance heat, there is no deferred replacement cost. This future cost should be discounted to present value using the nominal societal discount rate.

Where the DMSHP is a supplemental HVAC system, the full installation cost of the DMSHP (including any necessary electrical or distribution upgrades required) should be used without a deferred replacement cost.

If the install cost is unknown a default is provided above. Fuel switch scenarios are likely to require additional installation work which may include adding new electrical circuits, capping existing gas lines and upgrading electrical panels. These costs are likely to range significantly and actual values should be used wherever possible. If unknown, assume an additional $300 for fuel switch installations.

###### Loadshape

Loadshape C05 - Commercial Electric Heating and Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.  Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Savings

###### Electric And Fossil Fuel Energy Savings

Non fuel switch measures:

ΔkWhNon Fuel Switch	= ASHPSiteCoolingImpact + ASHPSiteHeatingImpact

Where:

For units with cooling capacities less than 65 kBtu/hr (ASHP only):

ASHPSiteCoolingImpact	= ((CoolingLoad/DuctlessSave * (1/(SEER2_base))) – (CoolingLoad * 1/(SEER2_ee )))/1,000

ASHPSiteHeatingImpact	= ((HeatLoad_Disp/DuctlessSave * (1/(HSPF2_base * HSPF2_ClimateAdj))) – (HeatLoad_Disp * 1/(HSPF2_ee * HSPF2_ClimateAdj))) / 1,000

For ASHP units with cooling capacities equal to or greater than 65 kBtu/hr and all WSHPs:

ΔkWhNon Fuel Switch	= ASHPSiteCoolingImpact + ASHPSiteHeatingImpact

Where:

ASHPSiteCoolingImpact	= ((CoolingLoad * (1/(IEER_base))) – (CoolingLoad * 1/(IEER_ee )))/1,000

ASHPSiteHeatingImpact	= (HeatLoad_Disp / 3,412 * (1/COP_base – 1/COP_ee))

Fuel switch measures:

Fuel switch measures must produce positive total lifecycle energy savings (i.e., reduction in Btus at the premises) in order to qualify. This is determined as follows (note for early replacement measures the lifetime savings should be calculated by calculating savings for the remaining useful life of the existing equipment and for the remaining measure life):

SiteEnergySavings (MMBTUs)	= FuelSwitchSavings + NonFuelSwitchSavings

FuelSwitchSavings	= GasHeatReplaced - HPSiteHeatConsumed

NonFuelSwitchSavings	= FurnaceFanSavings + HPSiteCoolingImpact

For units with cooling capacities less than 65 kBtu/hr (ASHP only):

ASHPSiteHeatConsumed	= ((HeatLoad_Disp * (1/(HSPF2_ee * HSPF2_ClimateAdj * PD_Adj))) /1,000  * 3,412)/ 1,000,000

ASHPSiteCoolingImpact 	= (((CoolingLoad/DuctlessSave * (1/(SEER2_base)) – ((CoolingLoad * 1/(SEER2_ee)))/1,000 * 3412) / 1,000,000

FurnaceFanSavings	= (FurnaceFlag * HeatLoad_Disp/DuctlessSave * 1/AFUEbase * Fe) / 1,000,000

GasHeatReplaced		= (HeatLoad_Disp/DuctlessSave * 1/AFUEbase) / 1,000,000

For ASHP units with cooling capacities greater than 65 kBtu/hr and all WSHPs:

ASHPSiteHeatConsumed	= (HeatLoad_Disp * (1/(COP_ee * PD_Adj))) / 1,000,000

ASHPSiteCoolingImpact 	= (((CoolingLoad * (1/(IEER_base)) – ((CoolingLoad * 1/(IEER_ee)))/1,000 * 3,412) / 1,000,000

FurnaceFanSavings	= (FurnaceFlag * HeatLoad_Disp * 1/AFUEbase * Fe) / 1,000,000

GasHeatReplaced		= (HeatLoad_Disp * 1/AFUEbase) / 1,000,000

If SiteEnergySavings calculated above is positive, the measure is eligible.

The appropriate savings claim is dependent on which utilities are supporting the measure as provided in a table below:

| Measure supported by: | Electric Utility claims (kWh): | Gas Utility claims (therms): |
| --- | --- | --- |
| Electric utility only | SiteEnergySavings * 1,000,000/3,412 | N/A |
| Electric and gas utility (Note utilities may make alternative agreements to how savings are allocated as long as total MMBtu savings remains the same). | %IncentiveElectric * SiteEnergySavings * 1,000,000/3,412 | %IncentiveGas * SiteEnergySavings * 10 |
| Gas utility only | N/A | SiteEnergySavings * 10 |

Note for Early Replacement measures, the efficiency terms of the existing unit should be used for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 6 years for furnace, 8 years for boilers, 15 years for electric resistance), and the efficiency terms for a new baseline unit should be used for the remaining years of the measure. See assumptions below.

Programs where existing system unknown

In programs where the existing fuel or system type is unknown, savings should be apportioned between the Fuel Switch and Non- Fuel Switch scenarios, as follows:

Savings from Non-Fuel Switch (kWh) 	= (1 – %FuelSwitch) * ΔkWhNon Fuel Switch

Plus

Savings from Fuel Switch (MMBtu converted to appropriate fuel as table above)

= %FuelSwitch * SiteEnergySavings (MMBTUs)

Where:

%FuelSwitch 	= The percentage of replacements resulting in fuel-switching.

= 1 when fuel switching is known, 0 if non fuel switch

= when unknown, e.g. midstream program, determine via evaluation

CoolingLoad 	= Annual cooling load for the building

= EFLHcool * Capacitycool

Capacitycool	= Output capacity of the cooling equipment in Btu per hour (1 ton of cooling capacity equals 12,000 Btu/hr).

= Actual installed

SEER2base	= Seasonal Energy Efficiency Ratio of the baseline equipment

= SEER from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code).

SEER2ee		= Seasonal Energy Efficiency Ratio of the energy efficient equipment.

= Actual installed

EFLHcool	= Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

DuctlessSave	= Factor used to adjust ducted heating or cooling load displaced by ductless systems that are not subject to losses from existing ductwork.

= 1-0.15 = 0.85 for ducted system displaced by ductless system

= 1.00 for ducted system displaced by ducted system or ductless system displaced by ductless system

HSPF2base	= Heating Seasonal Performance Factor of the baseline equipment

= HSPF from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume a blended baseline value of 5.1 HSPF2).

HSPF2ee	= Heating Seasonal Performance Factor of the energy efficient equipment.

= Actual installed. If rating is COP, HSPF = COP * 3.413

HSPF_ClimateAdj	= Adjustment factor to account for observed discrepency between seasonal heating performance relative to rated HSPF as provided by standard AHRI 210/240 rating conditions. Note, the adjustment is dependent on the test method use for the rating (i.e. HSPF or HSPF2 rating) :

| City (county based upon) | HSPF_ClimateAdj When using HSPF2 rating |
| --- | --- |
| 1 (Rockford) | 77% |
| 2 (Chicago) | 77% |
| 3 (Springfield) | 91% |
| 4 (Belleville) | 91% |
| 5 (Marion) | 91% |
| Weighted Average ComEd Ameren Statewide | 77% 89% 80% |

IEERbase	= Integrated Energy Efficiency Ratio of the baseline equipment

= IEER (or EER2) from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). For air-cooled units < 65 kBtu/hr, assume the following conversion from SEER2 to EER2 for calculation of peak savings:

EER2 = (-0.02 * SEER22) + (1.12 * SEER2)

IEERee	= Integrated Energy Efficiency Ratio (or EER2) of the energy efficient equipment. For air-cooled units < 65 kBtu/hr, if the actual EER2ee is unknown, assume the conversion from SEER2 to EER2 as provided above.

= Actual installed

HeatLoad_Disp	= Annual heat load for the building displaced by the ASHP (Btus)

= EFLHheat * Capacityheat * HeatLoadFactor

EFLHheat	= heating mode equivalent full load hours in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use.

Capacityheat	= output capacity of the heat pump equipment in Btu per hour.

= Actual installed

HeatLoadFactor	= Portion of HeatLoad displaced by ASHP in partial displacement applications. Varies by Switchover Temperature and Climate Region. If Switchover Temperature is unknown, use 32°F.

= 1.0 if full displacement (e.g. cold climate heat pumps and water source heat pumps) or if switchover temperature is lower than 17°F or if Partial Displacement with simultaneous operation

| Climate Zone (City based upon) | HeatLoadFactor (by Switchover Temperature) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 47°F | 44°F | 41°F | 38°F | 35°F | 32°F | 29°F | 26°F | 23°F | 20°F | 17°F |
| 1 (Rockford) | 4% | 8% | 12% | 16% | 26% | 36% | 45% | 58% | 66% | 71% | 78% |
| 2 (Chicago) | 4% | 9% | 15% | 21% | 32% | 43% | 52% | 66% | 74% | 77% | 84% |
| 3 (Springfield) | 4% | 9% | 15% | 21% | 37% | 52% | 59% | 69% | 76% | 79% | 85% |
| 4 (Belleville) | 7% | 14% | 22% | 30% | 41% | 55% | 66% | 77% | 85% | 90% | 93% |
| 5 (Marion) | 7% | 16% | 25% | 34% | 53% | 67% | 76% | 86% | 90% | 93% | 97% |
| Weighted Average ComEd Ameren Statewide | 4% 5% 4% | 9% 11% 9% | 15% 17% 16% | 20% 24% 21% | 31% 38% 33% | 43% 52% 45% | 51% 60% 54% | 66% 71% 67% | 73% 79% 75% | 77% 82% 79% | 84% 88% 85% |

PD_Adj	= Adjustment multiplier to account for increased heat pump efficiency in Partial Displacement applications when there is no electric resistance backup and switchover temperature is higher than 17F. Varies by Switchover Temperature and Climate Region. If Switchover Temperature is unknown, use 32F.

= 1.0 if full displacement (e.g. cold climate heat pumps or water source heat pumps) or if switchover temperature is lower than 17F or if Partial Displacement with simultaneous operation

| Climate Zone (City based upon) | PD_Adj (by Switchover Temperature) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 47°F | 44°F | 41°F | 38°F | 35°F | 32°F | 29°F | 26°F | 23°F | 20°F | 17°F |
| 1 (Rockford) | 153% | 149% | 146% | 143% | 138% | 134% | 132% | 128% | 126% | 124% | 122% |
| 2 (Chicago) | 153% | 148% | 145% | 142% | 138% | 134% | 132% | 128% | 126% | 125% | 123% |
| 3 (Springfield) | 153% | 148% | 145% | 142% | 137% | 133% | 132% | 129% | 128% | 127% | 125% |
| 4 (Belleville) | 152% | 149% | 145% | 143% | 139% | 135% | 133% | 131% | 128% | 127% | 126% |
| 5 (Marion) | 153% | 148% | 145% | 142% | 138% | 135% | 134% | 131% | 130% | 129% | 128% |
| Weighted Average ComEd Ameren Statewide | 153% 153% 153% | 148% 148% 148% | 145% 145% 145% | 142% 142% 142% | 138% 138% 138% | 134% 134% 134% | 132% 132% 132% | 128% 130% 129% | 126% 128% 127% | 125% 127% 126% | 123% 125% 124% |

3412		= Btu per kWh.

COPbase	= coefficient of performance of the baseline equipment

= COP from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). If rating is HSPF2, COP = HSPF2 / 3.413

COPee		= coefficient of performance of the energy efficient equipment.

= Actual installed. If rating is HSPF2, COP = HSPF2 / 3.413

AFUEbase 	= Baseline Annual Fuel Utilization Efficiency Rating. For early replacement measures, use actual AFUE rating for the remaining useful life of the existing equipment (6 years for furnace, 8 years for boilers). For new systems (time of sale, new construction or remaining years of early replacement), use appropriate code level efficiency.

FurnaceFlag	= 1 if system replaced is a gas furnace, 0 if not.

Fe		= Furnace Fan energy consumption as a percentage of annual fuel consumption

= 7.7%

%IncentiveElectric	= % of total incentive paid by electric utility

= Actual

%IncentiveGas		= % of total incentive paid by gas utility

= Actual

Code of Federal Redulations (baseline effective 1/1/2019):

| Equipment type | Cooling capacity | Heating type | Cooling Efficiency level | Heating Efficiency level | Compliance date |
| --- | --- | --- | --- | --- | --- |
| Small Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥65,000 Btu/h and <135,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 12.2 IEER = 14.1 | N/A | 1/1/2018 1/1/2024 |
|  |  | All Other Types of Heating | IEER = 12.0 IEER = 13.9 | COP = 3.3 COP = 3.4 | 1/1/2018 1/1/2024 |
| Large Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥135,000 Btu/h and <240,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 11.6 IEER = 13.5 | N/A | 1/1/2018 1/1/2024 |
|  |  | All Other Types of Heating | IEER = 11.4 IEER = 13.3 | COP = 3.2 COP = 3.3 | 1/1/2018 1/1/2024 |
| Very Large Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥240,000 Btu/h and <760,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 10.6 IEER = 12.5 | N/A | 1/1/2018 1/1/2024 |
|  |  | All Other Types of Heating | IEER = 10.4 IEER = 12.3 | COP = 3.2 | 1/1/2018 1/1/2024 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, Single-Phase, Split-System) | <65,000 Btu/h | All | SEER2 = 14.3 EER2 = 9.4 | HSPF2 = 7.5 | 1/1/2023 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, Single-Phase, Single-Package) | <65,000Btu/h | All | SEER2 = 13.4 EER2 = 8.8 | HSPF2 = 6.7 | 1/1/2023 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Split-System) | <65,000 Btu/h | All | SEER2 = 14.3 EER2 = 9.4 | HSPF2 = 7.5 | 1/1/2025 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Single-Package) | <65,000Btu/h | All | SEER2 = 13.4 EER2 = 8.8 | HSPF2 = 6.7 | 1/1/2025 |
| Small Commercial Packaged Air-Conditioning and Heating Equipment (Water Source: Water-to-Air, Water-Loop) | <17,000 Btu/h | All | EER = 12.2 | COP = 4.3 | 10/9/2015 |
|  | ≥17,000 Btu/h and <65,000 Btu/h | All | EER = 13.0 | COP = 4.3 | 10/9/2015 |
|  | ≥65,000 Btu/h and <135,000Btu/h | All | EER = 13.0 | COP = 4.3 | 10/9/2015 |

Minimum Efficiency Requirements: 2015 IECC (baseline effective 1/1/2016 to 6/30/2019)

Minimum Efficiency Requirements: 2018 IECC (baseline effective 7/1/2019 to 9/30/2022)

IECC2018 Table C403.3.2(2) continued from previous page:

Minimum Efficiency Requirements: 2021 IECC (baseline effective 10/1/2022 for New Construction measures)

IECC2021 Table C403.3.2(2) continued from previous page

Non Fuel Switch example, a 5-ton single phase split system 60,000 Btuh capacity heat pump, with an efficiency  SEER2 of 16, and an efficient HSPF2 of 9.5, at a new restaurant in Chicago with a building permit dated after 1/1/2023 saves:

ΔkWh	= Annual kWh Savingscool + Annual kWh Savingsheat

Annual kWh Savingscool 	= (Capacitycool * EFLHcool * (1/SEERbase – 1/SEERee))/1000

Annual kWh Savingsheat 	= (HeatLoad * (1/(HSPFbase * HSPF_ClimateAdj) – 1/(HSPFee* HSPF_ClimateAdj)/1000

ΔkWh 	= (60,000 * 761 * (1/14.3 – 1/16))/1000 + (60,000 * 797 * (1/(7.5 * 0.7) – 1/(9.5 * 0.7))/1000

= 2257 kWh

Fuel Switch Illustrative Examples

[for illustrative purposes 50:50 Incentive is used for joint programs]

New construction using gas furnace and central AC baseline:

For example, a 60,000 Btu, 16 SEER2, 9.5 HSPF2 single phase split system Air Site Heat Pump installed in a new Chicago restaurant, in place of a 120,000 Btuh natural gas furnace and 5 ton Central AC unit:

SiteEnergySavings (MMBTUs)	=  GasHeatReplaced + FurnaceFanSavings - HPSiteHeatConsumed + HPSiteCoolingImpact

GasHeatReplaced		= (HeatLoad * 1/AFUEbase) / 1,000,000

= (60,000 * 797 * 1/0.8) / 1000000

= 59.8 MMBtu

FurnaceFanSavings	= (FurnaceFlag * HeatLoad * 1/AFUEbase * Fe) / 1,000,000

= (1 * 60,000 * 797 * 1/0.8 * 0.077) / 1,000,000

= 4.6 MMBtu

HPSiteHeatConsumed	= ((HeatLoad * (1/(HSPFee * HSPF_ClimateAdj))) /1000 * 3412)/ 1,000,000

= ((60,000 * 797 * (1/(9.5 * 0.77))) / 1000 * 3412) / 1,000,000

= 22.3 MMBtu

HPSiteCoolingImpact 	= ((FLHcool * Capacitycool * (1/SEERbase - 1/SEERee))/1000 * 3412) / 1,000,000

= ((761 * 60,000 * (1/14.3 - 1/16)) / 1000 * 3412)/1,000,000

= 1.2 MMBtu

SiteEnergySavings (MMBTUs)	= 59.8 + 4.6 – 22.3 + 1.2 = 43.3 MMBtu [Measure is eligible]

Fuel Switch Illustrative Example continued

Savings would be claimed as follows:

| Measure supported by: | Electric Utility claims: | Gas Utility claims: |
| --- | --- | --- |
| Electric utility only | 43.3 * 1,000,000/3412 = 12,691 kWh | N/A |
| Electric and gas utility | 0.5 * 43.3 * 1,000,000/3412 = 6,345 kWh | 0.5 * 43.3 * 10 = 217 Therms |
| Gas utility only | N/A | 43.3 * 10 = 433 Therms |

###### Summer Coincident Peak Demand Savings

ΔkW	= ((Capacitycool/DuctlessSave * 1/EER2_base) – (Capacitycool * 1/EER2_ee)) / 1000 * CF

Where CF value is chosen between:

CFSSP	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

For example, a 5 ton single phase split system air source heat pump, with an efficient EER2 of 12.5 with a building permit dated after 1/1/2023 saves:

ΔkW		= ((60,000/1 * 1/9.4) – (60,000 * 1/12.5))/1000 *0.913

= 1.44 kW

###### Fossil Fuel Savings

Calculation provided together with Electric Energy Savings above.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Cost Effectiveness Screening and Load Reduction Forecasting when Fuel Switching

This measure can involve fuel switching from gas to electric.

For the purposes of forecasting load reductions due to fuel switch ASHP projects per Section 16-111.5B, changes in site energy use at the customer’s meter (using ΔkWh algorithm below), customer switching estimates, NTG, and any other adjustment factors deemed appropriate, should be used.

The inputs to cost effectiveness screening should reflect the actual impacts on the electric and fuel consumption at the customer meter and, for fuel switching measures, should therefore reflect the decrease in one fuel and increase in another, as opposed to the single savings value calculated in the “Electric and Fossil Fuel Energy Savings” section above. Therefore in addition to the calculation of savings claimed, the following values should be used to assess the cost effectiveness of the measure. For Early Replacement measures, the efficiency terms of the existing unit should be used for the remaining useful life of the existing equipment (6 years for ASHP and Central AC, 7 years for furnace, 8 years for boilers or GSHP, 15 years for electric resistance), and the efficiency terms for a new baseline unit should be used for the remaining years of the measure.

ΔTherms	= [Heating Consumption Replaced]

= [(%FuelSwitch * HeatLoad_Disp/DuctlessSave * 1/AFUEbase) / 100,000]

ΔkWh 		= [FurnaceFanSavings] - [HP heating consumption] + [Cooling savings]

For units with cooling capacities less than 65 kBtu/hr:

= %FuelSwitch * [FurnaceFlag * HeatLoad_Disp/DuctlessSave * 1/AFUEbase * Fe * 0.000293] - [(HeatLoad_Disp * (1/(HSPF2ee * HSPF2_ClimateAdj * PD_Adj))/1000] + [((CoolingLoad/DuctlessSave * 1/SEER2base) - (CoolingLoad * 1/SEER2ee))/1000]

For units with cooling capacities greater than 65 kBtu/hr:

= %FuelSwitch * [FurnaceFlag * HeatLoad_Disp * 1/AFUEbase * Fe * 0.000293] - [HeatLoad_Disp/3412 * 1/(COPee * PD_Adj)]  + [(CoolingLoad * (1/IEERbase - 1/IEERee))/1000]

###### Measure Code: CI-HVC-HPSY-V13-250101

###### Review Deadline: 1/1/2028

### 4.4.15	Single-Package and Split System Unitary Air Conditioners

###### Description

This measure promotes the installation of high-efficiency unitary air-, water-, and evaporatively-cooled air conditioning equipment, both single-package and split systems. Air conditioning (AC) systems are a major consumer of electricity and systems that exceed baseline efficiency requirements can significantly reduce energy consumption. This measure could apply to the replacing of an existing unit at the end of its useful life or the installation of a new unit in a new or existing building.

This measure was developed to be applicable to the following program types: TOS, NC, EREP. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is assumed to be a high-efficiency air-, water-, or evaporatively-cooled air conditioner that exceeds the energy efficiency requirements as prescribed by the program.

###### Definition of Baseline Equipment

In order for this characterization to apply, the baseline equipment is assumed to be a standard-efficiency air-, water, or evaporatively-cooled air conditioner that meets the Code energy efficiency requirements (IECC or Code of Federal Regulations whichever is higher) in effect on the date of equipment purchase (if date is unknown, assume current Code minimum).

For Early Replacement programs, use the actual efficiency of the existing unit or assume IECC code base in place at the original time of existing unit installation. To qualify under the early replacement characterization, baseline equipment must meet these additional qualifications:

- The existing unit is operational when replaced or the existing unit would be operational with minor repairs.

In order for this characterization to apply, the baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit. As code requirements and adoption can differ from municipality to municipality, the user should verify which version of code is applicable given these constraints.

Note, IECC 2021 became effective statewide on 1/1/2024. IECC 2018 is the requisite code for any projects with permitting dates spanning July 1, 2019 to 12/31/2023. Prior to July 1, 2019, IECC 2015 is the applicable code. If evaluation determines the applicable version of code, given location and timing, isn’t an appropriate baseline due to supply constraints, low compliance, or other issues, the previous iteration of code may be used through 2023.

IECC 2021 leverages new DOE testing methods and associated metrics. The following conversion factors are recommended for use if the efficient equipment is not rated under the new testing procedure but the stipulated baseline is:

SEER2 = X * SEER

EER2 = X * EER

HSPF2 = X * HSPF

Where:

| X | SEER2 | EER2 | HSPF2 |
| --- | --- | --- | --- |
| Ducted | 0.95 | 0.95 | 0.85 |
| Ductless | 1.00 | 1.00 | 0.90 |
| Packaged | 0.95 | 0.95 | 0.84 |

Note: new Federal Standards affecting heat pumps and air conditioning equipment became effective January 1, 2025.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 15 years.

For early replacement, the remaining life of existing equipment is assumed to be 5 years.

###### Deemed Measure Cost

The incremental capital cost for this measure is based upon capacity and efficiency level (defined be CEE specifications), as outlined in the following table:

|  | Incremental cost ($/ton) |  |
| --- | --- | --- |
| Capacity | Up to and including CEE Tier 1 units | CEE Tier 2 and above |
| < 135,000 Btu/hr | $63 | $127 |
| 135,000 Btu/hr to > 250,000 Btu/hr | $63 | $127 |
| 250,000 Btu/hr and greater | $19 | $38 |

For early replacement, the full cost of the installed unit should be used. If unknown use defaults below. The assumed deferred cost (after 5 years) of replacing existing equipment with a new baseline unit is also provided. This future cost should be discounted to present value using the real discount rate:

|  | Full Install Cost ($/ton) |  |  |
| --- | --- | --- | --- |
| Capacity | Base Units | Up to and including CEE Tier 1 units | CEE Tier 2 and above |
| < 135,000 Btu/hr | $895 | $958 | $1,021 |
| 135,000 Btu/hr to > 250,000 Btu/hr | $762 | $825 | $889 |
| 250,000 Btu/hr and greater | $673 | $691 | $710 |

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period and is presented so that savings can be bid into PJM’s capacity market.  Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

CFSSP	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Time of Sale:

For units with cooling capacities less than 65 kBtu/hr:

ΔkWH= (kBtu/hr) * [1SEER2base - 1SEER2ee(1/SEERee] * EFLH

For units with cooling capacities equal to or greater than 65 kBtu/hr:

ΔkWH= (kBtu/hr) * [1IEERbase - 1IEERee] * EFLH

Early replacement:

For units with cooling capacities less than 65 kBtu/hr:

For remaining life of existing unit (1st 5 years):

ΔkWH= (kBtu/hr) * [1SEER2exist - 1SEER2ee] * EFLH

For remaining measure life (next 10 years):

ΔkWH= (kBtu/hr) * [1SEER2base - 1SEER2ee] * EFLH

For units with cooling capacities equal to or greater than 65 kBtu/hr:

For remaining life of existing unit (1st 5 years):

ΔkWH= (kBtu/hr) * [1IEERexist - 1IEERee] * EFLH

NOTE: If the existing equipment age is such that IEER ratings are not available, EER may be substitued when necessary. In such instances both existing and efficient unit efficiencies should be specified in EER.

For remaining measure life (next 10 years):

ΔkWH= (kBtu/hr) * [1 IEERbase- 1IEERee] * EFLH

Where:

kBtu/hr 	= capacity of the cooling equipment actually installed in kBtu per hour (1 ton of cooling capacity equals 12 kBtu/hr)

SEER2base	= Seasonal Energy Efficiency Ratio of the baseline equipment

= SEER2 values from tables below, based on applicable Code on date of equipment purchase (if unknown assume current Code).

SEER2ee 		= Seasonal Energy Efficiency Ratio of the energy efficient equipment (actually installed)

SEE2Rexist	= Seasonal Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation

IEERbase	= Integrated Energy Efficiency Ratio of the baseline equipment. See table below based on applicable Code on date of equipment purchase (if unknown assume current Code).

IEERee		= Integrated Energy Efficiency Ratio of the energy efficient equipment (actually installed)

IEERexist		= Integrated Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation

EFLH 	= Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use

The rating conditions for the baseline and efficient equipment efficiencies must be equivalent.

Code of Federal Redulations (baseline effective 1/1/2025):

| Equipment type | Cooling capacity | Heating type | Efficiency level | Compliance date |
| --- | --- | --- | --- | --- |
| Small Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥65,000 Btu/h and <135,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 12.9 IEER = 14.8 | 1/1/2018 1/1/2023 |
|  |  | All Other Types of Heating | IEER = 12.7 IEER = 14.6 | 1/1/2018 1/1/2023 |
| Large Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥135,000 Btu/h and <240,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 12.4 IEER = 14.2 | 1/1/2018 1/1/2023 |
|  |  | All Other Types of Heating | IEER = 12.2 IEER = 14.0 | 1/1/2018 1/1/2023 |
| Very Large Commercial Packaged Air Conditioning and Heating Equipment (Air-Cooled) | ≥240,000 Btu/h and <760,000 Btu/h | Electric Resistance Heating or No Heating | IEER = 11.6 IEER = 13.2 | 1/1/2018 1/1/2023 |
|  |  | All Other Types of Heating | IEER = 11.4 IEER = 13.0 | 1/1/2018 1/1/2023 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Split-System) | <65,000 Btu/h | All | SEER2 = 13.4 | 1/1/2025 |
| Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Single-Package) | <65,000Btu/h | All | SEER2 = 13.4 | 1/1/2025 |

2015 IECC Minimum Efficiency Requirements (baseline effective 1/1/2016 to6/30/2019)

2018 IECC Minimum Efficiency Requirements (baseline effective 7/1/2019 to 9/30/2022)

2021 IECC Minimum Efficiency Requirements (baseline effective 10/1/2022)

For example, a 5 ton air cooled split system with a SEER2 of 15 at an existing retail strip mall in Rockford would save:

ΔkWH	= (60) * [(1/13.4) – (1/15)] * 697

= 290 kWh

###### Summer Coincident Peak Demand Savings

Time of Sale:

ΔkW = (kBtu/hr * (1EER2base - 1 EER2ee)* CFΔkW = (kBtu/hr) * (1EER2base - 1 EER2ee)* CF

Early Replacement:

For remaining life of existing unit (1st 5 years):

ΔkW= (kBtu/hr) * [1EER2exist - 1EER2ee] * CF

For remaining measure life (next 10 years):

ΔkW= (kBtu/hr) * [1EER2base - 1EER2ee] * CF

Where:

EER2base 	= Energy Efficiency Ratio of the baseline equipment

= EER values from tables above, based on applicable Code on date of equipment purchase (if unknown assume current Code). (For air-cooled units < 65 kBtu/hr, assume the following conversion from SEER to EER for calculation of peak savings: EER = (-0.02 * SEER2) + (1.12 * SEER))

EER2ee 	= Energy Efficiency Ratio of the energy efficient equipment.  If the actual EERee is unknown, assume the conversion from SEER to EER for calculation of peak savings as above).

= Actual installed

EER2exist		= Energy Efficiency Ratio of the existing equipment

= Actual, or assume Code base in place at the original time of existing unit installation

CFSSP	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

For example, a 5 ton air cooled split system with a SEER of 15 in Rockford would save:

ΔkWSSP 	= (60) * [(1/11.4) – (1/12.3)] * 0.913

= 0.352 kW

###### Fossil Fuel Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Measure Code: CI-HVC-SPUA-V11-250101

###### Review Deadline: 1/1/2026

### 4.4.58	Steam Trap Monitoring System

###### Description

The measure applies to the installation of a steam trap monitoring system. The measure is applicable to commercial applications, commercial HVAC including multifamily buildings, and industrial applications. An existing measure, 4.4.16 Steam Trap Replacement or Repair, covers the replacement of a faulty steam trap in the failed open or leaking state. In addition to the steam trap replacement savings, the proposed measure allows to account for savings due to faster repair of the steam traps. Once a failed steam trap is detected, it can be immediately repaired/replaced. Continuous steam trap monitoring leaves behind manual inspections (audits) by using sensors to transmit real-time conditions of the steam system.

Energy savings for each steam trap occurs only when failed open, and steam trap failure rates vary based on trap size, type, and pressure. Energy savings are calculated on a per trap basis with the assumed annual failure rate for each application. Separate savings methodologies are recommended for space heating and process heating applications.

This measure was developed to be applicable to the following program types: TOS, RF. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

Customers must install a steam trap monitoring system on properly functioning steam traps serving either space heating or process heating load. The monitoring system must be capable of tracking the following, but not limited to, number of steam traps, trap type, operating pressure, operating temperature, ambient temperature, trap condition, date/time, application, and trap location. Applicants must provide characteristics for the steam system such as heating efficiency, steam trap orifice size(s), and system pressure(s). Customer must commit to repairing/replacing steam traps identified as failed by the steam trap monitoring system.

###### Definition of Baseline Equipment

The baseline criterion are functioning steam traps serving either space heating or process heating load with no pre-existing monitoring system. No minimum leak rate is required.

###### Deemed Lifetime of Efficient Equipment

10 years based on vendor estimates.

###### Deemed Measure Cost

The costs are subject to the subscription period chosen by the customer as shown in table below. The approximate installed cost is per trap per year and includes sensors, gateway, cellular service, cloud hosting, User license, data, and reports.

| Number of Traps | Term |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1 Year | 2 Years | 3 Years | 4 Years | 5 Years |
| 100 – 250 | $300 | $282 | $265 | $249 | $234 |
| 250 – 499 | $291 | $274 | $257 | $242 | $227 |
| 500 – 999 | $282 | $265 | $249 | $234 | $220 |
| 1000 – 1999 | $274 | $257 | $242 | $227 | $214 |
| 2000 – 2999 | $266 | $250 | $235 | $221 | $207 |
| 3000 – 4999 | $262 | $246 | $232 | $218 | $204 |
| 5000 – 5999 | $258 | $242 | $228 | $214 | $201 |
| 6000 – 6999 | $254 | $238 | $224 | $210 | $198 |
| 7000+ | $251 | $235 | $221 | $207 | $196 |

Additional costs exist for the repair or replacement of steam traps once identifying a fault.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Secondary kWh Savings for Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure but should not be included in TRC tests to avoid double counting the economic benefit of water savings. These savings only apply to situations in which steam is lost from the steam system.

∆kWhwater=∆Water gallons1,000,000 ×Ewater supply

Where

Ewater supply 	= Water Supply Energy Factor (kWh/Million Gallons)

= 2571

###### Summer Coincident Peak Demand Savings

N/A

###### Fossil Fuel Savings

∆Therm=N ×Pmalfunctioning×Fo×Sa×Hv+Hs×T1-Tsource×Hours100,000×ηB

Where:

N 		= Total number of steam traps monitored through the steam trap monitoring system

Pmalfunctioning	= Annual Percentage of malfunctioning traps

Pmalfunctioning     =L×Taudit×Tu

Where:

L 	= Leaking & Blow-thru

= custom, if unknown:

| Steam System | L (%) |
| --- | --- |
| Commercial Dry Cleaners | 27% |
| Commercial Heating (including Multifamily) LPS | 27% |
| Industrial and Process Low Pressure ≤ 15 psig | 16% |
| Medium Pressure > 15 psig < 30 psig | 16% |
| Medium Pressure ≥ 30 < 75 psig | 16% |
| High Pressure ≥ 75 < 125 psig | 16% |
| High Pressure ≥ 125 < 175 psig | 16% |
| High Pressure ≥ 175 < 250 psig | 16% |
| High Pressure ≥ 300 psig | 16% |

Taudit 		= Average time between audits

Custom, if unknown use 1 year

Tu 	= Average percentage of year trap malfunctions are undetected for steam systems without a steam trap monitoring system

Custom, if unknown use 50%

Fo 		= Failed open to total failed ratio

= Custom, if unknown:

96%, Space heating applications

98%, Dry cleaners3

94%, All other steam systems and applications3

Sa		= Steam loss per leaking trap, lbshr

Hv		= Heat of vaporization of steam, Btulbm

| Steam System | Average Inlet Pressure psig | Heat of Vaporization Btulbm |
| --- | --- | --- |
| Commercial Dry Cleaners | -- | 890 |
| Commercial Space Heating (including Multifamily) LPS | 11.2 | 951 |
| Industrial/Process Low Pressure: psig < 15 | 11.29 | 951 |
| Medium Pressure: 15 ≤ psig < 30 | 16 | 944 |
| Medium Pressure: 30 ≤ psig < 75 | 47 | 915 |
| High Pressure: 75 ≤ psig < 125 | 101 | 880 |
| High Pressure: 125 ≤ psig < 175 | 146 | 859 |
| High Pressure: 175 ≤ psig < 250 | 202 | 837 |
| High Pressure: 250 ≤ psig < 300 | 263 | 816 |
| High Pressure: 300 ≤ psig | -- | Custom |

Hs 		= Specific heat of water, Btulbm*°R

= 1.001

T1 		= Temperature of Saturated Steam, °R

= 507.89×P10.0962

Where:

= 507.89=Constant, °R×in2lbf0.0962

Tsource		= 513.67 °R

Hours 		= Annual hours when steam system is pressurized

= custom, if unknown:

| Steam System | Zone (Where applicable) | Hours/Yr |
| --- | --- | --- |
| Commercial Dry Cleaners | All Climate Zones | 2,425 |
| Industrial/Process Low Pressure: psig < 15 |  | 8,282 |
| Medium Pressure: 15 ≤ psig < 30 |  | 8,282 |
| Medium Pressure: 30 ≤ psig < 75 |  | 8,282 |
| High Pressure: 75 ≤ psig < 125 |  | 8,282 |
| High Pressure: 125 ≤ psig < 175 |  | 8,282 |
| High Pressure: 175 ≤ psig < 250 |  | 8,282 |
| High Pressure: 250 ≤ psig < 300 |  | 8,282 |
| High Pressure: 300 ≤ psig |  | 8,282 |
| Commercial Space Heating LPS | Rockford | 4,272 |
|  | Chicago | 4,029 |
|  | Springfield | 3,406 |
|  | Belleville | 2,515 |
|  | Marion | 2,546 |
| Multifamily Space Heating LPS | For steam traps that are part of steam systems where the boiler cycles on/off to maintain space setpoint temperature or for steam traps located downstream of a steam control valve that opens/closes to maintain setpoint temperature, use Heating EFLH values in Section 4.4 for High Rise or Mid-Rise MF buildings. For steam traps that are exposed to steam continuously throughout the heating season, use the values listed above for Commercial Space Heating LPS for your appropriate climate zone. |  |

100,000 		= Conversion factor BtuTherms

ηB		= Boiler efficiency

= custom, if unknown:

80.7% for steam boilers, except multifamily low-pressure

64.8% for multifamily low-pressure steam boilers

Space Heating Savings Estimates

For systems used in space heating applications that operate at 5 psig or lower, use the following equation to calculate Sa. The condensate return system pressure, P2, will typically be atmospheric pressure, 14.696 psia.

Sa=1,519.3×P1×D2×1T1×γγ-1×P2P12γ-P2P1γ+1γ0.5×A×FF

Where:

1,519.3 		= Constant, s2×°R0.5ft×hr

P1 	= Average steam trap inlet pressure absolute, psia. If not available, use defaults provided in table below (note that defaults are provided in psig, not psia)

D 	= Diameter of orifice, inches. Actual value should be used wherever possible as this value has a significant impact on steam flowrate value.

γ 		= Heat Capacity Ratio unitless

= 5.071×10-4×P1+1.332

P2 	= Average steam trap outlet pressure absolute, psia. If unknown, assume atmospheric pressure, 14.696 psia

A 		= Adjustment factor

= 50%, all steam systems. This factor accounts for reduction in the maximum theoretical steam flow to the average steam flow (the Enbridge factor).

FF 	= Flow factor. In addition to the Adjustment factor (A), and additional 50% flow factor adjustment is recommended for medium and high-pressure steam systems to address industrial float and thermostatic style traps where additional blockage is possible.

Defaults are provided in table below if custom calculation is not performed. The savings are averages for common orifice diameters 18, 316,14,516inches at an assumed 5 psig.

| Savings per Steam Trap Orifice Size |  | 1/8 | 3/16 | 1/4 | 5/16 |
| --- | --- | --- | --- | --- | --- |
| Sa | (lbs/hr) | 3.84 | 8.64 | 15.35 | 23.99 |
| ΔTherms | (Therms/trap/yr) | 14.23 | 32.02 | 56.92 | 88.94 |

Process Heating Savings Estimates

Use the following equation, for all other steam systems and applications

Sa=24.24×P1×D2×A×FF

Where:

24.24 	= Constant, lbmhr×psia×in2

Defaults are provided in table below if custom calculation is not performed.

| Steam System | Average Steam Trap Inlet Pressure (psig) | Diameter of Orifice (in) | Adjustment Factor | Flow Factor | Sa (lbs/trap/hr) | ΔTherm |
| --- | --- | --- | --- | --- | --- | --- |
| Commercial Dry Cleaners | 82.8 | 0.1250 | 50% | 100% | 18.5 | 86 |
| Commercial LPS Space Heating | 11.2 | 0.2100 | 50% | 100% | 13.8 | 101 |
| Industrial/Process Low Pressure: psig < 15 | 11.2 | 0.210019 | 50% | 100% | 13.8 | 121 |
| Medium Pressure: 15 ≤ psig < 30 | 16 | 0.1875 | 50% | 50% | 6.5 | 57 |
| Medium Pressure: 30 ≤ psig < 75 | 47 | 0.2500 | 50% | 50% | 23.4 | 209 |
| High Pressure: 75 ≤ psig < 125 | 101 | 0.2500 | 50% | 50% | 43.8 | 395 |
| High Pressure: 125 ≤ psig < 175 | 146 | 0.2500 | 50% | 50% | 60.7 | 551 |
| High Pressure: 175 ≤ psig < 250 | 202 | 0.2500 | 50% | 50% | 82.1 | 745 |
| High Pressure: 250 ≤ psig < 300 | 263 | 0.2500 | 50% | 50% | 105.2 | 954 |

###### Water and Other Non-Energy Impact Descriptions and Calculation

The hourly water volume saved per each repaired or replaced leaking trap is calculated by dividing the “Steam Loss per Leaking Trap (lbm/hr/trap)” by the density of water saved, 8.33 lbm/gal, that replaces the lost steam. The steam loss is provided in the table for parameter Sa, the “Steam loss per leaking trap” in the Fossil Fuel savings section above. Annual water savings are calculated using Hours and Pmalfunctioning, the annual percentage of malfunctioning traps, as defined above.

Water savings only apply to situations where condensate is lost from the steam system. If a condensate recovery system is in place, assume zero water savings or provide a custom calculation based on site-specific operation.

The annual water savings for a replaced or repaired trap is given by:

∆Water=GAL×Hours×N ×Pmalfunctioning×Fo

Where:

GAL = average actual water volume saved per leaking trap, as listed in the following table and based on steam system type.

Other variables as defined above

| Steam System | Sa | GAL (gal/hr/trap) |
| --- | --- | --- |
| Commercial Dry Cleaners | 18.5 | 2.22 |
| Multifamily LPS Space Heating | 6.9 | 0.83 |
| Industrial/Process Low Pressure: psig < 15 | 13.8 | 1.66 |
| Medium Pressure: 15 ≤ psig < 30 | 6.5 | 0.79 |
| Medium Pressure: 30 ≤ psig < 75 | 23.4 | 2.81 |
| High Pressure: 75 ≤ psig < 125 | 43.8 | 5.26 |
| High Pressure: 125 ≤ psig < 175 | 60.9 | 7.31 |
| High Pressure: 175 ≤ psig < 250 | 82.1 | 9.85 |
| High Pressure: 250 ≤ psig < 300 | 105.2 | 12.63 |
| High Pressure: 300 ≤ psig | Calculated | Calculated Steam Loss / 8.33 |

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-STMS-V2-250101

###### Review Deadline: 1/1/2025

### 4.4.60	Variable Refrigerant Flow HVAC System

###### Description

This measure applies to the installation of air source Variable Refrigerant Flow (VRF) HVAC systems. VRF systems are heat pumps that have one outdoor condensing unit with refrigerant piped to multiple indoor evaporator units to deliver cooling and/or heating to individual interior zones as needed. This measure could apply to replacing an existing unit at the end of its useful life or the installation of a new unit in a new or existing building.

This measure was developed to be applicable to the following program times: TOS and NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

This measure applies to both retrofit and new construction installations of VRF systems. Savings are based in the inherent efficiency of VRF systems as compared to traditional HVAC systems. VRF systems should meet or exceed ASHRAE 90.1 minimum efficiency requirements for air source VRF systems.

###### Definition of Baseline Equipment

Time of Sale / New Construction

Non-fuel switch measures:

To calculate savings with an electric baseline, the baseline equipment is assumed to be a ducted split-system heat pump for non-residential buildings 25,000 square feet or fewer and is 3 floors or fewer. For non-residential buildings over 25,000 square feet or 4 floors or higher, the baseline equipment is assumed to be a standard-efficiency air cooled heat pump roof top unit (RTU) system. For residential buildings types which utilize individual in-unit HVAC systems, such as multifamily, lodging, dormitories, etc., the baseline equipment is assumed to be a residential style standard-efficiency packaged terminal heat pump split system.

Fuel switch measures:

To calculate savings with a gas or fuel heating baseline, the baseline equipment is assumed to be single zone furnace and air-conditioning units for non-residential buildings 25,000 square feet or fewer and is 3 floors or fewer. For non-residential buildings over 25,000 square feet or taller than 3 floors, the baseline equipment is assumed to be a packaged variable-air-volume (VAV) system with DX cooling and hot water reheat. For residential buildings types which utilize individual in-unit HVAC systems, such as multifamily, lodging, dormitories, etc., the baseline equipment is assumed to be a packaged terminal air conditioner (PTAC) with hot-water radiator heating. If the residential building is 4 stories or more, the baseline system will be a water source heat pump (WSHP) system with a boiler and cooling tower.

Standard efficiency implies equipment that complies with Code energy efficiency requirements (IECC or Code of Federal Regulations, whichever is higher) in effect on the date of equipment purchase (if date unknown, assume current Code minimum). The rating conditions for the baseline and efficient equipment efficiencies must be equivalent. Note: IECC 2018 is baseline for all New Construction permits from July 1, 2019, and if permit date unknown. Note: new Federal Standards affecting heat pumps become effective January 1, 2023.

Baseline selection:

The following table can be used to determine the appropriate baseline HVAC system type.

|  | Non-Fuel Switch | Fuel Switch |
| --- | --- | --- |
| Multifamily or Lodging, 3 floors or fewer | Packaged Terminal Heat Pump | PTAC w/ Hot Water Radiator |
| Multifamily or Lodging, 4 floors or more | Packaged Terminal Heat Pump | Water Source Heat Pump with Cooling Tower and Natural Gas Boiler |
| Non-residential <25,000 SF and 3 floors or fewer | Ducted-Split System Heat Pump | Packaged Single Zone (Furnace) + Air Conditioner |
| Non-Residential >25,000 SF OR more than 3 floors | Heat Pump RTU | Packaged VAV RTU with Hot Water Reheat |

###### Deemed Lifetime of Efficient Equipment

The expected measure life for VRF is 16 years.

###### Deemed Measure Cost

Time of Sale: For analysis, the incremental capital costs are summarized in the following table. Site specific cost data should be used where available.

| Baseline System | Incremental Cost ($/ton) |
| --- | --- |
| Packaged Terminal Heat Pump | $610 |
| Ducted Split System Heat Pump | $860 |
| Heat Pump RTU | $130 |
| PTAC w/ Hot Water Radiator | $160 |
| Water Source Heat Pump | $0 |
| Packaged Single Zone (Furnace) + Air Conditioner | $835 |
| Packaged VAV RTU with Hot Water Reheat | $540 |

###### Loadshape

Loadshape C05 – Commercial Electric Heating and Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits. The second represents the average savings over the defined summer peak period and is presented so that savings can be bid into PJM’s capacity market. Both values provided are based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren.

| CFSSP | = Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour) = 91.3% |
| --- | --- |
| CFPJM | = PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period) = 47.8% |

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Savings are calculated as a sum of system switching savings and efficiency savings, analogous to the following equation:

Annual Savings = [System Switch Savings] + [Savings from improved VRF efficiency]

For fuel-switching calculations, the above equation is used for calculating the cooling savings, while the heating savings are calculated by as the following:

Annual Savings = [Gas Heat Replaced x System Switch Adjustment Factor] + [Fan Savings] – [Heat Pump heat consumed x System Switch Adjustment Factor] + [Heat Pump Cooling  * System Switch Savings + Heat Pump Cooling Savings from improved VRF efficiency]

The system switching savings are calculated by multiplying the cooling or heating load (EFLH times heat or cool capacity) and multiplying it by system heating (Heatadj) and cooling (Cooladj) factors. These adjustment factors were calculated with energy model data of different building types. The VRF performance curves were calibrated based on independent field monitored data.

- The difference in building code baseline efficiency between VRF and the baseline system.

- The improved part load performance of the VRF inverter driven compressor compared to single-stage or two-stage compressors.

- Heat recovery mode savings from the VRF units.

- Decrease in energy from cooling towers (WSHP baseline) and water pumps (baseline systems with hot water and WSHP).

- WSHP electric heating and boiler fuel consumption (WSHP baseline).

- Differences in treating ventilation between mixed recirculating systems and VRF systems with dedicated outdoor air systems (Heat Pump RTU and VAV baseline systems only).

Savings from improved VRF efficiency is similar to other efficiency savings from other TRM measures, where savings are calculated as the load multiplied by the change in efficiency.

Non-fuel switch measures:

| For units with cooling capacities less than 65 kBtu/hr: |  |
| --- | --- |
| ΔkWh Annual kWh Savingscool Annual kWh Savingsheat FanSavings | = Annual kWh Savingscool + Annual kWh Savingsheat + FanSavings = [System Switch Savings] + [Savings from improved VRF efficiency] = (Cooladj * Capacitycool * EFLHcool /3,412)+ (Capacitycool * EFLHcool * (1/SEERbase – 1/SEERee))/1000 = [System Switch Savings] + [Savings from improved VRF efficiency] = (Heatadj * HeatLoad/3,412) + (HeatLoad * (1/HSPFbase – 1/HSPFee))/1000 = (Flag * HeatLoad * 1/AFUEbase * Fe) / 3,412 |
| For units with cooling capacities equal to or greater than 65 kBtu/hr: |  |
| ΔkWh Annual kWh Savingscool Annual kWh Savingsheat FanSavings | = Annual kWh Savingscool + Annual kWh Savingsheat + FanSavings = [System Switch Savings] + [Savings from improved VRF efficiency] = (Cooladj * Capacitycool * EFLHcool/3,412) + (Capacitycool * EFLHcool * (1/IEERbase – 1/IEERee))/1000 = [System Switch Savings] + [Savings from improved VRF efficiency] = (Heatadj * HeatLoad)/3,412 + (HeatLoad * (1/COPbase – 1/COPee)) /3,412 = (Flag * HeatLoad * 1/AFUEbase * Fe) / 3,412 |

Fuel switch measures:

Fuel switch measures must produce positive total lifecycle site energy savings in order to qualify. This is determined as follows (note for early replacement measures the lifetime savings should be calculated by calculating savings for the remaining useful life of the existing equipment and for the remaining measure life):

| SiteEnergySavings (MMBTU) | = GasHeatReplaced + FanSavings – HPSiteHeatConsumed + HPSiteCoolingImpact |
| --- | --- |
| GasHeatReplaced (MMBTU) | = (GasHeatadj * HeatLoad * 1/AFUEbase) / 1,000,000 |
| FanSavings (MMBTU) | = (Flag * HeatLoad * 1/AFUEbase * Fe) / 1,000,000 |
| For units with cooling capacities less than 65 kBtu/hr: |  |
| HPSiteHeatConsumed (MMBTU) | = (Heatadj * HeatLoad * (1/HSPFee)) * 3,412 / 1,000 / 1,000,000 |
| HPSiteCoolingImpact (MMBTU) | = [System Switch Savings] + [Savings from improved VRF efficiency] = ((Cooladj * Capacitycool * EFLHcool) / 1,000,000) + ((EFLHcool * Capacitycool * (1/SEERbase - 1/SEERee)) * 3,412 / 1,000 / 1,000,000) |
| For units with cooling capacities greater than 65 kBtu/hr: |  |
| HPSiteHeatConsumed (MMBTU) | = (Heatadj * HeatLoad * (1/COPee)) / 1,000,000 |
| HPSiteCoolingImpact (MMBTU) | = [System Switch Savings] + [Savings from improved VRF efficiency] = ((Cooladj * Capacitycool * EFLHcool) / 1,000,000) + ((EFLHcool * Capacitycool * (1/IEER_base - 1/IEER_ee)) * 3,412 /1,000 / 1,000,000) |

Savings are adjusted by heating (Heatadj) and cooling (Cooladj) factors presented in the following table. These values bring the expected savings in line with energy model estimated savings.

| Baseline System | GasHeatadj | Cooladj | Heatadj |
| --- | --- | --- | --- |
| Packaged Terminal Heat Pump | N/A | 0.1 | 0.0 |
| Ducted Split System Heat Pump | N/A | 0.0 | 0.0 |
| Heat Pump RTU | N/A | -0.2 | 0.5 |
| PTAC w/ Hot Water Radiator | 0.7 | 0.0 | 1.3 |
| Water Source Heat Pump | 0.4 | 0.1 | 0.5 |
| Packaged Single Zone (Furnace) + Air Conditioner | 1.4 | 0 | 1.6 |
| Packaged VAV RTU with Hot Water Reheat | 0.9 | -0.2 | 1.8 |

If SiteEnergySavings calculated above is positive, the measure is eligible. The appropriate savings claim is dependent on which utilities are supporting the measure as provided in a table below:

| Measure supported by: | Electric Utility claims (kWh): | Gas Utility claims (therms): |
| --- | --- | --- |
| Electric utility only | SiteEnergySavings * 1,000,000/3,412 | N/A |
| Electric and gas utility (Note: utilities may make alternative agreements to how savings are allocated as long as total MMBtu savings remains the same). | %IncentiveElectric * SiteEnergySavings * 1,000,000/3,412 | %IncentiveGas * SiteEnergySavings * 10 |
| Gas utility only | N/A | SiteEnergySavings * 10 |

Where:

| Cooladj |  | = This cooling adjustment factor is derived from energy modeling results to calibrate TRM calculation savings to energy modeling savings estimates. Adjustment factor values are presented in a table above. |  |
| --- | --- | --- | --- |
| Heatadj |  | = This heating adjustment factor is derived from energy modeling results to calibrate TRM calculation savings to energy modeling savings estimates. Adjustment factor values are presented in a table above. |  |
| GasHeatadj |  | = This gas heating adjustment factor is derived from energy modeling results to calibrate TRM calculation savings to energy modeling savings estimates. Adjustment factor values are presented in a table above. |  |  |
| Capacitycool |  | = input capacity of the cooling equipment in Btu per hour (1 ton of cooling capacity equals 12,000 Btu/hr). = Actual installed |  |
| SEERbase |  | =Seasonal Energy Efficiency Ratio of the baseline equipment = SEER from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). |  |
| SEERee |  | = Seasonal Energy Efficiency Ratio of the energy efficient equipment. = Actual installed |  |
| EFLHcool |  | = Equivalent Full Load Hours for cooling in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use. |  |
| HSPFbase |  | = Heating Seasonal Performance Factor of the baseline equipment = HSPF from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). |  |
| HSPFee |  | = Heating Seasonal Performance Factor of the energy efficient equipment. = Actual installed. If rating is COP, HSPF = COP * 3.413 |  |
| IEERbase |  | = Integrated Energy Efficiency Ratio of the baseline equipment = IEER from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). |  |
| IEERee |  | = Integrated Energy Efficiency Ratio of the energy efficient equipment. = Actual installed |  |
| HeatLoad |  | = Calculated heat load for the building = EFLHheat * Capacityheat |  |
|  |  | Where: |  |
|  |  | EFLHheat = heating mode equivalent full load hours in Existing Buildings or New Construction are provided in section 4.4 HVAC End Use. Capacityheat = Actual installed input capacity of the heat pump equipment in Btu per hour. |  |
| 3412 |  | = Btu per kWh. |  |
| COPbase |  | = coefficient of performance of the baseline equipment = COP from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). If rating is HSPF, COP = HSPF / 3.413 |  |
| COPee |  | = coefficient of performance of the energy efficient equipment. = Actual installed. If rating is HSPF, COP = HSPF / 3.413 |  |
| AFUEbase |  | = Baseline Annual Fuel Utilization Efficiency Rating. Use appropriate code level efficiency. |  |
| Flag |  | = 1 if system replaced is an RTU or ducted system with furnace fan, 0 if not. |  |
| Fe |  | = Fan energy consumption as a percentage of annual fuel consumption = 7.7% for RTU replacement, 3% for multifamily (residential style) furnace replacement |  |
| %IncentiveElectric |  | = % of total incentive paid by electric utility = Actual |  |
| %IncentiveGas |  | = % of total incentive paid by gas utility = Actual |  |

Non Fuel Switch example, a heat recovery VRF system with 8 ton cooling capacity and 96 kbtu heating capacity, an efficient IEER of 18.5 and COP of 3.75, at a new construction low-rise office in Chicago in 2024 saves:

| ΔkWh | = Annual kWh Savingscool + Annual kWh Savingsheat + FanSavings |
| --- | --- |
| Annual kWh Savingscool Annual kWh Savingsheat FanSavings | = (Cooladj * Capacitycool * EFLHcool / 3412) + (Capacitycool * EFLHcool * (1/IEERbase – 1/IEERee))/1000 = (Heatadj * Heat Load / 3412) + (HeatLoad * (1/COPbase – 1/(COPee))/3412 = (Flag * HeatLoad * 1/AFUEbase * Fe) / 3412 |
| ΔkWh | = (0.0 * 96000 * 989/3,412) + (96000 * 989 * (1/14.4 – 1/18.5)/1000 + (0.0 * 916 * 60000/3412) + (916 * 60000 * (1/3.3 – 1/3.75) / 3412) + (1 * 916 * 60000 * 1/0.8 * 0.077) / 3412 |
| ΔkWh | = 3597 kWh |

Fuel Switch example, a heat recovery VRF system with 8-ton cooling capacity and 96 kbtu heating capacity, an efficient IEER of 18.5 and COP of 3.75, at a new construction low-rise office in Chicago, assuming a packaged single zone (furnace) and air conditioner baseline. Assuming 50%-50% Incentive agreement is used for joint programs, savings:

| SiteEnergySavings (MMBTUs) | = GasHeatReplaced + FanSavings – HPSiteHeatConsumed + HPSiteCoolingImpact |
| --- | --- |
| GasHeatReplaced | = (GasHeatadj * HeatLoad * 1/AFUEbase) / 1,000,000 |
|  | = 1.4 * (96000 * 916 * 1/0.8) / 1000000 |
|  | = 153.9 MMBtu |
| FanSavings | = (Flag * HeatLoad * 1/AFUEbase * Fe) / 1,000,000 |
|  | = (1 * 96000 * 916 * 1/0.8 * 0.030) / 1000000 |
|  | = 3.30 MMBtu |
| For units with cooling capacities greater than 65 kBtu/hr: |  |
| HPSiteHeatConsumed | = (Heatadj * HeatLoad * (1/COPee)) / 1,000,000 |
|  | = (1.6 * 96000 * 916 * (1/3.75)) / 1,000,000 |
|  | = 37.9 MMBtu |
| HPSiteCoolingImpact | = (Cooladj * Capacitycool * EFLHcool / 1,000,000) * (FLHcool * Capacitycool * (1/IEERbase - 1/IEERee)) * 3,412 / 1,000 / 1,000,000 |
|  | = ((0.0 * 989 * 96000)/1,000,000) + (989 * 96000 * (1/14.4-1/18.5)) * 3,412 / 1,000 / 1,000,000 |
|  | = 5.0 MMBtu |
| SiteEnergySavings (MMBTUs) | = 153.9 + 3.30 – 37.9 + 5.0 = 124.3 [Measure is eligible] |

Savings would be claimed as follows, assuming a 50%-50% incentive agreement:

| Measure supported by: | Electric Utility claims (kWh): | Gas Utility claims (therms): |
| --- | --- | --- |
| Electric utility only | 124.3 * 1,000,000/3,412 = 36,430 kWh | N/A |
| Electric and gas utility (Note utilities may make alternative agreements to how savings are allocated as long as total MMBtu savings remains the same). | 0.5 * 124.3 * 1,000,000/3,412 = 18,215 kWh | 0.5 * 124.3 * 10 = 622 therms |
| Gas utility only | N/A | 124.3 * 10 = 1,243 therms |

###### Summer Coincident Peak Demand Savings

ΔkW = (Capacitycool / 1,000 * (1/EERbase – 1/EERee)) *CF

Where:

EERbase		= Energy Efficiency Ratio of the baseline equipment

= EER from tables below, based on the applicable Code on the date of equipment purchase (if unknown assume current Code). For air-cooled units < 65 kBtu/hr, assume the following conversion from SEER to EER for calculation of peak savings:

EER = (-0.02 * SEER2) + (1.12 * SEER)

EERee	= Energy Efficiency Ratio of the energy efficient equipment. For air-cooled units < 65 kBtu/hr, if the actual EERee is unknown, assume the conversion from SEER to EER as provided above.

= Actual installed

CF value is chosen between:

CFSSP	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

For example, a heat recovery VRF system with 8-ton cooling capacity and 96 kbtu heating capacity, an efficient EER of 12.5, saves:

ΔkW 	= (96,000/1,000 * (1/10.8 – 1/12.5)) *0.913

= 1.1 kW

###### Fossil Fuel Savings

Calculation provided together with Electric Energy Savings above.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

COST EFFECTIVENESS SCREENING AND LOAD REDUCTION FORECASTING WHEN FUEL SWITCHING

This measure can involve fuel switching from gas to electric.

For the purposes of forecasting load reductions due to fuel switch ASHP projects per Section 16-111.5B, changes in
site energy use at the customer’s meter (using ΔkWh algorithm below), customer switching estimates, NTG, and any other adjustment factors deemed appropriate, should be used.

The inputs to cost effectiveness screening should reflect the actual impacts on the electric and fuel consumption at the customer meter and, for fuel switching measures, should therefore reflect the decrease in one fuel and increase in another, as opposed to the single savings value calculated in the “Electric and Fossil Fuel Energy Savings” section above. Therefore in addition to the calculation of savings claimed, the following values should be used to assess the cost effectiveness of the measure.

| ΔTherms | = [Heating Consumption Replaced] = [GasHeatAdj * HeatLoad * 1/AFUEbase) / 100,000] |
| --- | --- |
| ΔkWh | = [FurnaceFanSavings] - [HP heating consumption] + [Cooling savings] |
| For units with cooling capacities less than 65 kBtu/hr: |  |
| ΔkWh | = [FurnaceFlag * HeatLoad * 1/AFUEbase * Fe * 0.000293] - [HeatAdj * HeatLoad/3412 * (1/(COPee ))/1000] + [Cooladj * (Capacitycool * EFLHcool * (1/EERbase - 1/EER_ee))/1000] |
| For units with cooling capacities greater than 65 kBtu/hr: |  |
| ΔkWh | = [FurnaceFlag * HeatLoad * 1/AFUEbase * Fe * 0.000293] - [Heatadj * HeatLoad/3412 * (1/COPee)] + [Cooladj * (Capacitycool * EFLHcool * (1/IEERbase - 1/IEER_ee))/1000] |

###### Measure Code: CI-HVC-VFFY-V4-250101

###### Review Deadline: 1/1/2026

### 4.8.8	Commercial Secondary Windows

###### Description

Commercial Secondary Windows (CSW) are window units with one or more transparent panes in a frame that attach to the interior or exterior of existing windows without replacing the original glass or frame. Secondary windows are retrofitted to existing commercial windows to improve their overall thermal performance by adding a layer of glazing. CSWs have a non-disruptive installation and can improve windows to meet current IECC standards, resulting in heating and cooling energy savings.

Single-pane clear windows can increase the energy load through increased heat gain or heat loss, ultimately disrupting occupant comfort, and raising energy costs. Replacing windows can be costly, time-consuming, and disruptive to occupants, and hence it presents an opportunity of secondary window retrofits as a cost-effective energy efficiency measure.

A prescriptive methodology was developed to calculate energy savings associated with CSW retrofits in different commercial buildings across all Illinois climate zones through an energy modeling analysis. An AERC single-pane, metal-framed window was used as the baseline during the analysis and compared to a CSW retrofit meeting IECC 2021 standards for exterior fenestration assemblies. Heating and Cooling energy savings factors are derived from the energy modeling analysis for different building types and climate zones in Illinois and are utilized in the methodology section to calculate measure energy savings.

An external spreadsheet calculator has been developed to calculate energy savings associate with this measure based on building-specific inputs listed below.

- Building Types

- Hospital, Hotel, Multifamily, Office, Restaurant, Retail/Strip Mall and School

- Total Area of CSW Retrofit

- Heating System Fuel

- Gas or Electric

- Gas Heating System Efficiency

- Electric Heating System Efficiency

- Cooling System Efficiency

- Building Location Zip Code

  - Zip codes for the state of Illinois matching one of the following climate zones:

    - 1 – Rockford

    - 2– Chicago

    - 3– Springfield

    - 4– Belleville

    - 5 – Marion

The calculator incorporates heating and cooling energy savings factors for different building types and locations based on the energy modeling analysis performed on the DOE's Prototype Building Models.

###### Definition of Efficient Equipment

Efficient equipment in this measure refers to commercial secondary windows (CSW) retrofitted in buildings. Retrofitted CSW assembly shall have minimum thermal properties as indicated in table below.

|  | Center of Glass U-Factor of the Overall window assembly with CSW Retrofit (Btu/hr °F ft2) | Solar Heat Gain Coefficient of the Overall window assembly with CSW Retrofit |
| --- | --- | --- |
| Efficient CSW Unit | 0.36 | 0.58 |

###### Definition of Baseline Equipment

Baseline equipment refers to existing non-operable clear single-pane windows in existing buildings.

###### Deemed Lifetime of Efficient Equipment

The measure life is assumed to be 30 years.

###### Deemed Measure Cost

Total installation cost for retrofitting the Commercial Secondary Windows is the deemed measure cost. Total measure cost is assumed to be 32$ per square feet of CSW systems installed.

###### Loadshape

Loadshape C03- Commercial Cooling

Loadshape C04 - Commercial Electric Heating

Loadshape C05 - Commercial Electric Heating and Cooling

###### Coincidence Factor

CFSSP	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period

= 47.8%

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh 	= (ΔkWh_cooling + ΔkWh_heatingElectric + ΔkWh_heatingGas)

ΔkWh_cooling		= CSF * A *3412.14/ (ηCool*1000)

Where:

CSF		= Cooling energy savings factor, kWh/ft2/Btu/Wh

| Building Types | Cooling Energy Savings Factor for Different Climate Zones and Building Types (kWh/ft2/BTU/Wh) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1-Rockford | 2-Chicago | 3-Springfield | 4-Belleville | 5-Marion |
| Hospital | 19.48 | 19.41 | 21.42 | 21.37 | 21.24 |
| Hotel | 16.07 | 16.21 | 18.61 | 18.09 | 18.61 |
| Multifamily | 14.46 | 14.54 | 16.96 | 16.54 | 17.32 |
| Office | 16.24 | 15.87 | 17.91 | 17.06 | 17.91 |
| Restaurant | 13.54 | 13.63 | 16.19 | 15.63 | 16.55 |
| Retail/Strip Mall | 16.54 | 16.80 | 18.92 | 17.98 | 18.82 |
| School | 16.51 | 16.12 | 18.31 | 17.09 | 17.79 |

A		= Area of CSW system installed, ft2

ηCool		= Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh)

= Actual value (where new or where it is possible to measure or reasonably estimate) or refer to IECC 2012 minimum efficiency ratings based on the type of cooling equipment or refer to the table below if equipment type is unknown.

| Equipment Type | ŋCool Estimate |
| --- | --- |
| Unknown cooling equipment | 13 |

ΔkWh_heatingElectric	= HSF * A * 8.58/ ηHeat

Where:

HSF		= Heating energy savings factor, Therms/ft2/Btu/Wh

= Refer to Fossil Fuel Savings section

8.58		= Factor to account for Therms to Wh and for Btu to kWh unit conversions

ηHeat		= Efficiency of heating system

= Actual value (where new or where it is possible to measure or reasonably estimate) or refer to CFR 431 minimum efficiency ratings based on the type of heating equipment or refer to the table below if equipment type is unknown.

| System Type | Age of Equipment | HSPF Estimate | ηHeat (Effective COP Estimate) (HSPF/3.413) |
| --- | --- | --- | --- |
| Resistance | N/A | N/A | 1 |
| Unknown | N/A | 10.92 | 3.2 |

ΔkWh_heatingGas	= If gas furnace heat, kWh savings for reduction in fan run time

= ΔTherms * Fe * 29.3

Where:

Fe	= Furnace Fan energy consumption as a percentage of annual fuel consumption

= 7.7%

29.3 		= kWh per therm

For Example, a hotel in Rockford with an all electric HVAC system installing 50 sqft of commercial secondary windows would save:

ΔkWh = ΔkWh Cooling + ΔkWh HeatingElectric + ΔkWh HeatingGas

ΔkWh Cooling 	= CSF * A * 3,412.14 / (ηCool * 1,000)

= 16.07 * 50 * 3412.14/(13 * 1000)

= 210.9 kWh

ΔkWh Heating Electric = HSF * A * 8.58 / ηHeat

= 0.94 * 50 * 8.58/3.2

= 126.1 kWh

ΔkWh 	= 210.9 + 126.1 + 0

= 337.0 kWh

###### Summer Coincident Peak Demand Savings

∆kW		= (∆kWh_cooling / EFLH_cooling) * CF

Where:

EFLHcooling 	= Equivalent full load hours of air conditioning in Existing Buildings or New Construction are provided in Section 4.4, HVAC end use

CFSSP 	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

###### Fossil Fuel Savings

ΔTherms	= (HSF * A) / ηHeat

Where:

HSF			= Heating energy savings factor, Therms/ft2

| Building Types | Heating Energy Savings Factor for Different Climate Zones and Building Types (Therms/ft2) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1-Rockford | 2-Chicago | 3-Springfield | 4-Belleville | 5-Marion |
| Hospital | 0.83 | 0.80 | 0.64 | 0.62 | 0.61 |
| Hotel | 0.94 | 0.89 | 0.77 | 0.71 | 0.69 |
| Multifamily | 1.03 | 0.99 | 0.88 | 0.79 | 0.76 |
| Office | 0.82 | 0.80 | 0.72 | 0.65 | 0.63 |
| Restaurant | 0.96 | 0.90 | 0.81 | 0.76 | 0.73 |
| Retail/Strip Mall | 0.90 | 0.84 | 0.76 | 0.72 | 0.69 |
| School | 0.85 | 0.83 | 0.75 | 0.69 | 0.66 |

ηHeat	= Efficiency of heating system in Et or Ec where Et is the thermal efficiency and Ec is the combustion efficiency as defined in 10 CFR 431.

= Actual or if known use values from table below

| Equipment type | Certified rated input | ηHeat |
| --- | --- | --- |
| Gas Furnaces | ≥300,000 Btu/h (from 01/01/1994 – 01/01/2023) | 80% Et |
|  | ≥300,000 Btu/h (After 01/01/2023) | 81% Et |
| Gas-fired hot water Boilers | ≥300,000 Btu/h and ≤2,500,000 Btu/h | 80% Et |
|  | >2,500,000 Btu/h | 82% Ec |
| Gas-fired steam Boilers | ≥300,000 Btu/h (till 03/02/2022) | 77% Et |
|  | ≥300,000 Btu/h (after 03/02/2022) | 79% Et |

For Example, a hotel in Rockford with a gas furnace installed before 2023 installing 50 sqft of Commercial Secondary Windows would save:

ΔkWh = ΔkWh Cooling + ΔkWh HeatingElectric + ΔkWh Heating Gas

ΔkWh HeatingGas = ΔTherms * Fe * 29.3

ΔTherms = HSF * A * ηHeat

= 0.94 * 50 * 80%

= 37.6 Therms

ΔkWh Heating Gas = 37.6 * 7.7% * 29.3

= 84.8 kWh

ΔkWh = 210.9 + 0 + 84.8

= 295.7 kWh

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-SHL-CSW-V02-250101

###### Review Deadline: 1/1/2029

### 5.6.3	Floor Insulation Above Crawlspace

###### Description

Insulation is added to the floor above a vented crawl space that does not contain pipes or HVAC equipment. If there are pipes, HVAC, or a basement, it is desirable to keep them within the conditioned space by insulating the crawl space walls and ground. Insulating the floor separates the conditioned space above from the space below the floor, and is only acceptable when there is nothing underneath that could freeze or would operate less efficiently in an environment resembling the outdoors. Even in the case of an empty, unvented crawl space, it is still considered best practice to seal and insulate the crawl space perimeter rather than the floor. Not only is there generally less area to insulate this way, but there are also moisture control benefits. There is a “Basement Insulation” measure for perimeter sealing and insulation. This measure assumes the insulation is installed above an unvented crawl space and should not be used in other situations.

This measure was developed to be applicable to the following program types:  RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

This measure requires a member of the implementation staff or a participating contractor to evaluate the pre and post R-values and measure surface areas. The requirements for participation in the program will be defined by the utilities.

###### Definition of Baseline Equipment

The existing condition will be evaluated by implementation staff or a participating contractor and is likely to be no insulation on any surface surrounding a crawl space.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 30 years.

Note a mid-life adjustment to account for replacement of HVAC equipment during the measure life should be applied after 10 years or 13 years for boilers. See section below for detail.

###### Deemed Measure Cost

The actual installed cost for this measure should be used in screening.

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

Loadshape R08 - Residential Cooling

Loadshape R09 - Residential Electric Space Heat

Loadshape R10 - Residential Electric Heating and Cooling

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period, and is presented so that savings can be bid into PJM’s capacity market.

CFSSP 		= Summer System Peak Coincidence Factor for Central A/C (during utility peak hour)

= 68%

CFSSP SF  	= Summer System Peak Coincidence Factor for Heat Pumps in single family homes (during system peak hour)

= 72%

CFSSP, MF	= Summer System Peak Coincidence Factor for Heat Pumps in multifamily homes (during system peak hour)

= 67%

CFPJM  	= PJM Summer Peak Coincidence Factor for Central A/C (average during PJM peak period)

= 46.6%

CFPJM SF 	= PJM Summer Peak Coincidence Factor for Heat Pumps in single family homes (average during PJM peak period)

= 46.6%

CFPJM, MF	= PJM Summer Peak Coincidence Factor for Heat Pumps in multifamily homes (average during peak period)

= 28.5%

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

Where available savings from shell insulation measures should be determined through a custom analysis. When that is not feasible for the program the following engineering algorithms can be used with the inclusion of an adjustment factor to de-rate the heating savings.

ΔkWh	= (ΔkWh_cooling + ΔkWh_ heatingElectric + ΔkWh_heatingFurnace)

Where:

ΔkWh_cooling 	= If central cooling, reduction in annual cooling requirement due to insulation

= ((((1/R_old - 1/(R_added+R_old)) * Area * (1-Framing_factor)) * 24 * CDD * DUA) / (1000 * ηCool))) * ADJFloorCool * %Cool

R_old	= R-value value of floor before insulation, assuming 3/4” plywood subfloor and carpet with pad

= Actual. If unknown assume 3.53

R_added	= R-value of additional spray foam, rigid foam, or cavity insulation.

Area	 	= Total floor area to be insulated

Framing_factor	= Adjustment to account for area of framing

= 12%

24		= Converts hours to days

CDD	= Cooling Degree Days

| Climate Zone (City based upon) | Conditioned CDD 65 |
| --- | --- |
| 1 (Rockford) | 877 |
| 2 (Chicago) | 1047 |
| 3 (Springfield) | 1183 |
| 4 (Belleville) | 1641 |
| 5 (Marion) | 1450 |
| Weighted Average | 1098 |

DUA	= Discretionary Use Adjustment (reflects the fact that people do not always operate their AC when conditions may call for it).

= 0.75

1000		= Converts Btu to kBtu

ηCool		= Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh)

= Actual (where it is possible to measure or reasonably estimate). Note where new HVAC is installed in addition to shell measures, the old HVAC unit efficiency should be used and the shell measure savings calculated first, the HVAC measure then assuming the reduced heat/cooling loads. If using rated efficiencies, derate efficiency value by 1% per year  (maximum of 30 years) to account for degradation over time, or if unknown assume the following. If unknown value is used, it should not be derated by age.

| Age of Equipment | ηCool Estimate |
| --- | --- |
| Before 2006 | 9.5 |
| 2006 - 2014 | 12.4 |
| Central AC After 1/1/2015 | 12.4 |
| Heat Pump After 1/1/2015 | 13.3 |
| Unknown (for use in program evaluation only) | 10.0 |

ADJFloorCool 	= Adjustment for cooling savings from floor to account for prescriptive engineering algorithms overclaiming savings

= 75%

%Cool	= Percent of homes that have cooling

| Central Cooling? | %Cool |
| --- | --- |
| Yes | 100% |
| No | 0% |
| Unknown (for use in program evaluation only) | 66% |

ΔkWh_heatingElectric 	= If electric heat (resistance or heat pump), reduction in annual electric heating due to insulation

= (((1/R_old - 1/(R_added + R_old)) * Area * (1-Framing_factor) * 24 * HDD)/ (3,412 * ηHeat)) * ADJFloorHeat *%ElectricHeat

HDD		= Heating Degree Days:

| Climate Zone (City based upon) | Conditioned HDD 60 |  |
| --- | --- | --- |
| 1 (Rockford) | 5230 |
| 2 (Chicago) | 4798 |
| 3 (Springfield) | 4266 |
| 4 (Belleville) | 3188 |
| 5 (Marion/Murphysboro) | 3390 |
| Weighted Average | 4631 |

ηHeat	= Efficiency of heating system

= Actual Heating Efficiency * Distribution Efficiency (where it is possible to measure or reasonably estimate). Note where new HVAC is installed in addition to shell measures, the old HVAC unit efficiency should be used and the shell measure savings calculated first, the HVAC measure then assuming the reduced heat/cooling loads. If using rated efficiencies, derate efficiency value by 1% per year  (maximum of 30 years) to account for degradation over time, or if not available refer to default table below. If unknown value is used, it should not be derated by age. If actual Distribution Efficiency is not available, use 85%.

| System Type | Age of Equipment | HSPF2 Estimate | ηHeat (Effective COP Estimate * Distribution Efficiency) (HSPF2/3.413)*0.85 |
| --- | --- | --- | --- |
| Heat Pump (if age unknown, assume 2006-2014) | Before 2006 | 5.8 | 1.44 |
|  | After 2006 -2014 | 6.5 | 1.62 |
|  | 2015 on | 7 | 1.74 |
| Resistance | N/A | N/A | 1 |
| Unknown (for use in program evaluation only) | N/A | N/A | 1.32 |

ADJFloorHeat	= Adjustment for floor insulation to account for prescriptive engineering algorithms overclaiming savings

= 63%

%ElectricHeat	= Percent of homes that have electric space heating

= 100 % for Electric Resistance or Heat Pump

= 0 % for Fossil Fuel heating

= If unknown, use the following table:

| Utility | Location |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Single Family | Single Family Low Income | Multi Family | Multi Family Low Income | Unknown |
| Ameren | 18% | 26% | 38% | 39% | 29% |
| ComEd | 14% | 22% | 43% | 48% | 21% |
| PGL | 1.0% | 1.5% | 4.0% | 2.8% | 2.2% |
| NSG | 1.3% | 0.8% | 32.5% | 1.2% | 3.3% |
| Nicor | 1.3% | 0.8% | 32.5% | 1.2% | 3.3% |
| All DUs |  |  |  |  | 26% |

Note: If a measure is supported by a gas and electric utility through a joint program, and it is unknown whether the participant has a gas supply, the electric utility values in the table above should be used. If it is known that the participant has a gas supply, the values from the gas utility above should be applied.

Other factors as defined above.

For example, a single family home in Chicago with a 20 by 25 footprint, insulated with R-30 spray foam above the crawlspace, a 10.5 SEER Central AC and a newer heat pump:

ΔkWh 	= (ΔkWh_cooling + ΔkWh_heating)

= ((((1/3.53 -1/(30+3.53))*(20*25)*(1-0.12)* 24 * 1047*0.75)/(1000*10.5)) * 0.75 * 1 + (((1/3.53 -1/(30+3.53))*(20*25)*(1-0.15) * 24 * 4798)/(3412*1.92)) * 0.63 * 1)

= (150.1 + 1192.9)

= 1343 kWh

ΔkWh_heatingFurnace	= If fossil fuel furnace heat, kWh savings for reduction in fan run time

= ΔTherms * Fe * 29.3

Fe		= Furnace Fan energy consumption as a percentage of annual fuel consumption

= 3.14%

29.3		= kWh per therm

For example, a single family home in Chicago with a 20 by 25 footprint, insulated with R-30 spray foam above the crawlspace, and a 70% efficient furnace (for therm calculation see Fossil Fuel Savings section):

ΔkWh 	= 112.4 * 0.0314 * 29.3

= 103.4 kWh

###### Summer Coincident Peak Demand Savings

ΔkW 	= (ΔkWh_cooling / FLH_cooling) * CF

Where:

FLH_cooling	= Full load hours of air conditioning

= Dependent on location:

| Climate Zone (City based upon) | Single Family | Multifamily |
| --- | --- | --- |
| 1 (Rockford) | 547 | 499 |
| 2 (Chicago) | 709 | 629 |
| 3 (Springfield) | 779 | 707 |
| 4 (Belleville) | 1082 | 982 |
| 5 (Marion) | 956 | 868 |
| Weighted Average ComEd Ameren Statewide | 676 875 731 | 603 791 655 |

Use Multifamily if: Building meets utility’s definition for multifamily and HVAC system serves single unit. For residential sized systems serving 2 or more units, assume single family hours.

CFSSP 		= Summer System Peak Coincidence Factor for Central A/C (during utility peak hour)

= 68%

CFSSP SF  	= Summer System Peak Coincidence Factor for Heat Pumps in single family homes (during system peak hour)

= 72%

CFSSP, MF	= Summer System Peak Coincidence Factor for Heat Pumps in multifamily homes (during system peak hour)

= 67%

CFPJM  	= PJM Summer Peak Coincidence Factor for Central A/C (average during PJM peak period)

= 46.6%

CFPJM SF 	= PJM Summer Peak Coincidence Factor for Heat Pumps in single family homes (average during PJM peak period)

= 46.6%

CFPJM, MF	= PJM Summer Peak Coincidence Factor for Heat Pumps in multifamily homes (average during peak period)

= 28.5%

For example, a single family home in Chicago with a 20 by 25 footprint, insulated with R-30 spray foam above the crawlspace, a 10.5 SEER Central AC and a newer heat pump:

ΔkWSSP 	= 150.1 / 709 * 0.68

= 0.144 kW

ΔkWSSP 	= 150.1 / 709 * 0.466

= 0.099 kW

###### Fossil Fuel Savings

If Fossil Fuel heating:

ΔTherms 	= (((1/R_old - 1/(R_added+R_old)) * Area * (1-Framing_factor) * 24 * HDD) / (100,000 * ηHeat)) * ADJFloorHeat * %FossilHeat

Where:

ηHeat		= Efficiency of heating system

= Equipment efficiency * distribution efficiency

= Actual (where it is possible to measure or reasonably estimate). Note where new HVAC is installed in addition to shell measures, the old HVAC unit efficiency should be used and the shell measure savings calculated first, the HVAC measure then assuming the reduced heat/cooling loads. If using rated efficiencies, derate efficiency value by 1% per year  (maximum of 30 years) to account for degradation over time, or if unknown assume 72% for existing system efficiency. If unknown value is used, it should not be derated by age. If actual Distribution Efficiency is not available, use 85%.

%FossilHeat	= Percent of homes that have fossil fuel space heating

= 100 % for Fossil Fuel heating

= 0 % for Electric Resistance or Heat Pump

= If unknown, use the following table:

| Utility | Location |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Single Family | Single Family Low Income | Multi Family | Multi Family Low Income | Unknown |
| Ameren | 82% | 74% | 62% | 61% | 71% |
| ComEd | 86% | 78% | 57% | 52% | 79% |
| PGL | 98.9% | 98.5% | 96.0% | 96.9% | 97.7% |
| NSG | 98.3% | 99.2% | 67.5% | 98.8% | 96.6% |
| Nicor | 98.3% | 99.2% | 67.5% | 98.8% | 96.6% |
| All DUs |  |  |  |  | 74% |

Note: If a measure is supported by a gas and electric utility through a joint program, and it is unknown whether the participant has a gas supply, the electric utility values in the table above should be used. If it is known that the participant has a gas supply, the values from the gas utility above should be applied.

Other factors as defined above.

For example, a single family home in Chicago with a 20 by 25 footprint, insulated with R-30 spray foam above the crawlspace, and a 72% efficient furnace:

ΔTherms = ((1 / 3.53 – 1 /(30 + 3.53))*(20 * 25) * (1 - 0.12) * 24 * 4798) / (100,000 * 0.72) * 0.63 * 1

= 112.4 therms

Mid-Life adjustment

In order to account for the likely replacement of existing heating and cooling equipment during the lifetime of this measure, a mid-life adjustment should be applied. To calculate the adjustment, re-calculate the savings above using the following new baseline system efficiency assumptions:

| Efficiency Assumption | System Type | New Baseline Efficiency |
| --- | --- | --- |
| ηCool | Central AC | 13.4 SEER2 |
|  | Heat Pump | 14.3 SEER2 |
| ηHeat | Electric Resistance | 1.0 COP |
|  | Heat Pump (7.5HSPF/3.413)*0.85 | 1.87 COP |
|  | Gas Furnace 80% AFUE * 0.85 | 68% AFUE |
|  | Oil Furnace 83% AFUE * 0.85 | 71% AFUE |
|  | Gas Boiler | 84% AFUE |
|  | Oil Boiler | 86% AFUE |

This reduced annual savings should be applied following the assumed remaining useful life of the existing equipment, estimate to be 10 years or 13 years for boilers. Note if the existing equipment efficiency is greater than the new baseline efficiency listed above, do not apply a mid-life adjustment.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: RS-SHL-FINS-V17-250101

###### Review Deadline: 1/1/2030

Consortium for Energy Efficiency (CEE), Testing, Testing, M1, 2, 3, Transitioning to New Federal Minimum Standards, CEE Summer Program Meeting, August, 2022.

Consistent with Residential assumptions – should be updated with Commercial data when available. Program tracking data from ComEd and Ameren between 2018 and 2020 was used to develop these assumptions. During this period the air source heat pump programs operated downstream and projects were classified as Time of Sale or Early Replacement. Note that any fuel switch scenario at the time would have been classified as Time of Sale and therefore the rates provided likely represent a low estimate of the true early replacement rates. In the absence of alternative data, the TAC agreed to apply these rates and the deemed full v partial displacement assumptions listed, but these assumptions should be revisited through future evaluation.

Consistent with Residential measure and based on 2016 DOE Rulemaking Technical Support document, as recommended in Guidehouse ‘ComEd Effective Useful Life Research Report’, May 2018.

Assumed to be one third of effective useful life of replaced equipment.

Assume full measure life (16 years) for replacing electric resistance as we would not expect that resistance heat would fail during the lifetime of the efficient measure.

Based on a review of TRM incremental cost assumptions from Vermont, Wisconsin, and California.

Full install ASHP costs are based upon data provided by Ameren. See ‘ASHP Costs_06242022’.

Furnace and boiler costs are based on data provided in Appendix E of the Appliance Standards Technical Support Documents including equipment cost and installation labor. Where efficiency ratings are not provided, the values are interpolated from those that are.

Based on 3 ton initial cost estimate for a conventional unit from ENERGY STAR Central AC calculator

The cost per ton table provides reasonable estimates for installation costs of DMSHP, which can vary significantly due to requirements of the home. It is estimated that all units, even those 1 ton or less will be at least $2000 to install.

Full costs based upon full install cost of an ASHP plus incremental costs provided in Memo from Opinion Dynamics Evaluation Team, Ductless Mini-Split Heat Pumps: Incremental Cost Analysis, April 27, 2017.

Memo from Opinion Dynamics Evaluation Team, Ductless Mini-Split Heat Pumps: Incremental Cost Analysis, April 27, 2017

All baseline replacement costs are consistent with their respective measures and include inflation rate of 1.91%.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Blended Baseline value came from percentage of accounts with heat pumps (40.17%) at 7.5 HSPF2 and electric furnaces (59.83%) at 3.41 HSPF as reported in the ComEd Baseline Study August 14, 2020.

Adjustment factors are based on findings from NEEA, July 2020 ‘EXP07:19 Load-based and Climate-Specific Testing and Rating Procedures for Heat Pumps and Air Conditioners’. See ‘NEEA HP data’ for calculation. Findings were consistent with other reviewed sources including ASHRAE, 2020 ‘Right-Sizing Electric Heat Pump and Auxiliary Heating for Residential Heating Systems Based on Actual Performance Associated with Climate Zone’ and Cadmus, 2022 ‘Residential ccASHP Building Electrification Study’. The difference between HSPF and HSPF2 ratings is based on the change in testing procedure that will correct for some of this effect where ducted systems will have an approximately 9% lower HSPF2 rating as compared to HSPF, based on CEE presentation, July 2022, ‘Testing Testing, M1, 2, 3: Transitioning to New Federal Minimum Standards’.

Weighting for Ameren is based on electric heat accounts in each of the heating zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Based on Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder. Note this is appropriate for single speed units only.

Values based on Morehead Energy 2024 analysis of TMYx typical hourly weather data for 2007-2021. See 'ASHP Partial Displacement Analysis 20240611_HDD55.xlsx'.

Weighting for Ameren is based on electric heat accounts in each of the heating zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Values based on Morehead Energy 2024 analysis of TMYx typical hourly weather data for 2007-2021. See 'ASHP Partial Displacement Analysis 20240611_HDD55.xlsx'.

Weighting for Ameren is based on electric heat accounts in each of the heating zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Fe is estimated using TRM models for the three most popular building types for programmable thermostats: low-rise office (10.2%), sit-down restaurant (8.6%), and retail – strip mall (4.4%). 7.7% reflects the average Fe of the three building types. See “Fan Energy Factor Example Calculation 2021-06-23.xlsx” for reference.

Code of Federal Regulations: Table 3 to §431.97—Updates to the Minimum Cooling Efficiency Standards for Air Conditioning and Heating Equipment and Table 4 to §431.97—Updates to the Minimum Heating Efficiency Standards for Air-Cooled Air Conditioning and Heating Equipment [Heat Pumps]. For 1/1/2024 compliance dates, note these manufacturing and import federal standards go into effect on 1/1/2023. The measure characterization is recommending delaying adopting these standards until 1/1/2024.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Based on ComEd Small Business Trade Ally feedback. For units rated at less than 20 ton units, the cost of common repairs is under $2,000, significantly less than the cost of purchasing new equipment. Therefore, if the cost of repair is less than $2,000, it can be considered early replacement because customers would repair instead of replace a failed unit. Repair cost data was not available for units larger than 20 tons.

Consortium for Energy Efficiency (CEE), Testing, Testing, M1, 2, 3, Transitioning to New Federal Minimum Standards, CEE Summer Program Meeting, August, 2022.

Measure Life Report: Residential and Commercial/Industrial Lighting and HVAC Measures, GDS Associates, Inc., June 2007.

Assumed to be one third of effective useful life.

CEE Commercial Unitary Air-conditioning and Heat Pumps Specification, which provides high efficiency performance specifications for single-package and split system unitary air conditioners.

NEEP Incremental Cost Study (ICS) Final Report – Phase 3, May 2014.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

The two equations are provided to show how savings are determined during the initial phase of the measure (existing to efficient) and the remaining phase (new baseline to efficient). In practice, the screening tools used may either require a First Year savings (using the first equation) and then a “number of years to adjustment” and “savings adjustment” input which would be the (new base to efficient savings)/(existing to efficient savings).

Code of Federal Regulations: Table 3 to §431,97 – Updates to Minimum Cooling Efficiency Standards for Air Conditioning and Heating Equipment

Based on Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder. Note this is appropriate for single speed units only.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Measure life as referenced in Michigan CI Technologies & Franklin Energy “Work paper FES-H8a – Steam Trap Monitoring System” dated September 2016.

The Everactive Steam Trap Monitoring Service Price

This factor includes 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study. For more information please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’. Note since the water loss associated with this measure is due to evaporation and does not discharge into the wastewater system, only the water supply factor is used here.

Dry cleaners survey data as referenced in CLEAResult “Work Paper Steam Traps Revision #2" Revision 3 dated March 2, 2012.

The energy savings estimates of this measure assume that without an automatic steam trap monitoring system, manual audits would be performed once per year, so a leaking steam trap would, on average, leak for 6 months before being detected and repaired/replaced when the trap fails

Results from Steam Trap Audit/Replacement efficiency improvement research through the C&I and public Sector Prescriptive Rebate Program, Small Business Program and the Multi-family program. The evaluation included project and population data from years 2019 through 2022

Heat of vaporization of steam at the inlet pressure to the steam trap. Implicit assumption that the average boiler nominal pressure where the vaporization occurs, is essentially that same pressure. Referenced in CLEAResult “Work Paper Steam Traps Revision #2" Revision 3 dated March 2, 2012.

Results from Armstrong International research through the steam trap management platform SAGE. The research population data included Commercial Heating LPS as well as Industrial or Process Low Pressure, < 15 psi applications. The search of the database yield 120,853 steam traps meeting these parameters: Average orifice size 0.21” and average pressure 11.2 psi.

US DOE Building America Program. Building America Analysis Spreadsheet. For Chicago, IL.

Medium and high-pressure steam trap annual operating hours based on Navigant analysis of source collected during program implementation by Nicor Gas for GPY1 through GPY4. For each steam trap project, the data provided measure savings description, operating pressure, installation Zip code, business building type, program year, and annual operating hours.

US DOE Building America Program. Building America Analysis Spreadsheet. For Chicago, IL.

Katrakis, J. and T.S. Zawacki. “Field-Measured Seasonal Efficiency of Intermediate-sized Low-Pressure Steam Boilers”. ASHRAE V99, pt. 2, 1993.

See “Derivation of Equation for Subsonic Compressible Flow through an Orifice and Supporting Calculations for Illinois TRM Steam Trap Measure” paper for more information

Enbridge adjustment factor used as referenced in CLEAResult “Work paper Steam Traps Revision #2” Revision 3 dated March 2, 2012 and DOE Federal Energy Management Program Steam Trap Replacement Assessment.

Default values are directly calculated using the equations above.

Medium and high-pressure steam trap inlet pressure based on Navigant analysis of source collected during program implementation by Nicor Gas for GPY1 through GPY4. For each steam trap project, the data provided measure savings description, operating pressure, installation Zip code, business building type, program year, and annual operating hours. Dry cleaning steam trap inlet pressure based on C5 Steam Traps – Nicor FINAL 10.27.11.

Default values are directly calculated using the equations above.

Results from Armstrong International research through the steam trap management platform SAGE. The research population data included Commercial Heating LPS as well as Industrial or Process Low Pressure, < 15 psi applications. The search of the database yields 120,853 steam traps meeting these parameters: Average orifice size 0.21” and average pressure 11.2 psi.

Consistent with Residential air source heat pump measure and based on a 2016 DOE Rulemaking Technical Support document, as recommended in Guidehouse ‘ComEd Effective Useful Life Research Report’, May 2018.

Estimated measure incremental costs for PTHP, HP RTU and PTAC based other incremental costs and differences in installed cost from U.S. Energy Information Administration (EIA), Updated Buildings Sector Appliance and Equipment Costs and Efficiencies: https://www.eia.gov/analysis/studies/buildings/equipcosts/pdf/full.pdf. For Ducted Split HP, Packaged Single Zone Furnace + AC and Packaged VAV RTU is based on Mid-Atlantic Technical Reference Manual version 9, Variable Refrigerant Flow (VRF) Heat Pump Systems measure. Published October, 2019. Water-source HP systems estimated from data collected from manufacturers. Water-source heat pump systems were not very different compared to VRF systems.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Based on Variable Refrigerant Flow Study. See ‘Variable Refrigerant Flow Study 2023’.

Based on Variable Refrigerant Flow Study. See ‘Variable Refrigerant Flow Study 2023’.

Based on Variable Refrigerant Flow Study. See ‘Variable Refrigerant Flow Study 2023’.

Fe is estimated using TRM models for the three building types: low-rise office, sit-down restaurant and retail-strip mall. 7.7% represents the average Fe of the three building types. See “Fan Energy Factory Example Calculation 2021-06-23.xlsx” for reference. Mutlifamily is 3%, lower than commercial, due to typically lower fan static pressure in residential style applications.

Based on Wassmer, M. (2003).  A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder. Note this is appropriate for single speed units only.

IECC 2021 – https://codes.iccsafe.org/content/IECC2021P2 based on current state code defined under https://www.energycodes.gov/status/states/illinois

Energy Modeling was Performed in EnergyPlus (E+), using the DOE's Office of Energy Efficiency & Renewable Energy (EERE) Prototype Building Models with different Illinois climate zones. Detailed information on energy modeling methodology, inputs and assumptions along with references are detailed in the calculator tool, see Energy Savings Calculator for CSW 05-15.xlsm

AERC 1 – Attachments Energy Rating Council

See Energy Savings Calculator for CSW 05-15.xlsm

DOE EERE Prototype Buildings

Minimum thermal properties for the efficient Commercial Secondary Window unit are based on the 2021 International Energy Efficiency Code- maximum allowable U-factors and Solar Heat Gain Coefficients (SHGC) for fixed windows.

https://codes.iccsafe.org/content/IECC2021P2/chapter-4-ce-commercial-energy-efficiency#IECC2021P2_CE_Ch04_SecC402

Effective useful life based on commercial secondary glazing systems measure in regional technical forum, technical advisory committee to Northwest Power and Conservation Council.

Commercial Secondary Glazing Systems (nwcouncil.org)

Average total installed cost for CSW systems from “Secondary Glazing Systems: Market and Deployment Development” by Slipstream prepared for the Nicor Gas Energy Efficiency Program.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Cooling energy savings factor based on energy modeling on U.S. Department of Energy – Commercial prototype building models comparing window performance with CSW Retrofits and baseline single pane windows. Energy model inputs, results and assumptions will be externally attached for the Illinois Stakeholder Advisory Group – Technical Advisory Committee (TAC).

Building type classification should be based on definitions under Illinois Technical Reference Manual version 12, volume 1: overview and user guide, section 3.6. IL-TRM_Effective_010124_v12.0_Vol_1_Overview_09222023_FINAL_clean.pdf (ilsag.info).

For building types unknown, building type should be selected to closely resemble one of the building types listed in the table per interpretation of the program implementor based on actual building usage.

International Energy Efficiency Code 2012, chapter 4 Commercial Energy Efficiency, table c403.2.3(1) minimum efficiency requirements: electrically operated unitary air conditioners and condensing units. https://codes.iccsafe.org/content/IECC2012/chapter-4-ce-commercial-energy-efficiency

IECC 2012 conservative minimum SEER rating of 13.0 is assumed for cooling system efficiency if the system type is unknown.

Heating energy savings factor based on energy modeling on U.S. Department of Energy – Commercial prototype building models comparing window performance with CSW Retrofits and baseline single pane windows. Energy model inputs, results and assumptions will be externally attached for the Illinois Stakeholder Advisory Group – Technical Advisory Committee (TAC).

U.S. Department of energy, federal code for standards, Title 10, chapter II, subchapter D, part 431.97(b). eCFR :: 10 CFR Part 431 -- Energy Efficiency Program for Certain Commercial and Industrial Equipment

Fe is estimated using TRM models for the three most popular building types for programmable thermostats: low-rise office (10.2%), sit-down restaurant (8.6%), and retail–strip mall (4.4%). 7.7% reflects the average Fe of the three building types. See “Fan Energy Factor Example Calculation 2021-06-23.xlsx” for reference.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Heating energy savings factor based on energy modeling on U.S. Department of Energy – Commercial prototype building models comparing window performance with CSW Retrofits and baseline single pane windows. Energy model inputs, results and assumptions will be externally attached for the Illinois Stakeholder Advisory Group – Technical Advisory Committee (TAC).

Building type classification should be based on definitions under Illinois Technical Reference Manual version 12, volume 1: overview and user guide, section 3.6. IL-TRM_Effective_010124_v12.0_Vol_1_Overview_09222023_FINAL_clean.pdf (ilsag.info).

For building types unknown, building type should be selected to closely resemble one of the building types listed in the table based on the interpretation of the program implementor.

Code of federal regulations, title 10, chapter ii, subchapter D, part 431, subpart C Energy and water conservation standards.  eCFR :: 10 CFR Part 431 Subpart D -- Commercial Warm Air Furnaces

Code of federal regulations, title 10, chapter ii, subchapter D, part 431, subpart E Energy Efficiency standards.

eCFR :: 10 CFR Part 431 Subpart E -- Commercial Boilers

As recommended in Guidehouse ‘EMV Group A, Deliverable 16 EUL Research – Residential Insulation’, prepared for California Public Utilities Commission, June 2021.

This is intentionally longer than the assumptions found in the early replacement measures as the application of this measure will occur in a variety of homes that will not be targeted for early replacement HVAC systems.

Based on metering of 24 homes with central AC during PY4 and PY5 in Ameren Illinois service territory.

Based on analysis of metering results from 24 heat pumps in Ameren Illinois service territory in PY5 coincident with AIC’s 2010 system peak; ‘Impact and Process Evaluation of Ameren Illinois Company’s Residential HVAC Program (PY5)’.

Multifamily coincidence factors both from; All-Electric Homes PY6 Metering Results: Multifamily HVAC Systems, Cadmus, October 2015

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Based on 2005 ASHRAE Handbook – Fundamentals: assuming ¾” subfloor, ½” carpet with rubber pad, and accounting for a still air film above and below: 0.68 + 0.94 + 1.23 + 0.68 = 3.53

ASHRAE, 2001, “Characterization of Framing Factors for New Low-Rise Residential Building Envelopes (904-RP),” Table 7.1

Weighted based on number of occupied residential housing units in each zone (US Census 2010).

Energy Center of Wisconsin, May 2008 metering study; “Central Air Conditioning in Wisconsin, A Compilation of Recent Field Research”, p31.

Justification for degradation factors can be found on page 14 of ‘AIC HVAC Metering Study Memo FINAL 2_28_2018’. Estimate efficiency as (Rated Efficiency * (1-0.01)^Equipment Age).

These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Central AC was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time means that using the minimum standard is appropriate. Note all ratings have been converted to SEER2 equivalents – since the new rating better reflects the actual efficiency of the units.

As demonstrated in two years of metering evaluation by Opinion Dynamics, see Memo “Results for AIC PY6 HPwES Billing Analysis”, dated February 20, 2015. TAC negotiated adjustment factor is 80%. During update cycle for version v.12, applied the percent change of NCEI Annual Normals CDD65 from 30 yr data set (1981-2010) to more recent 15 yr data (2006-2020) for all cooling-related adjustment values.

Percentage of homes in Illinois that have central cooling from “Table HC7.9  Air Conditioning in Homes in Midwest Region, Divisions, and States, 2009” from Energy Information Administration, 2009 Residential Energy Consumption Survey

National Centers for Environmental Information (NCEI) Annual Normals, from 2006 - 2020, calculated with a base temp of 50°F to account for lower impact of unconditioned space on heating system. There is a county mapping table in Volume 1, Section 3.7 providing the appropriate city to use for each county of Illinois.

Weighted based on number of occupied residential housing units in each zone.

Justification for degradation factors can be found on page 14 of ‘AIC HVAC Metering Study Memo FINAL 2_28_2018’. Estimate efficiency as (Rated Efficiency * (1-0.01)^Equipment Age).

These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Heat Pumps was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time means that using the minimum standard is appropriate. An 85% distribution efficiency is then applied to account for duct losses for heat pumps. Note all ratings have been converted to HSPF2 equivalents – since the new rating better reflects the actual efficiency of the units.

As demonstrated in two years of metering evaluation by Opinion Dynamics, see Memo “Results for AIC PY6 HPwES Billing Analysis”, dated February 20, 2015. TAC negotiated adjustment factor is 60%. During update cycle for version v.12, applied the percent change of NCEI Annual Normals HDD60 from 30 yr data set (1981-2010) to more recent 15 yr data (2006-2020) for all heating-related adjustment values.

Based on the average % Natural Gas used for space heating in Unknown residential structure types across all utilities covered by the IL program. Residence types include: SF, SF LI, MF & MF LI. Utilities included: Ameren, ComEd, People’s Gas, Northshore Gas & Nicor. Data provided from 2016 Ameren Illinois Demand Side Management (DSM) Market Potential Study by Applied Energy Group, ComEd’s 2019 Baseline Survey on residential space heating share, and PY2022-2023 Implementation Contractors Data for People’s Gas, Northshore Gas & Nicor .

For the weighted average calculations, please see the Analysis file. PGL, NSG, Nicor & gas customers were assumed to follow the provided split. ComEd total customers, minus overlap with PGL,NSG & Nicor, therefore electric only homes. Ameren is total customers minus Nicor.

Fe is not one of the AHRI certified ratings provided for residential furnaces, but can be reasonably estimated from a calculation based on the certified values for fuel energy (Ef in MMBtu/yr) and Eae (kWh/yr).  An average of a 300 record sample (non-random) out of 1495 was 3.14%.  This is, appropriately, ~50% greater than the ENERGY STAR version 3 criteria for 2% Fe. See “Programmable Thermostats Furnace Fan Analysis.xlsx” for reference.

Full load hours for Chicago, Moline and Rockford are provided in “Final Evaluation Report: Central Air Conditioning Efficiency Services (CACES), 2010, Navigant Consulting”, p.33. An average FLH/Cooling Degree Day (from NCDC) ratio was calculated for these locations and applied to the CDD of the other locations in order to estimate FLH. There is a county mapping table in Volume 1, Section 3.7 providing the appropriate city to use for each county of Illinois. During update cycle for version v.12, applied percent change of CDD65, NCEI Annual Normals from 30 yr data set (1981-2010) to more recent 15 yr data (2006-2020) to all FLHcool values.

Weighting for Ameren is based on electric accounts in each of the cooling zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Based on metering of 24 homes with central AC during PY4 and PY5 in Ameren Illinois service territory.

Based on analysis of metering results from 24 heat pumps in Ameren Illinois service territory in PY5 coincident with AIC’s 2010 system peak; ‘Impact and Process Evaluation of Ameren Illinois Company’s Residential HVAC Program (PY5)’.

Multifamily coincidence factors both from; All-Electric Homes PY6 Metering Results: Multifamily HVAC Systems, Cadmus, October 2015

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Justification for degradation factors can be found on page 14 of ‘AIC HVAC Metering Study Memo FINAL 2_28_2018’. Estimate efficiency as (Rated Efficiency * (1-0.01)^Equipment Age).

Based on average Nicor PY4 nameplate efficiencies derated by 15% for distribution losses.

Based on the average % Natural Gas used for space heating in Unknown residential structure types across all utilities covered by the IL program. Residence types include: SF, SF LI, MF & MF LI. Utilities included: Ameren, ComEd, People’s Gas, Northshore Gas & Nicor. Data provided from 2016 Ameren Illinois Demand Side Management (DSM) Market Potential Study by Applied Energy Group, ComEd’s 2019 Baseline Survey on residential space heating share, and PY2022-2023 Implementation Contractors Data for People’s Gas, Northshore Gas & Nicor .

For the weighted average calculations, please see the Analysis file. PGL, NSG, Nicor & gas customers were assumed to follow the provided split. ComEd total customers, minus overlap with PGL,NSG & Nicor, therefore gas only homes. Ameren is total customers minus Nicor.

This is intentionally longer than the assumption found in the early replacement measures as the application of this measure will occur in a variety of homes and will not be targeting those homes appropriate for early replacement HVAC systems.