Memorandum

To:	Technical Advisory Committee

FROM:	KEITH CRONIN, PROJECT LEAD and SAM DENT, TECHNICAL LEAD - VEIC

subject:	v14.0 Errata Measures effective 01/01/2026

Date:	6/18/2026

Cc:	CELIA JOHNSON, SAG

This memo documents errata changes to Version 14.0 of the Illinois Technical Reference Manual (TRM) that the Technical Advisory Committee (TAC) recommends be made effective 01/01/2026.

VEIC has provided a summary table below showing the errata measures and a brief summary of what was changed, followed by the v14.0 measures themselves.

TRM Policy Document, Section 3.2.1, states that,

“TAC participants should notify the TAC when a TRM mistake or omission is found. If a significant mistake or omission is found in the TRM that results in an unreasonable savings estimate, the Program Administrators, Evaluators, TRM Administrator, and TAC will strive to reach consensus on a solution that will result in a reasonable savings estimate. For example, an unreasonable savings estimate may result from an error or omission in the TRM.

“In these limited cases where consensus is reached, the TRM Administrator shall inform the Evaluators to use corrected TRM algorithms and inputs to calculate energy and capacity savings, in addition to using the Commission-approved TRM algorithms and inputs to calculate savings. If the corrected TRM algorithms and inputs are stipulated for acceptance by all the parties in the Program Administrator’s savings docket, then the corrected TRM savings verification values may be used for the purpose of measuring savings toward compliance with the Program Administrator’s energy savings goals. Errors and omissions found in the TRM will be officially corrected through the annual TRM Update proceeding and will be identified as ‘Errata’.”

It is our belief and understanding that the following measures have been determined to be consensus errata by the Program Administrators, Evaluators, and the entire TAC. The term ‘errata’ is used to describe these measures, and in accordance with the TRM Policy Document, the Evaluators may use this version of the measures during evaluation of the current program year (in addition to the measures currently in Version 14.0 of the TRM).

Summary of Errata Measures

| Section |  | Measure Name |  | Measure Code |  | Brief Summary of Change | TAC Reviewed and Approved As of |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4.1.14 | High Efficiency Grain Dryer | CI-AGE-GDRY-V03-260101 | Fix to unit issue in algorithm causing significant error in savings. | New |
| 4.4.30 | Notched V Belts for HVAC Systems | CI-HVC-NVBE-V07-260101 | Reverting fan run hour table in algorithm section to prior version as agreed by TAC late in 2025. | New |
| 4.4.62 | Cooling Tower Water Side Economizer | CI-HVC-CTWE-V03-260101 | Measure was overclaiming savings by using full load tons since savings only occurs during cooler weather. 25% load factor added. | New |
| 4.6.13 |  | Add Doors to Open Refrigerated Display Cases |  | CI-RFG-DOOR-V04-260101 |  | Terms relating to night covers and additional lights were not being multiplied by case length. Also units clarified for unit conversions. | New |
| 4.8.2 |  | Spring Loaded Garage Door Hinge |  | CI-SHL-SLDH-V03-260101 |  | Errors in calculation spreadsheet: Three Existing Building Electric savings values were using incorrect hour assumptions and delta T was not adjusted by location. | 12/22/2025 |
| 4.9.10 | Efficient Thermal Oxidizers | CI-MSC-ETOX-V03-260101 | Fixing issue with formula to calculate energy for heating oxidizer combustion air. Changed to compare ambient temp with combustion chamber temperature. | New |
| 5.1.17 | ENERGY STAR All-in-One Clothes Waser-Dryer | RS-APL-ACWD-V03-260101 | Removal of IQadj in efficient consumption algorithm. | New |
| 5.3.4 |  | Duct Insulation and Sealing |  | RS-HVC-DINS-V15-260101 |  | Gas Equivalent Full Load Hours (EFLHs) were incorrectly the same as the electric EFLHs. Fixed to be consistent with other gas measures. | 12/22/2025 |
| 5.7.4 | Heat Pump Swimming Pool Heater | RS-MSC-HPPH-V02-260101 | Adjustments to fuel switch algorithms to reflect actual electric added and gas replaced. | New |
| 6.2.1 |  | Voltage Optimization |  | CC-SYS-VOPT-V04-260101 |  | Update to reflect the ICC’s approval of the Ameren Illinois Multi-Year Integrated Grid Plan (MYIGP) and the new baseline energy use period of 2019-2021. | 12/22/2025 |

### 4.1.14	High Efficiency Grain Dryer

###### Description

This measure characterizes the energy savings from the replacement of an existing inefficient grain dryer with a new efficient grain dryer (Early Replacement incentive program).  Alternatively, this measure is for the purchase of a new high efficiency grain dryer instead of a new standard efficiency grain dryer for an existing facility (Time of Sale program) or a new facility (New Construction incentive program).  Energy savings are achieved by drying grain more efficiently through: improved dryer air flow design, improved dryer controls, warm air heat recovery, and burner efficiency improvements.  Efficient dryers also have the benefits of increased throughput capacity and reduced annual hours of operation.

This measure was developed to be applicable to the following program types: TOS, EREP, and NC. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient equipment is assumed to be a new, high efficiency grain dryer. Bushels per hour must be provided by the manufacturer, as rated at 5% moisture removal rate per bushel processed.

###### Definition of Baseline Equipment

The baseline for this measure is a standard efficiency grain dryer currently on the market.  Bushels per hour must be provided by the manufacturer, as rated at 5% moisture removal rate per bushel processed.

###### Deemed Lifetime of Efficient Equipment

The measure life for the energy-efficient grain dryer is deemed to be 20 years.

###### Deemed Measure Cost

If known, the actual material and labor cost of installation should be used. If unknown, the cost of the measure is assumed to be the values summarized in the table below:

| Tier (bushels per hour) | Tier (annual bushels) | High-Efficiency Dryer Total Installation Cost (for Early Replacement only) | Average Incremental Cost of High-Efficiency Dryer vs Standard Dryer | Average Incremental Cost of Variable Speed Drive added to Cost of High-Efficiency Dryer |
| --- | --- | --- | --- | --- |
| <500 | < 170,000 | $83,000 (Based on baseline price of $50,000 + ($50/Bu/hr * 250 Rated Bu/hr) + Incremental Cost of High Efficiency) | $20,000 | $4,000 (Based on baseline price of $2,500 + 0.046kW/Bu/hr * 250 Rated Bu/hr) *$100/kW) |
| ≥ 500 and < 1,000 | ≥ 170,000 and < 330,000 | $118,000 (Based on 750 Rated Bu/hr) | $30,000 | $6,000 (Based on 750 Rated Bu/hr) |
| ≥ 1,000 and < 2,000 | ≥ 330,000 and < 670,000 | $165,000 (Based on 1,500 Rated Bu/hr) | $40,000 | $9,000 (Based on 1,500 Rated Bu/hr) |
| ≥ 2,000 and < 3,500 | ≥ 670,000 and < 1,200,000 | $258,000 (Based on 2,750 Rated Bu/hr) | $70,000 | $15,000 (Based on 2,750 Rated Bu/hr) |
| ≥ 3,500 and ≤ 5,000 | ≥ 1,200,000 and ≤ 1,700,000 | $363,000 (Based on 4,250 Rated Bu/hr) | $100,000 | $22,000 (Based on 4,250 Rated Bu/hr) |
| > 5,000 | > 1,700,000 | $488,000 (Based on 6,250 Rated Bu/hr) | $125,000 | $31,000 (Based on 6,250 Rated Bu/hr) |

Early Replacement: The full installation cost is provided in the table above. The assumed deferred cost (after 6.5 years [one third of useful life]) of replacing existing equipment with a new baseline unit is assumed to be the installation cost discounted to present value using the nominal discount rate.

###### Loadshape

Loadshape NRE11 – Non-Residential Agriculture

###### Coincidence Factor

There are no summer peak savings associated with this measure as it is assumed grain dryers do no operate during peak summer months.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

If grain dryer is heated exclusively with electricity:

∆kWh  =  CapacityBushels/HrCapacity * Annual_Hr_Use@Rated_CapacityHours * (Moisture%In - Moisture%Out100% - Moisture%OutMoisture_%In - Moisture_%Out) *  GrainLbGrain_Lb_Moisture_/_Bushel * Btuu/LbLb Evap * (1 / Dryer _EffcyStd -1/ Dryer _EffcyEff) / 3,412  + (Dryer _Fan _PowerStandard - Dryer _Fan _PowerEfficient) * Bushels/HrCapacityCapacity  * Annual_Hr_Use@Rated_CapacityHours

Where:

Capacity 	= Capacity of Grain Dryer in Bushels per hour when reducing grain moisture 
content by 5%

= Actual

Hours		= Average annual hours of use of typical grain dryer

= Deemed value of 336.3 hr/year

Annual hours of use were calculated based on following table.  Deemed value is arithmetic average of Average Use per Year

| Savings Tier (Bushels/hr) from Manufacturer | Savings Tier (Bushels/yr) | Hours |
| --- | --- | --- |
| >= 0 Bu/Hr | 170,000 | 340 |
| >= 500 Bu/Hr | 330,000 | 330 |
| >= 1,000 Bu/Hr | 670,000 | 335 |
| >= 2,000 Bu/Hr | 1,200,000 | 343 |
| >= 3,500 Bu/Hr | 1,700,000 | 340 |
| >= 5,000 Bu/Hr | 2,475,000 | 330 |

Moisture%In	= 23%, a deemed value representing average % moisture in grain arriving at grain dryer facility

Moisture%Out	= 15%, a deemed value representing average % moisture in grain after being dried at grain dryer facility

GrainLb    	= Standard weight of a bushel of grain in lbs per bushel. Lookup value from following table.

| Grain Type | Weight of "Standard Bushel" |
| --- | --- |
| Alfalfa | 60.0 Lb/Std Bu |
| Barley | 48.0 Lb/Std Bu |
| Clover | 60.0 Lb/Std Bu |
| Corn, Shelled (15.5%) | 56.0 Lb/Std Bu |
| Corn, Ear (15.5%) | 68.4 Lb/Std Bu |
| Cotton | 32.0 Lb/Std Bu |
| Cowpeas | 60.0 Lb/Std Bu |
| Flax | 60.0 Lb/Std Bu |
| Grass, Exc Timothy | 14.0 Lb/Std Bu |
| Grass, Timothy | 45.0 Lb/Std Bu |
| Lespedeza | 45.0 Lb/Std Bu |
| Millet | 80.0 Lb/Std Bu |
| Oats | 32.0 Lb/Std Bu |
| Rape | 60.0 Lb/Std Bu |
| Tye | 56.0 Lb/Std Bu |
| Sorghum, Forage | 50.0 Lb/Std Bu |
| Sorghum, grain (13.0%) | 56.0 Lb/Std Bu |
| Soybeans | 60.0 Lb/Std Bu |
| Sudan grass | 28.0 Lb/Std Bu |
| Sunflower, oil type | 28.0 Lb/Std Bu |
| Trefoil, Birdsfoot | 60.0 Lb/Std Bu |
| Vetch | 60.0 Lb/Std Bu |
| Wheat (13.5%) | 60.0 Lb/Std Bu |

BtuLb Evap	= 990 Btu per Lb of Water Evaporated; an engineering constant

Dryer EffStd 	= Electric grain dryer efficiency of a standard-efficiency electric bin dryer, expressed as a %, defined as Btu of moisture evaporated in the dryer divided by the heating Btu input into the dryer

=71%, a deemed value, based on the following table, which represents BTU/Lb evaporated and equivalent Overall Efficiency for the dryers and heating sources used in this TRM:

| Grain Dryer Description | Dryer Efficiency |  | Dryer Fan Power (Dryer Fan Power) |
| --- | --- | --- | --- |
|  | Dryer Eff | Btu/lb Water Evaporated (Btu/lb Water) | kW / Bushel |
| Baseline Gas Grain Dryer w/ Constant Speed Fan Operation | 44% | 2,241 | 0.044 |
| Efficient Gas Grain Dryer w/ Constant Speed Fan Operation | 61% | 1,625 | 0.044 |
| Efficient Gas Grain Dryer w/ Damper Fan Operation | 61% | 1,625 | 0.035 |
| Efficient Gas Grain Dryer w/ Fan VFD | 61% | 1,625 | 0.002 |
| Baseline Electric Bin Grain Dryer w/ Constant Speed Fan Operation | 71% | 1,400 | 0.44 |
| Efficient Electric Bin Grain Dryer w/ Constant Speed Fan Operation | 88% | 1,120 | 0.044 |
| Efficient Electric Bin Grain Dryer w/ Damper Fan Operation | 88% | 1,120 | 0.035 |
| Efficient Electric Bin Grain Dryer w/ Fan VFD | 88% | 1,120 | 0.002 |

Dryer EffEff  	= Actual or a deemed value based upon above table. If unknown assume 88%.  See prior footnote for derivation of this value.

3,412	= Conversion factor of kWh to Btu; engineering constant.

Dryer Fan PowerStd	= 0.044 kW/Bu, from above table, a deemed value, based on the following average standard bin dryer operational parameters, and the engineering equation:

kW/BuStd 	= CFM/BuStd *  in._wcStd  /  6,354 / Fan_EfficiencyStd  * 0.746  /  Motor EffStd

In the above equation, the following deemed constants are typical for standard-efficiency Grain Dryers:

Where:
CFM/BuStd 		= 61 CFM/Bu

in._wcStd	 	= 3.0” wc

6,354	 	=Units conversion from cfm * in. wc. / Fan_Efficiency to BHP

Fan_EffieciencyStd 	= 60%

0.746 		= Units conversion from BHP to kW

Motor EffcyStd 	= 80%.

kW/Bu = 61 * 3.0 / 6,354 / 60% * 0.746 / 80%
              = 0.044 kW/Bu

Dryer Fan PowerEff	= 0.035 kW/Bu, if fan volume is controlled using outlet damper, or

= 0.002 kW/Bu, if fan volume is controlled using VFD.

Above values are deemed constants, based on the following average high-efficiency bin dryer operational parameters, and the engineering equation:

kW/BuEff = CFM/BuEff *  in._wcEff  /  6,354 / Fan_EffieciencyEff  * 0.746  /  Motor_EffcyEff  /  Drive_EffcyEff

In the above equation, the following deemed constants are assumed to apply to high-efficiency Grain Dryers:

Where:
CFM/BuEff 		= 22

in._wcEff 		= 4.4” if Outlet Damper control; 0.4” if VFD control

6,354		=Units conversion from cfm * in. wc. / Fan_Efficiency to BHP

Fan_EfficiencyEff 	= 60%

0.746 		= Units conversion from BHP to kW

Motor EffEff 	= 80%

Drive EffEff 	= 100% if Outlet Damper control; 95% if VFD control.

For high-efficiency dryer with VFD control:

kW/Bu 	= 22  *  0.4  /  6,354 /  60% *  0.746  /  80%  /  95%
            	= 0.002 kW/Bu

For example, using the default assumptions on the installation of a 3,000 bushels/hr electric grain dryer with Outlet Damper used for Alfalfa:

###### ΔkWh  	= (3,000 * 336.3 * (0.23 - 0.15) 1-0.15(0.23 - 0.15) * 0.60 * 990 * (1/0.71 - 1/0.88)/3,412) + ((0.044 - 0.035) * 3,000 * 336.3)

= 458,865 kWh

###### Summer Coincident Peak Demand Savings

N/A

###### Fossil Fuel Savings

If grain dryer is heated exclusively with natural gas:

∆Therms = Bushels/HrCapacityCapacity * Annual_Hr_Use@Rated_CapacityHours * (Moisture_%In - Moisture_%Out1- Moisture_%OutMoisture_%In - Moisture_%Out) *  GrainLbGrain_Lb_Moisture_/_Bushel * Btu/LbLb EEvap * (1 / Dryer _EffcyStd -1/ Dryer _EffcyEff) / 100,000

Where:

100,000	= Conversion factor of Therms to Btu; engineering constant.

All variables are as defined and derived in the preceding electric savings calculations, but using values in the dryer efficiency table above for Baseline or Efficient "Gas or Propane Grain Dryer".

Note: When a variable frequency drive (VFD) is incorporated on the drying fan, electrical savings may be claimed by the fan power derivation in the electric savings algorithm for additive electrical savings for a gas heated grain dryer.

For example, using the default assumptions on the installation of a 3,000 bushels/hr gas grain dryer with Outlet Damper used for Alfalfa:

###### ΔTherms  	= 3,000 * 336.3 * ((0.23 - 0.15) / (1 – 0.15)) * 60 * 990 * (1/0.44 - 1/0.61)/100,000

= 35,725 Therms

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-AGE-GDRY-V03-260101

###### Review Deadline: 1/1/2030

### 4.4.30	Notched V Belts for HVAC Systems

###### Measure Description

This measure is for replacement of smooth v-belts in non-residential package and split HVAC systems with notched v-belts or for installing new equipment with synchronous belts instead of smooth v-belts.  Typically there is a v-belt between the motor and the supply air fan and/or return air fan in larger package and split HVAC systems (RTU).

In general there are two styles of grooved v-belts, notched and synchronous.  The DOE defines each as follows;

Notched V-Belts - A notched belt has grooves or notches that run perpendicular to the belt’s length, which reduces the bending resistance of the belt. Notched belts can use the same pulleys as cross-section standard V-belts. They run cooler, last longer, and are about 2% more efficient than standard V-belts.

Synchronous Belts - Synchronous belts (also called cogged, timing, positive-drive, or high-torque drive belts) are toothed and require the installation of mating grooved sprockets. These belts operate with a consistent efficiency of 98% and maintain their efficiency over a wide load range.

- Smooth v-belts are usually referred to in five basic groups:

- “L” belts are low end belts that are for small, fractional horsepower motors and these are not used in RTUs.

- “A” and “B” belts are the two types typically used in RTUs.  The “A” belt is a ½ inch width by 5/16 inch thickness and the “B” belt is larger, 21/32 inch wide and 12/32 inch thick so it can carry more power.  V-belts come in a wide variety of lengths where 20 to 100 inches is typical.

- “C” and “D” belts are primarily for industrial applications with high power transmission requirements.

- V-belts are provided by various vendors.  The notched version of these belts typically have an “X” added to the designation.  For this HVAC fans notched v-belt Replacement measure, only the “A” and “B” v-belts are considered.  A typical “A” v-belt is replaced by a notched “AX” v-belt and a “B” is replaced by a “BX.”  In general, smooth v-belts have an efficiency of 90% to 98% while notched v-belts have an efficiency of 95% to 98%.  Because notched v-belts are more flexible they work with smaller diameter pulleys and they have less resistance to bending.  Lower bending resistance increases the power transmission efficiency, lowers the waste heat, and allows the belt to last longer than a smooth belt.

Three research papers   show that the notched v-belt efficiency is 2% to 5% better than a typical smooth v-belt.  A fourth paper by USDOE’s Energy Efficiency and Renewable Energy  group reviewed most of the earlier literature and recommended using a conservative 2% efficiency improvement for energy savings for calculations.

For this measure it is assumed that upgrading a standard smooth v-belt with a new notched v-belt will result in a fan energy reduction of 2%.

###### Definition of Efficient Equipment

For the Notched V-Belt characterization to apply, the Efficient Equipment is HVAC RTUs that have notched v-belts installed on the supply and/or return air fans.  This can be done as a retrofit, TOS, or NC project.

For the Synchronous Belt characterization to apply, the Efficient Equipment is HVAC RTUs that have synchronous belts installed on the supply and/or return air fans. This can be done as a TOS or NC project. Retrofit projects can also claim savings, but costs should be verified independently (typically the cost of installing synchronous belts as a retrofit is not economically viable).

###### Definition of Baseline Equipment

The Baseline Equipment is HVAC RTUs that have smooth v-belts installed on the supply and/or return air fans (i.e., RTU does not already have a notched v-belt installed).

###### Deemed Lifetime of Efficient Equipment

A v-belt has a life based on fan run hours which varies by building type based primarily on occupancy schedule because the fans are required by code to operate continuously during occupied hours.  The supply and return fans will also run a few hours during unoccupied hours for heating and cooling as needed.  For the notched v-belt EUL calculation, the default hours in the following table are used for a variety of building types and HVAC applications.

EUL 	= Belt Life / Occupancy Hours per year

Where:

Belt Life 				= 24,000 hours

Occupancy Hours per year 	= values from Table below

The notched v-belt measure EUL is summarized by building type in the following table.

Notched v-belt Effective Useful Life (EUL)

| Building Type | Total Fan Run Hours | EUL (Years) | Model Source |
| --- | --- | --- | --- |
| Assembly | 7235 | 3.3 | eQuest |
| Assisted Living | 8760 | 2.7 | eQuest |
| Auto Dealership | 7451 | 3.2 | OpenStudio |
| College | 4836 | 5.0 | OpenStudio |
| Convenience Store | 7004 | 3.4 | eQuest |
| Drug Store | 7156 | 3.4 | OpenStudio |
| Elementary School | 3765 | 6.4 | OpenStudio |
| Emergency Services | 8760 | 2.7 | OpenStudio |
| Garage | 7357 | 3.3 | eQuest |
| Grocery | 8543 | 2.8 | OpenStudio |
| Healthcare Clinic | 4314 | 5.6 | OpenStudio |
| High School | 3460 | 6.9 | OpenStudio |
| Hospital - VAV econ | 4666 | 5.1 | OpenStudio |
| Hospital - CAV econ | 8021 | 3.0 | OpenStudio |
| Hospital - CAV no econ | 7924 | 3.0 | OpenStudio |
| Hospital - FCU | 4055 | 5.9 | OpenStudio |
| Manufacturing Facility | 8706 | 2.8 | eQuest |
| MF - High Rise | 8760 | 2.7 | OpenStudio |
| MF - Mid Rise | 8760 | 2.7 | OpenStudio |
| Hotel/Motel - Guest | 2409 | 10.0 | OpenStudio |
| Hotel/Motel - Common | 8683 | 2.8 | OpenStudio |
| Movie Theater | 7505 | 3.2 | eQuest |
| Office - High Rise - VAV econ | 2369 | 10.1 | OpenStudio |
| Office - High Rise - CAV econ | 2279 | 10.5 | OpenStudio |
| Office - High Rise - CAV no econ | 5303 | 4.5 | OpenStudio |
| Office - High Rise - FCU | 1648 | 14.6 | OpenStudio |
| Office - Low Rise | 6345 | 3.8 | OpenStudio |
| Office - Mid Rise | 3440 | 7.0 | OpenStudio |
| Religious Building | 7380 | 3.3 | eQuest |
| Restaurant | 7302 | 3.3 | OpenStudio |
| Retail - Department Store | 7155 | 3.4 | OpenStudio |
| Retail - Strip Mall | 6921 | 3.5 | OpenStudio |
| Warehouse | 6832 | 3.5 | OpenStudio |
| Unknown | 6241 | 3.8 | n/a |

The lifetime of a synchronous belt system is the same as the lifetime of the equipment it is installed on because it is a permanent upgrade, involving the installation of toothed pulleys. Typical HVAC RTU lifetime is 15 years, which applies to synchronous belts as well. This is not to suggest that the actual belt component has an equivalent lifetime because they do require replacement. However, their O&M cost savings (derived from not having to tension, etc.) are assumed to offset the replacement cost of the belt, resulting in a net cost of zero. As a result, neither a separate lifetime nor O&M savings are quantified for synchronous belts and lifetime can therefore be considered as the lifetime of the equipment they’re installed on because it would not be possible to install a traditional or notched belt on the synchronous pulleys.

###### Deemed Measure Cost

Costs of belts and pulleys are known to vary substantially based on belt length and pulley diameter. Two cost estimations are provided below; a fully deemed approach for applications such as an upstream program where limited information is known, and a semi-custom approach that is useful when more accurate cost estimates are desired.

Fully Deemed:

A review of the Grainger online pricing for “A,” “B,” “AX,” and “BX” v-belts revealed the incremental costs to upgrade to notched v-belts as summarized in the table below:

Notched V-belt Incremental Cost Summary

| Smooth V-Belt Industry Number | Outside Length (Inches) | Dayton Smooth V-Belt* | Notched V-belt Industry Number | Dayton Notched v-belt* | Price Increase | % Increase |
| --- | --- | --- | --- | --- | --- | --- |
| A30 (Item # 1A095) | 32 | $10.38 | AX30 (Item # 3GWU4) | $14.64 | $4.26 | 41% |
| B29 (Item # 6L208) | 32 | $14.38 | BX29 (Item # 5TXL4) | $20.80 | $6.42 | 45% |
| * Pricing based on Dayton Belts as found on Grainger Website 10/30/14 |  |  |  |  |  |  |

Note that the incremental cost for notched V-Belts assumes that the notched belt is purchased and installed instead of a smooth v-belt. There is no difference in the cost of installation, only the material.

Synchronous Belt Incremental Cost Summary

| Smooth V-Belt Industry Number | Smooth belt system Price* | Synchronous Belt Industry Number | Synchronous System Price* | Price Difference |
| --- | --- | --- | --- | --- |
| Belt A30 (Item # 1A095) | $10.38 | Belt 1DHL5 (Item # 322L050) | $15.37 | $4.99 |
| Gearbelt pulley BK47 (Item #5UHD5) | $47.98 | Gearbelt sprocket GTR-36G-8M-12 (Item # 2UWH6) | $113.91 | $65.93 |
| * Costs based on Grainger pricing. |  |  |  |  |

Incremental cost for a NC or TOS project is $136.85. This is the price of synchronous equipment (belt, two sprockets) subtract v-belt equipment (belt, two pulleys). Labor cost is assumed to be equal in the baseline and efficient cases.

Incremental cost for a RF project is $380.49. This is the price of synchronous equipment and labor to install it (not including a trip charge), less the cost of the v-belt (but not the pulleys).

Semi-Custom

Use the following relationships along with NC, TOS and RF assumptions outlined above to estimate semi-custom costs.

| Component | Type | Cost Function (per inch) | Inch Measurement |
| --- | --- | --- | --- |
| Standard V-Belt | A | $0.28/in + $0.96 | Outside Length |
| Standard V-Belt | B | $0.29/in + $9.15 | Outside Length |
| Standard Pulley | A, B, AX, BX | $11.85/in - $9.47 | Outside Diameter |
| Notched Belt | AX | $0.36/in + $1.07 | Outside Length |
| Notched Belt | BX | $0.49/in + $2.33 | Outside Length |
| Synchronous Belt | 1/2 inch | $0.58/in + $8.90 | Pitch Length |
| Synchronous Belt | 1 inch | $0.26/in + $5.67 | Pitch Length |
| Synchronous Pulley | for use with 1/2 inch belt | $27.20/in - $21.19 | Pitch Diameter |
| Synchronous Pulley | for use with 1 inch belt | $25.04/in - $27.23 | Pitch Diameter |

###### Deemed O&M Cost Adjustments

N/A

###### Loadshape

Loadshape C05 - Commercial Electric Heating and Cooling

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh  = kWconnected* Hours * ESF

Where:

kWConnected 	=kW of equipment is calculated using motor efficiency

= (HP * 0.746 kW/HP* Load Factor)/Motor Efficiency

Load Factor 	=Motors are assumed to have a load factor of 80% for calculating KW if actual values cannot be determined.  Custom load factor may be applied if known.

Motor Efficiency 	= Actual motor efficiency shall be used to calculate KW.  If not known a value from the motor efficiency refrence tables below should be used.  Default motor is a NEMA Premium Efficiency, ODP, 4-pole/1800 RPM fan motor.

| Baseline Motor Efficiencies (EPACT) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
|  | # of Poles |  |  |  |  |  |
|  | 6 | 4 | 2 | 6 | 4 | 2 |
|  | Speed (RPM) |  |  |  |  |  |
|  | 1200 | 1800 | 3600 | 1200 | 1800 | 3600 |
| 1/8 | - | 44.00% | - | - | - | - |
| 1/6 | 57.50% | 62.00% | - | - | - | - |
| 1/4 | 68.00% | 68.00% | - | 68.00% | 64.00% | - |
| 1/3 | 70.00% | 70.00% | 72.00% | 70.00% | 68.00% | 72.00% |
| 1/2 | 78.50% | 80.00% | 68.00% | 72.00% | 74.00% | 68.00% |
| 3/4 | 77.00% | 78.50% | 74.00% | 77.00% | 75.50% | 74.00% |
| 1 | 80.00% | 82.50% | 75.50% | 80.00% | 82.50% | 75.50% |
| 1.5 | 84.00% | 84.00% | 82.50% | 85.50% | 84.00% | 82.50% |
| 2 | 85.50% | 84.00% | 84.00% | 86.50% | 84.00% | 84.00% |
| 3 | 86.50% | 86.50% | 84.00% | 87.50% | 87.50% | 85.50% |
| 5 | 87.50% | 87.50% | 85.50% | 87.50% | 87.50% | 87.50% |
| 7.5 | 88.50% | 88.50% | 87.50% | 89.50% | 89.50% | 88.50% |
| 10 | 90.20% | 89.50% | 88.50% | 89.50% | 89.50% | 89.50% |
| 15 | 90.20% | 91.00% | 89.50% | 90.20% | 91.00% | 90.20% |
| 20 | 91.00% | 91.00% | 90.20% | 90.20% | 91.00% | 90.20% |
| 25 | 91.70% | 91.70% | 91.00% | 91.70% | 92.40% | 91.00% |

| Efficient Motor Efficiencies (NEMA Premium) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Size HP | Open Drip Proof (ODP) |  |  | Totally Enclosed Fan-Cooled (TEFC) |  |  |
|  | # of Poles |  |  | # of Poles |  |  |
|  | 2 | 4 | 6 | 2 | 4 | 6 |
|  | Speed (RPM) |  |  | Speed (RPM) |  |  |
|  | 1200 | 1800 (Default) | 3600 | 1200 | 1800 | 3600 |
| 0.125 * | - | 44.00% | - | - | - | - |
| 1/6 | 57.50% | 62.00% | - | - | - | - |
| 1/4 | 68.00% | 68.00% | - | 68.00% | 64.00% | - |
| 1/3 | 70.00% | 70.00% | 72.00% | 70.00% | 68.00% | 72.00% |
| 1/2 | 78.50% | 80.00% | 68.00% | 72.00% | 74.00% | 68.00% |
| 3/4 | 77.00% | 78.50% | 74.00% | 77.00% | 75.50% | 74.00% |
| 1 | 82.50% | 85.50% | 77.00% | 82.50% | 85.50% | 77.00% |
| 1.5 | 86.50% | 86.50% | 84.00% | 87.50% | 86.50% | 84.00% |
| 2 | 87.50% | 86.50% | 85.50% | 88.50% | 86.50% | 85.50% |
| 3 | 88.50% | 89.50% | 85.50% | 89.50% | 89.50% | 86.50% |
| 5 | 89.50% | 89.50% | 86.50% | 89.50% | 89.50% | 88.50% |
| 7.5 | 90.20% | 91.00% | 88.50% | 91.00% | 91.70% | 89.50% |
| 10 | 91.70% | 91.70% | 89.50% | 91.00% | 91.70% | 90.20% |
| 15 | 91.70% | 93.00% | 90.20% | 91.70% | 92.40% | 91.00% |
| 20 | 92.40% | 93.00% | 91.00% | 91.70% | 93.00% | 91.00% |
| 25 | 93.00% | 93.60% | 91.70% | 93.00% | 93.60% | 91.70% |

Hours 	= When available, actual hours should be used. If actual hours are not available, default hours are provided in table below for HVAC fan operation, which varies by building type:

| Building Type | Total Fan Run Hours | Model Source |
| --- | --- | --- |
| Assembly | 7235 | eQuest |
| Assisted Living | 8760 | eQuest |
| Auto Dealership | 7451 | OpenStudio |
| College | 4836 | OpenStudio |
| Convenience Store | 7004 | eQuest |
| Drug Store | 7156 | OpenStudio |
| Elementary School | 3765 | OpenStudio |
| Emergency Services | 8760 | OpenStudio |
| Garage | 7357 | eQuest |
| Grocery | 8543 | OpenStudio |
| Healthcare Clinic | 4314 | OpenStudio |
| High School | 3460 | OpenStudio |
| Hospital - VAV econ | 4666 | OpenStudio |
| Hospital - CAV econ | 8021 | OpenStudio |
| Hospital - CAV no econ | 7924 | OpenStudio |
| Hospital - FCU | 4055 | OpenStudio |
| Manufacturing Facility | 8706 | eQuest |
| MF - High Rise | 8760 | OpenStudio |
| MF - Mid Rise | 8760 | OpenStudio |
| Hotel/Motel - Guest | 2409 | OpenStudio |
| Hotel/Motel - Common | 8683 | OpenStudio |
| Movie Theater | 7505 | eQuest |
| Office - High Rise - VAV econ | 2369 | OpenStudio |
| Office - High Rise - CAV econ | 2279 | OpenStudio |
| Office - High Rise - CAV no econ | 5303 | OpenStudio |
| Office - High Rise - FCU | 1648 | OpenStudio |
| Office - Low Rise | 6345 | OpenStudio |
| Office - Mid Rise | 3440 | OpenStudio |
| Religious Building | 7380 | eQuest |
| Restaurant | 7302 | OpenStudio |
| Retail - Department Store | 7155 | OpenStudio |
| Retail - Strip Mall | 6921 | OpenStudio |
| Warehouse | 6832 | OpenStudio |
| Unknown | 6241 | n/a |

ESF 		= Energy Savings Factor, the ESF for notched v-belt Installation is assumed to be 2%

= the ESF for notched Synchronous Belt Installation is assumed to be 3.1%

For example, a notched v-belt installation in an low rise office building RTU with a 5 HP NEMA premium efficiency motor using the default hours of operation, motor load and 89.5% motor efficiency;

ΔkWh	= kWconnected* Hours * ESF

= ((HP * 0.746 kW/HP* Load Factor)/Motor Efficiency) * Hours * ESF

= ((5 HP * 0.746 kW/HP* 80%) / 89.5%) * 6345 * 2%

= 423.1 kWh Savings

Summer Coincident Peak Demand Savings

ΔkW  = kWconnected* ESF * CF

Where:

kWConnected  	= kW of equipment is calculated using motor efficiency.

= (HP *0 .746 kW/HP* Load Factor)/Motor Efficiency

CFSSP  	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM 	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Variables as provided above

For example, an office building RTU with a 5 HP NEMA premium efficiency motor using the default motor load and 89.5% motor efficiency;

ΔkWSSP	= kWconnected* ESF * CF

= ((HP * 0.746 kW/HP* Load Factor)/Motor Efficiency) * ESF * CF

= ((5 HP * 0.746 kW/HP* 80%) / 89.5%) * 2% * 0.913

= 0.0609 kW Savings

###### Fossil Fuel Savings

N/A

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-HVC-NVBE-V07-260101

###### Review Deadline: 1/1/2027

### 4.4.62	Cooling Tower Water Side Economizer

###### Description

A waterside economizer works by running the cooling tower loop in the winter and parts of the shoulder seasons as a source of cooling and transferring cooling energy to the building (secondary) cooling loop. This requires a dedicated plate-and-frame heat exchanger that is used only during waterside economizer operations, during which time the chillers are locked out.

A waterside economizer may contribute to reduced energy use in the following ways:

- Reducing the mechanical cooling load on chillers by pre-cooling return water

- Reducing energy use of the plant by allowing chillers to turn off at times of free cooling

Energy consumption (kWh) may decrease with the use of a waterside economizer because the leaving chilled water temperature can be reduced based on the wet bulb temperature. With this control strategy, the effect will be a reduction in motor speed (rpms) of the compressor as well as the pre-cooling of the chilled water return through the waterside economizer. Water side economizers must be sized to provide 100% of the cooling demand at 50 degrees (F) dry-bulb and 45 degrees (F) wet-bulb and below.

###### Definition of Efficient Equipment

Installation of integrated waterside economizer heat exchanger to existing chilled-water system with cooling tower. Heat exchanger approach may range from 1° to 6°. Weather data is used to identify the annual hours in which outdoor air conditions are sufficient to provide water at a desirable temperature. Typically, demand savings may not be present with this measure because the process systems require water temperatures around 55-65°F and a cooling tower cannot meet these temperatures during the peak period.

###### Definition of Baseline Equipment

No waterside heat exchanger installed or functional.

###### Deemed Lifetime of Efficient Equipment

The expected lifetime of the measure is 10 years

###### Deemed Measure Cost

Use actual chiller manufacturer provided cost.

###### Loadshape

Loadshape C03 - Commercial Cooling

###### Coincidence Factor

CFSSP	= Summer System Peak Coincidence Factor for Commercial cooling (during system peak hour)

= 91.3%

CFPJM	= PJM Summer Peak Coincidence Factor for Commercial cooling (average during peak period)

= 47.8%

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

ΔkWh = (TONS*LFwinter) * IPLVbase * (Hr)Free

Where:

TONS 	= chiller nominal cooling capacity in tons (note: 1 ton = 12,000 Btu/hr)

= Actual installed

LFwinter                    = Average winter cooling load, expressed as percentage of peak system capacity (tons)

= If unknown, assume 25%

IPLVbase	= efficiency of baseline equipment expressed as Integrated Part Load Value (kW/ton). Chiller units are dependent on chiller type. See Chiller Units, Conversion Values and Baseline Efficiency Values by Chiller Type and Capacity in the Reference Tables section.

= Actual installed

(Hr)Free	= Annual hours in which outdoor air conditions are sufficient to provide condenser water at a desirable temperature that the chiller does not need to operate.

= If unknown, use default values from table below:

| Climate Zone | Hours |
| --- | --- |
| Zone 1 (Rockford) | 4334 |
| Zone 2 (Chicago) | 4253 |
| Zone3 (Springfield) | 3760 |
| Zone 4 (Belleville) | 3536 |
| Zone 5 (Marion) | 3432 |

###### Summer Coincident Peak Demand Savings

N/A

###### Fossil Fuel Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

There are no expected O&M costs or savings associated with this measure.

###### Measure Code: CI-HVC-CTWE-V03-260101

###### Review Deadline: 1/1/2030

### 4.6.13	Add Doors to Open Refrigerated Display Cases

###### Description

Open display cases are typically found in grocery and convenience stores and have been a preference of store owners because they allow customers a clear view and easy access to refrigerated products. This measure is retrofitting existing, open, refrigerated display cases by adding and installing doors. The baseline equipment is an open vertical or horizontal display case with no doors or covering. The efficient equipment is the installation of solid doors on the existing display case. Replacement of open display cases with new display cases with doors is not covered under this measure characterization.

Energy savings are based on air infiltration reduction from the addition of doors to the open display cases. The air infiltration reductions assume a reduced heat gain and subsequent reduced load on the refrigeration compressors. Both radiant and conduction heat losses were factored into the analysis as well. Energy savings are based on a per linear foot of display case.

Interactive HVAC energy savings were also included in the measure savings analysis. The HVAC interactive effects calculation assesses the measure's impact on the heating and cooling equipment. With adding a door to an open refrigerated display case, excess cold air leaking into the conditioned space no longer must be treated by the heating system, resulting in additive savings. Similarly, the reduction in cold air from the open refrigerated display case no longer supplements the efforts of the space cooling equipment, which results in an overall increase in its consumption.

High, medium, and low temperature cases are eligible for this measure; however, the measure assumptions detailed in this characterization are based on medium temperature display cases, with the installation of zero energy doors, as it was deemed the most likely candidate for participation in this measure. Open low temperature or freezer display cases are not common. If the retrofitted door has LED fixtures, it is recommended to leverage ‘4.5.4 LED Bulbs and Fixtures for quantifying savings and measure benefits.

This measure was developed to be applicable to the following program types: RF.

If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

The efficient condition is retrofitting an existing open, refrigerated, display case by adding doors.

###### Definition of Baseline Equipment

The baseline condition is an open, refrigerated, display case without any covering.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is 15 years.

###### Deemed Measure Cost

The incremental cost, which includes both material and labor, differs depending on whether or not the installed door is equipped with LED lighting. The estimated incremental cost for doors without LED lighting is $390 per linear foot. The incremental cost for doors with LED lighting is $419 per linear foot.

###### Loadshape

Loadshape C03 - Commercial Cooling

Loadshape 22: Commercial Refrigeration

###### Coincidence Factor

There are two components to the demand savings of this measure, one that impacts the refrigeration equipment itself, and another that has an interactive impact on the space cooling equipment. As a result, the measure details two summer coincidence peak demand factors.

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

∆kWh=(ΔHG*CL/ (EER*W/kW1000) *8760)+(MMBtuHVAC Cool * kBtu/MMBtu*CL *(1 / SEER2) *1000)- ((kWhNight Covers - kWhAdded Lights ) ∗ CL)

Where:

∆kWh		= gross customer annual kWh savings

∆HG	= Heat Gain, the decreased load or the reduced heat gain on the open refrigerated display case with the installation of a door (Btu/hr-linear foot)

= 1,172 Btu/h-ft for vertical cases or 202.3 Btu/h-ft for horizontal cases.

CL		= Case Length, refrigerated case length in feet

= Actual

EER		= Energy Efficiency Ratio; display case compressor efficiency (Btu/hr-watt)

= 11.36

W/kW		= Conversion from watts to kilowatts (W / kW)

= 1,000

8760		= Annual operating hours of the refrigerated display case

MMBtuHVAC Cool	= Total cooling load increase on the HVAC equipment per linear foot of display case. Varies by location:

| Zone | MMBtuHVAC Cool Vertical | MMBtuHVAC Cool Horizontal |
| --- | --- | --- |
| 1 (Rockford) | -2.632 | -0.454 |
| 2 (Chicago) | -2.763 | -0.477 |
| 3 (Springfield) | -3.284 | -0.567 |
| 4 (Belleville) | -3.254 | -0.562 |
| 5 (Marion) | -3.335 | -0.576 |

kBtu/MMBtu	= Conversion from MMBtu to kBtu (kBtu/MMBtu)

= 1,000

SEER2	= Seasonal Energy Efficiency Ratio; HVAC equipment operating efficiency (kBtu/kWh) * Distribution Efficiency

= Actual, if unknown assume 11.1 SEER2.

kWhNight Covers	= Reduction in energy savings if existing display case utilizes night covers (kWh/linear-ft)

= 0 if no night covers are deployed. See table below if display case uses night covers.

| Display Case Description | Case Temperature Range (°F) | ∆kWh/ft reduction (= 9% reduction of electricity use,) |
| --- | --- | --- |
| Vertical Open, Remote Condensing, Medium Temperature | 35°F to 55°F | 131 |
| Vertical Open, Remote Condensing, Low Temperature | 0°F to 30°F | 296 |
| Vertical Open, Self-Contained Medium Temperature | 35°F to 55°F | 252 |

kWhAdded Lights	= Reduction in energy savings if new lighting is added to the case (kWh/linear-ft)

= 0 if no lighting is added, or if lighting is added but existing lighting is removed. If lighting is retrofit, determine case lighting savings using ‘4.5.4 LED Bulbs and Fixtures’.

= Actual installed equipment specifications or use case lighting values from ‘4.5.4 LED Bulbs and Fixtures'.

For example, a grocery store in Chicago installed zero energy doors on four open refrigerated cases that do not use night covers, which amounted to 12 linear feet of retrofitted display cases, savings the site:

ΔkWh 	= ((1172 * 12) / (11.36 * 1000) * 8760) + (-2.763 * 1000 * 12 * (1 / 11.1))

= 7858 kWh

###### Summer Coincident Peak Demand Savings

∆kW=((ΔHG*CL / (EER*1000W/kW)-(kWAdded Lights * CL)*CFRefrigeration)+((MMBtuHVAC Cool * kBtu/MMBtu)/ HoursCool *CL *(1 / SEER2) *1000)*CFCool)

Where:

HoursCool 	= Total combined hours the site is providing cooling. Varies by location:

| Zone | Hours Cool |
| --- | --- |
| 1 (Rockford) | 2,994 |
| 2 (Chicago) | 3,143 |
| 3 (Springfield) | 3,736 |
| 4 (Belleville) | 3,702 |
| 5 (Marion) | 3,794 |

kWAdded Lights	= Reduction in demand savings if new lighting is added to the case (kW/linear-ft)

= 0 if no lighting is added, or if lighting is added but existing lighting is removed. If lighting is retrofit, determine case lighting savings using ‘4.5.4 LED Bulbs and Fixtures’.

= Actual installed equipment specifications or use case lighting values from ‘4.5.4 LED Bulbs and Fixtures'.

CFRefrigeration	= Summer peak coincidence factor for the refrigerated display case

= 0.964

CFCool	= Summer peak coincidence factor for the HVAC cooling system. This is the summer system peak coincidence factor for commercial dooling (during system peak hours)

= 0.913

###### Fossil Fuel Savings

ΔTherms= (MMBtuHVAC Heat*CL*(1 / AFUE) *10

Where:

∆Therms	= gross customer annual therms savings

MMBtuHVAC Heat	= Total heating load decrease on the HVAC equipment per linear foot of display case. Varies by locations:

| Zone | MMBtuHVAC Heat Vertical | MMBtuHVAC Heat Horizontal |
| --- | --- | --- |
| 1 (Rockford) | 5.068 | 0.875 |
| 2 (Chicago) | 4.937 | 0.852 |
| 3 (Springfield) | 4.416 | 0.762 |
| 4 (Belleville) | 4.446 | 0.767 |
| 5 (Marion) | 4.365 | 0.753 |

CL		= Case Length, refrigerated case length in feet

= Actual

AFUE		= Efficiency of heating system, including distribution losses.

Actual, if unknown assume 0.821.

10		= Conversion from MMBtu to therms

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-RFG-DOOR-V04-260101

###### Review Deadline: 1/1/2028

### 4.8.2 Spring-Loaded Garage Door Hinge

###### Description

Existing overhead doors often close loosely at the perimeter weather strips and between panels. Conditioned air escapes through these gaps, leading to energy loss. Spring-loaded hinges create tension and reduce gaps at the perimeter and between panels. The product is applicable for small-commercial and residential sectors, but the savings estimated by this measure apply only to small-commercial applications. This measure applies to sites where the inside area of the garage is conditioned during the heating season by natural gas.

This measure was developed to be applicable to the following program types: NC, RF.  If applied to other program types, the measure savings should be verified as a custom measure.

###### Definition of Efficient Equipment

The efficient equipment consists of a heavy-duty spring-loaded hinge installed in place of a standard hinge on a garage overhead door. The number of hinges per project may vary depending on the door type, size, and number of panels. The efficient condition is an air sealed garage door with no gaps around the perimeter or between panels.

###### Definition of Baseline Equipment

The baseline equipment is a garage door with a 1/8-inch gap between the door and the weather-stripping around the perimeter of the door. The bottom of the door is assumed sealed.

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 20 years.

###### Deemed Measure Cost

Incremental costs equal installed cost and will vary based on the number of hinges required per door. Based on information provided by the manufacturer to Nicor Gas, average material cost is $126 per garage door and installation cost is $63 per garage door for a total installed cost of $189 per garage door. The typical garage door is assumed to have 4 panels and 9 total hinges.

###### Loadshape

Loadshape C04 - Commercial Electric Heating

###### Coincidence Factor

Savings relate to heating only so coincidence factor is assumed to be 0.

Algorithm

###### Calculation of Energy Savings

Savings are calculated based on a reduction in airflow rate associated with decreased infiltration across the leakage area. The algorithm below for change in cubic feet per minute, ∆CFM, is modeled after equation 48 in Chapter 16: Ventilation and infiltration of the 2017 ASHRAE Handbook—Fundamentals.

###### Electric Energy and Fossil Fuel Savings

∆kWh= ∆HeatLoad/COPheat/ConvkWh * EFLHH

∆Therms= ∆HeatLoad/Effheat/ConvBTU* EFLHH

∆HeatLoad= ∆CFM*Convmin* Densityair*SpecificHeatair*∆T

∆CFM= Al*Cs*∆T+Cw*Ws20.5

Where:

Al 	= Leakage area, estimated at 51 (in2), of air gap before retrofit.

Cs 	= Stack coefficient, 0.0299 (cfm2/in4*°F), adjustment based on airflow at average building height.

Cw 	= Wind coefficient, 0.0086 (cfm2/in4*mph2), adjustment based on airflow at average building height and wind shelter classification.

∆T 	= Average temperature difference between outside air temperature (OAT) during the heating season  and assumed indoor heating temperature setpoint 70°F; see table below.

Ws 	= Average wind speed (mph) during heating season, see table below.

| Climate Zone | Average OAT, Heating (°F) | Average Delta T, Heating (°F) | Average heating Season Wind Speed (mph) |
| --- | --- | --- | --- |
| 1 (Rockford) | 32 | 38 | 10 |
| 2 (Chicago) | 34 | 36 | 10 |
| 3 (Springfield) | 35 | 35 | 10 |
| 4 (Belleville) | 36 | 34 | 9 |
| 5 (Marion) | 39 | 31 | 7 |

Convmin 	= Conversion from minutes to hours, 60 minutes/hour.

Densityair	= The density of air, 0.08 (lb/ft3) at 1 atmosphere pressure and approximately 30-40°F.

SpecificHeatair	= Specific heat of air, 0.24 (BTU/lb) at 1 atmosphere pressure and 32°F.

COPheat 		= COP of electric heating system

= If heat pump, assume 2.5 for New Construction and 2.05 for existing buildings

= 1.0 if electric resistance heating

Effheat		= Efficiency of the heating system, assume 0.82 for planning purposes.

ConvkWh		= Conversion from BTUs to kWh

= 3,412 BTU/kWh

ConvTherms 	= Conversion from BTUs to therms

= 100,000 BTU/therm.

EFLHH 	=Equivalent Full Load Heating Hours in Existing Buildings or New Construction are listed in section 4.4 HVAC End Use.

Savings for all climate zones and selected building types are presented in the following tables:

| Annual kWh Savings Existing Buildings, Heat Pump |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 667.9 | 575.6 | 492.8 | 325.6 | 294.2 |
| Garage | 444.2 | 407.7 | 345.8 | 254.2 | 227.4 |
| High School | 814.9 | 780.6 | 669.4 | 594.7 | 490.4 |
| Manufacturing | 472.6 | 426.3 | 381.2 | 211.9 | 191.7 |
| Office - Low Rise | 1274.0 | 1104.6 | 960.0 | 750.2 | 616.8 |
| Retail - Strip Mall | 607.5 | 557.5 | 480.2 | 397.7 | 331.4 |
| Warehouse | 579.5 | 541.1 | 479.0 | 428.8 | 370.1 |

| Annual kWh Savings Existing Buildings, Electric Resistance |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 1369.2 | 1180.0 | 1010.2 | 667.4 | 603.1 |
| Garage | 910.6 | 835.9 | 709.0 | 521.1 | 466.1 |
| High School | 1670.5 | 1600.1 | 1372.2 | 1219.2 | 1005.4 |
| Manufacturing | 968.9 | 873.8 | 781.4 | 434.5 | 393.0 |
| Office - Low Rise | 2611.7 | 2264.3 | 1968.0 | 1538.0 | 1264.4 |
| Retail - Strip Mall | 1245.3 | 1143.0 | 984.4 | 815.3 | 679.3 |
| Warehouse | 1188.0 | 1109.3 | 981.9 | 878.9 | 758.7 |

| Annual kWh Savings New Construction, Heat Pump |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Grocery | 1033.6 | 962.0 | 848.5 | 729.5 | 643.9 |
| High School | 555.4 | 534.5 | 455.4 | 393.3 | 322.1 |
| Office - Low Rise | 352.8 | 316.1 | 274.9 | 204.4 | 164.6 |
| Retail - Strip Mall | 359.8 | 299.2 | 323.5 | 262.7 | 192.6 |
| Warehouse | 522.5 | 479.6 | 465.3 | 397.9 | 319.8 |

| Annual kWh Savings New Construction, Electric Resistance |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Grocery | 2583.9 | 2405.0 | 2121.1 | 1823.8 | 1609.7 |
| High School | 1388.6 | 1336.2 | 1138.4 | 983.2 | 805.2 |
| Office - Low Rise | 882.0 | 790.1 | 687.4 | 511.1 | 411.6 |
| Retail - Strip Mall | 899.5 | 747.9 | 808.8 | 656.7 | 481.6 |
| Warehouse | 1306.3 | 1199.0 | 1163.3 | 994.7 | 799.6 |

| Annual Therm Savings Existing Buildings |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 57.0 | 49.1 | 42.0 | 27.8 | 25.1 |
| Garage | 37.9 | 34.8 | 29.5 | 21.7 | 19.4 |
| High School | 69.5 | 66.6 | 57.1 | 50.7 | 41.8 |
| Manufacturing | 40.3 | 36.4 | 32.5 | 18.1 | 16.4 |
| Office - Low Rise | 108.7 | 94.2 | 81.9 | 64.0 | 52.6 |
| Retail - Strip Mall | 51.8 | 47.6 | 41.0 | 33.9 | 28.3 |
| Warehouse | 49.4 | 46.2 | 40.9 | 36.6 | 31.6 |

| Annual Therm Savings New Construction |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Grocery | 107.5 | 100.1 | 88.3 | 75.9 | 67.0 |
| High School | 57.8 | 55.6 | 47.4 | 40.9 | 33.5 |
| Office - Low Rise | 36.7 | 32.9 | 28.6 | 21.3 | 17.1 |
| Retail - Strip Mall | 37.4 | 31.1 | 33.7 | 27.3 | 20.0 |
| Warehouse | 54.4 | 49.9 | 48.4 | 41.4 | 33.3 |

Savings for all climate zones and selected building types per linear foot (dividing by 34 linear ft) are presented in the following tables:

| Annual kWh Savings per Linear Foot Existing Buildings, Heat Pump |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 19.6 | 16.9 | 14.5 | 9.6 | 8.7 |
| Garage | 13.1 | 12.0 | 10.2 | 7.5 | 6.7 |
| High School | 24.0 | 23.0 | 19.7 | 17.5 | 14.4 |
| Manufacturing | 13.9 | 12.5 | 11.2 | 6.2 | 5.6 |
| Office - Low Rise | 37.5 | 32.5 | 28.2 | 22.1 | 18.1 |
| Retail - Strip Mall | 17.9 | 16.4 | 14.1 | 11.7 | 9.7 |
| Warehouse | 17.0 | 15.9 | 14.1 | 12.6 | 10.9 |

| Annual kWh Savings per Linear Foot Existing Buildings, Electric Resistance |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 40.3 | 34.7 | 29.7 | 19.6 | 17.7 |
| Garage | 26.8 | 24.6 | 20.9 | 15.3 | 13.7 |
| High School | 49.1 | 47.1 | 40.4 | 35.9 | 29.6 |
| Manufacturing | 28.5 | 25.7 | 23.0 | 12.8 | 11.6 |
| Office - Low Rise | 76.8 | 66.6 | 57.9 | 45.2 | 37.2 |
| Retail - Strip Mall | 36.6 | 33.6 | 29.0 | 24.0 | 20.0 |
| Warehouse | 34.9 | 32.6 | 28.9 | 25.9 | 22.3 |

| Annual kWh Savings per Linear Foot New Construction, Heat Pump |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Grocery | 30.4 | 28.3 | 25.0 | 21.5 | 18.9 |
| High School | 16.3 | 15.7 | 13.4 | 11.6 | 9.5 |
| Office - Low Rise | 10.4 | 9.3 | 8.1 | 6.0 | 4.8 |
| Retail - Strip Mall | 10.6 | 8.8 | 9.5 | 7.7 | 5.7 |
| Warehouse | 15.4 | 14.1 | 13.7 | 11.7 | 9.4 |

| Annual kWh Savings per Linear Foot New Construction, Electric Resistance |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Grocery | 76.0 | 70.7 | 62.4 | 53.6 | 47.3 |
| High School | 40.8 | 39.3 | 33.5 | 28.9 | 23.7 |
| Office - Low Rise | 25.9 | 23.2 | 20.2 | 15.0 | 12.1 |
| Retail - Strip Mall | 26.5 | 22.0 | 23.8 | 19.3 | 14.2 |
| Warehouse | 38.4 | 35.3 | 34.2 | 29.3 | 23.5 |

| Annual Therm Savings per Linear Foot Existing Buildings |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Convenience Store | 1.68 | 1.44 | 1.24 | 0.82 | 0.74 |
| Garage | 1.11 | 1.02 | 0.87 | 0.64 | 0.57 |
| High School | 2.04 | 1.96 | 1.68 | 1.49 | 1.23 |
| Manufacturing | 1.19 | 1.07 | 0.96 | 0.53 | 0.48 |
| Office - Low Rise | 3.20 | 2.77 | 2.41 | 1.88 | 1.55 |
| Retail - Strip Mall | 1.52 | 1.40 | 1.20 | 1.00 | 0.83 |
| Warehouse | 1.45 | 1.36 | 1.20 | 1.08 | 0.93 |

| Annual Therm Savings per Linear Foot New Construction |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Type | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |
| Grocery | 3.16 | 2.94 | 2.60 | 2.23 | 1.97 |
| High School | 1.70 | 1.64 | 1.39 | 1.20 | 0.99 |
| Office - Low Rise | 1.08 | 0.97 | 0.84 | 0.63 | 0.50 |
| Retail - Strip Mall | 1.10 | 0.92 | 0.99 | 0.80 | 0.59 |
| Warehouse | 1.60 | 1.47 | 1.42 | 1.22 | 0.98 |

###### Summer Coincident Peak Demand Savings

N/A, electric savings is for space heating that only occurs during the winter.

###### Fossil Fuel Savings

Calculation provided together with Electric Energy Savings above.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: CI-SHL-SLDH-V03-260101

###### Review Deadline: 1/1/2030

### 4.9.10	Efficient Thermal Oxidizers

###### Description

Thermal oxidizers are used to destroy volatile organic compounds (VOCs) from process exhausts, before emitting the treated air to the environment. VOC emissions are precursors to the formation of ground-level ozone pollution, and its control is mandated by the U.S. EPA. Some VOC constituents are individually toxic and require efficient destruction. Some waste streams have high enough concentrations to present an explosion hazard. Other waste streams merely present nuisance odors that need to be mitigated.

A facility may be required to utilize a thermal oxidizer by a state regulatory agency air quality permit. Some permits may require a VOC destruction efficiency that must be demonstrated with periodic emissions testing. Other permits merely require maintaining an oxidizer chamber temperature. A facility may also choose to utilize a thermal oxidizer for other purposes (nuisance odors) without a regulatory requirement.

The Efficient Thermal Oxidizer measure seeks to evaluate fossil fuel savings from utilizing more efficient means for VOC destruction with the use of a recuperative or regenerative thermal oxidizer. The heat recovery (either recuperative or regenerative) is used to pre-heat the inlet process air stream. This primary heat recovery is used within the thermal oxidizer process and the only heat recovery that is covered in this measure protocol. Fossil fuel savings will result from reduced burner firing. There is a “secondary” form of heat recovery that recovers heat from the combustion exhaust stack for other purposes like space heating, DHW heating, etc.

###### Definition of Efficient Equipment

Two thermal oxidizer technologies can be considered as efficient equipment: recuperative and regenerative.

Recuperative Thermal Oxidizer

In a recuperative thermal oxidizer, the exhaust air stream is sent through a heat exchanger to indirectly pre-heat the inlet air stream coming from the process. The heat exchanger efficiency for a recuperator is typically 50-70%. The chamber temperature is typically 1,400°F to 1,500°F.

Regenerative Thermal Oxidizer

A regenerative thermal oxidizer utilizes a two-chamber ceramic bed as its heat exchanger system. The exhaust air passes through one bed, imparting its heat onto the ceramic media, while the intake air passes through the other bed, capturing the waste heat from the previous cycle. The flow reverses every few minutes so that the intake bed becomes the exhausted bed and vice versa. The heat exchanger efficiency of a regenerative system is much higher than a recuperative system. These efficiencies can reach 85% to 97%. However, the ceramic media needs to be periodically cleaned or replaced. The chamber temperatures in regenerative thermal oxidizers are typically 1,500°F to 1,600°F (depending on VOC requirements).

###### Definition of Baseline Equipment

Depending on the facility process, there may be two baseline selection options: incinerator or recuperator.

The baseline thermal oxidizer with no heat recovery is referred to as an incinerator. This baseline is recommended for selection if it currently exists on site or in new construction when there is a specific process that cannot practically utilize a recuperator due to VOCs coating or clogging the heat exchanger.  This system employs a burner to provide direct fire to a process exhaust air stream. Typical operative temperatures are 1,400°F to 2,200°F. The advantage of an afterburner is a quick startup and shutdown time that is ready on demand. The equipment cost is lower than the efficient equipment, but the fuel consumption is much higher.

In all other cases (existing equipment is recuperative or new construction/ expansion of manufacturing process), a recuperative thermal oxidizer is recommended as the appropriate baseline.

###### Deemed Lifetime of Efficient Equipment

The expected useful life of any thermal oxidizer system is assumed to 20 years.

###### Deemed Measure Cost

The cost of any thermal oxidizer is dependent on various variables such as air flow capacity, destruction efficiency, heat exchanger efficiency, etc. Shown below is an example of a system for 20,000 cfm.

Recuperative thermal oxidizer costs, based on their heat recovery efficiency, are detailed in the table below.

| Heat Recovery Efficiency | Equipment Cost |
| --- | --- |
| 0% | $106,042 |
| 35% | $174,193 |
| 50% | $203,801 |
| 70% | $253,801 |
| Average | $184,317 |

A regenerative thermal oxidizer at 95% heat recovery has a deemed cost of $546,000.

Incinerator cost is treated as 0% heat recovery in the recuperative cost summary table above and has a deemed cost of $106,042.

###### Loadshape

N/A

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

Energy savings from thermally efficient equipment are entirely fossil fuel related. There are no electricity savings nor peak demand savings, as the blower fans and valve actuators are assumed to operate the same in all conditions.

###### Electric Energy Savings

N/A

###### Summer Coincident Peak Demand Savings

N/A

###### Fossil Fuel Savings

ΔTherms = ((Baseline QT Air Pollution Control Device - Proposed QT Air Pollution Control Device) x Hours) / LHV

Where:

LHV 	= Latent Heat of Vaporization

= If the post is regenerative thermal oxidizer, LHV = 0.953.

= If the post is recuperative thermal oxidizer, LHV = 1.

Regenerative or Recuperative: A baseline or proposed regenerative or recuperative air pollution control device can each be modeled in the following heat balance equation:

QT (btuh) = QI + QCC + QRL – QVOC

Incinerator: A baseline incinerator air pollution control device can be modeled as the following heat balance equation:

QT (btuh) = QI + QCC + QRL

Where:

QT	= Total Energy Input

QI	= Energy (btuh) used to raise the temperature of process air (FI)

QCC	= Heat (btuh) used to raise the temperature of combustion air (FCC)

QRL	= Radiation heat loss (btuh) from Regenerative thermal oxidizer

QVOC	= Heat release (btuh) provided by VOC combustion

Hours	= Annual hours per year that oxidizer is used

Where:

QI = FI * 1.08 * (TO – TI)

TO	= Average stack outlet temperature (°F) (actual trended average or use efficiency equation below to solve for TO under assumed conditions)

TO	= (TC - N * TC - TI) * FI( FI +  FCC)

TC	= Combustion chamber temperature (°F), trended or design value provided by the manufacturer

N	= Thermal Efficiency of Heat Exchanger

| Thermal Oxidizer | Efficiency |
| --- | --- |
| Regenerative | 97% |
| Recuperative | 70% |
| Incinerator | 0% |

TI	= Inlet air temperature (°F), this is the temperature of the air coming from the process

FI	= Process air flow (cfm), actual loading or use maximum design value

1.08	= Conversion Factor

= 60 (min/hr) * 0.07489 (lb/ft3, density air at standard conditions) * 0.2404 btu/°F-lb, (specific heat of air), where 0.2404 is average heat capacity of intake air

Where:

QCC = FCC * 1.08 * (TC – TA)

FCC	= Additional combustion air flow (cfm) at provided FI value

= If unknown, assume 3% of design value

TC	= Combustion chamber temperature (°F) (same as above)

TA	= Combustion intake air temperature (°F)

= Indoor: Actual, or assume 70 °F year-round

= Outdoor: Actual annual average found near the facility, or assume  annual averages below:

| Climate Zone | Average Outdoor Air Temperature (°F) |
| --- | --- |
| 1 (Rockford) | 49.7 |
| 2 (Chicago) | 51.4 |
| 3 (Springfield) | 54.3 |
| 4 (Belleville) | 58.0 |
| 5 (Marion) | 56.8 |

Where:

QRL = SA * HLF

SA	= Thermal oxidizer exterior surface area (ft2) (provided by the manufacturer or rough measurements taken)

HLF	= Assume a heat loss factor of 240 btuh/ft2 if installed outdoors; otherwise, 0 btuh/ft2 for indoor installation since the waste heat provides space heating and offset gas-fired space heating equipment

Where:

QVOC = VOC * HC * (%Dest / 100)

VOC	= Average lbs/hr from process to oxidizer

HC	= btu/lb, weighted average for the heat of combustion of VOCS

= Site-specific, lookup table

%Dest	= Destruction efficiency of VOCs provided by the manufacturer, or use:

Hours	= Annual hours of operation of the air pollution control device, assume customer production schedule or hours of occupancy

LHV	= Lower heating value of natural gas

= 983 btu/CF

HHV	= High heating value of natural gas

= 1,031 btu/CF

0.953	= LHV / HHV conversion factor

To calculate the fossil fuel savings by upgrading from an incinerator to an efficient thermal oxidizer system, the new temperatures must be considered. The addition of heat recovery (either recuperative or regenerative) will increase the inlet temperature, TI, above that found in the facility.

The calculation should consider changes in the inlet temperature. First, the key temperature required for 99.99% destruction efficiency of various VOC compounds must be determined. The U.S. EPA’s Innovative Strategies and Economics Group produced some guidance on the key temperatures for the following compounds:

| VOC Compound | Key Destruction Temperature (°F) |
| --- | --- |
| Acrylonitrile | 1,344 |
| Allyl chloride | 1,276 |
| Benzene | 1,350 |
| Chlorobenzene | 1,407 |
| 1,2 – dichloromethane | 1,368 |
| Methyl chloride | 1,596 |
| Toluene | 1,341 |
| Vinyl chloride | 1,369 |

For VOC compounds not listed above, the Key Destruction Temperature should be determined through product literature, equipment vendors, Material Data Safety Sheets (MSDS), or some other source.

When employing heat recovery, either recuperative or regenerative, the increased outlet temperature is limited to the heat exchanger efficiency. This efficiency, or in other words how much heat can be recovered, is limited to the auto-ignition temperatures of the VOCs in the air stream. Regenerative thermal oxidizers offer the advantage of recovering more heat as the combustion can occur within the heat exchanger, whereas with recuperative thermal oxidizers, the heat exchanger efficiency is much lower to prevent premature combustion in the stack of the recuperator.

While the VOCs in the waste air stream have some heating value that contributes to reaching the required chamber temperature, such contributions do not have as high of an impact in the overall energy consumption calculation when compared to the heat exchanger efficiency.

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A, as VOCs are still oxidized under the baseline condition and not contributing to overall site emissions.

###### Deemed O&M Cost Adjustment Calculation

The ceramic media in the regenerative thermal oxidizer requires regular servicing and may need to be considered as a regular part of facility O&M.

###### Measure Code: CI-MSC-ETOX-V03-260101

###### Review Deadline: 1/1/2030

### 5.1.17	ENERGY STAR All-in-One Clothes Washer-Dryer

###### Description

This measure relates to the installation of a residential combination all-in-one clothes washer-dryer meeting the ENERGY STAR criteria. ENERGY STAR qualified combination all-in-one clothes washer-dryers save energy through a combination of more efficient drying and reduced runtime of the drying cycle. More efficient washing and drying is achieved through heat pump technology, modifying operating conditions such as air flow and/or heat input rate, improving air circulation through better drum design, and improving efficiency of motors. ENERGY STAR provides criteria for electric clothes washer-dryers with heat pump technology.

This measure was developed to be applicable to the following program types: Time of Sale, New Construction, Retrofit. If applied to other program types, the measure savings should be verified.

###### Definition of Efficient Equipment

All-in-one clothes washer-dryer must meet the ENERGY STAR or ENERGY STAR Most Efficient criteria, as required by the program. Units utilizing the Heat Pump designation must meet the same ENERGY STAR criteria and be classified as Heat Pump units.

###### Definition of Baseline Equipment

The baseline condition for a washing cycle is a clothes washer meeting the minimum federal baseline as of January 2018.

| Efficiency Level | Top Loading ≥1.6 Cu ft | Front Loading ≥1.6 Cu ft |
| --- | --- | --- |
| Federal Standard | ≥1.57 IMEF, ≤6.5 IWF | ≥1.84 IMEF, ≤4.7 IWF |

The baseline condition used for a washing cycle for this measure is a weighted average of 1.7 IMEF.

The baseline condition for a drying cycle is a clothes dryer meeting the minimum federal requirements for units manufactured on or after January 1, 2015.

| Efficiency Level | Front Loading ≥4.5 Cu ft |
| --- | --- |
| Federal Standard for Clothes Dryer | 3.11 CEF for Vented Electric, 2.84 CEF for Vented Gas |

###### Deemed Lifetime of Efficient Equipment

The expected measure life is assumed to be 14 years.

###### Deemed Measure Cost

The average cost of the ENERGY STAR combination all-in-one clothes washer-dryer $2,331 with no additional installation cost for a total measure cost of $2,331.

For a non-IQ participant, the incremental cost is assumed to be $1,328.

For an IQ participant, the incremental cost is assumed to be $1,224.

###### Loadshape

Loadshape R17 - Residential Electric Dryer

###### Coincidence Factor

The coincidence factor for this measure is 3.8%.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Non Fuel Switch Measures

ΔkWhtotal = ΔkWhclothes washer  + ΔkWhdryer

ΔkWhclothes washer = [Capacity * IQAdjCW/IMEFbase * Ncycles * (%CWbase + (%DHWbase *  %Electric_DHW))] - [Capacity * 1/IMEFeff * Ncycles * (%CWeff + (%DHWeff * %Electric_DHW))]

ΔTherms	= [Capacity * IQAdjCW/IMEFbase * Ncycles * (%DHWbase * %Fossil_DHW * R_eff)] - [Capacity * 1/IMEFeff * Ncycles * (%DHWeff * %Fossil_DHW *R_eff)] * ThermConvert

ΔkWhdryer = ((Load/CEFbase* IQAdjD) – Load/CEFeff) * Ncycles * %Electric

Fuel Switch/Electrification Measures

Total Site Energy Savings (MMBTUs) = Site Energy Savings (MMBTUs)clothes washer + Site Energy Savings (MMBTUs)dryer

Break out savings calculated for the washing cycle for a baseline clothes washer with gas DHW replaced with an all-in-one clothes washer-dryer with electric DHW

SiteEnergySavings(MMBTUs)clothes washer = [NonFuelSwitchSavingsclothes washer]

NonFuelSwitchSavingsclothes washer	= [(ElectricConsumptionBaseline clothes washer  + GasConsumptionBaseline clothes                  washer) – (EfficientConsumptionefficient clothes washer + GasConsumptionefficient clothes washer)]

ElectricConsumptionBaseline clothes washer  = [Capacity * IQAdjCW/IMEFbase * Ncycles * (%CWbase + (%DHWbase * %Electric_DHW)) * MMBtu_convert]

GasConsumptionBaseline clothes washer           = [Capacity * IQAdjCW/IMEFbase * Ncycles * (%DHWbase * %Fossil_DHW * R_eff) * MMBtu_convert ]

ElectricConsumptionefficient clothes washer     = [Capacity * 1/IMEFeff * Ncycles * (%CWeff + (%DHWeff * %Electric_DHW) * MMBtu_convert]

GasConsumptionefficient clothes washer           = [Capacity * 1/IMEFeff * Ncycles * (%DHWeff * %Fossil_DHW * R_eff) * MMBtu_convert ]

Break out savings calculated for the drying cycle for a baseline gas dryer replaced with an all-in-one clothes washer-dryer.

Site Energy Savings (MMBTUs)dryer6  = [FuelSwitchSavingsdryer] + [NonFuelSwitchSavingsdryer]

FuelSwitchSavingsdryer  = [Load/CEFbaseGas * IQAdjD * Ncycles * MMBtu_convert * %GasGas] - [Load/CEFeffElec * Ncycles * MMBtu_convert * %GasGas]

NonFuelSwitchSavingsdryer   = [Load/CEFbaseGas * IQAdjD * Ncycles* MMBtu_convert * %ElectricGas] - [Load/CEFeffElec * Ncycles * MMBtu_convert * %ElectricGas]

If Total Site Energy Savings (MMBTUs) calculated above is positive, the measure is eligible.

The appropriate savings claim is dependent on which utilities are supporting the measure as provided in a table below:

| Measure supported by: | Electric Utility claims (kWh): | Gas Utility claims (therms): |
| --- | --- | --- |
| Electric utility only | SiteEnergySavings * 1,000,000/3,412 | N/A |
| Gas utility only | N/A | SiteEnergySavings * 10 |

Where:

Capacity	= Unit capacity (cubic feet)

= Actual. If capacity is unknown assume 4.9 cubic feet

IMEFbase	= Integrated Modified Energy Factor of baseline clothes washer unit

= 1.71

IQAdjCW	=Baseline consumption adjustment for IQ program participants to account for a portion of participants who would have utilized the secondary market.

= 1.02 if IQ, 1.0 if non-IQ

IMEFeff	= Integrated Modified Energy Factor of Efficient Combination All-in-One Washer-Dryer unit

= Actual. If unknown assume average values provided below.

| Efficiency Class | IMEFeff |
| --- | --- |
| ENERGY STAR | 2.76 |
| ENERGY STAR Most Efficient | 2.92 |

Ncycles	= Number of cycles per year

= 276

%CW	= Percentage of total energy consumption for Clothes Washer operation (different for baseline and efficient unit – see table below)

%DHW	= Percentage of total energy consumption used for water heating (different for baseline and efficient unit – see table below)

| Product Class | Percentage of Total Energy Consumption of Clothes Washer |  |
| --- | --- | --- |
|  | %CW | %DHW |
| Baseline | 6.7% | 15.8% |
| Efficient | 6.6% | 13.0% |

%Electric_DHW	= Percentage of DHW savings assumed to be electric

= 100 % for Electric

= 0 % for Fossil Fuel

= If unknown, use the following table:

| Product Class | Location |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Utility | Single Family | Single Family Low Income | Multi Family | Multi Family Low Income | Unknown |
| Ameren | 19.7% | 30.6% | 63.3% | 67.3% | 31.4% |
| ComED | 14.0% | 21.5% | 43.0% | 48.4% | 32.9% |
| People’s Gas | 2.1% | 2.0% | 1.7% | 2.4% | 2.2% |
| Northshore Gas | 1.5% | 1.8% | 10.0% | 2.4% | 2.4% |
| Nicor Gas | 7.6% | 9.9% | 14.4% | 22.6% | 10.0% |
| All DUs |  |  |  |  | 29% |

Note: If a measure is supported by a gas and electric utility through a joint program, and it is unknown whether the participant has a gas supply, the electric utility values in the table above should be used. If it is known that the participant has a gas supply, the values from the gas utility above should be applied.

Load 	= The average total weight (lbs) of clothes per drying cycle. If unit size is unknown, assume standard.

| Unit Size | Load (lbs) |
| --- | --- |
| Standard | 8.45 |

CEFbase 	= Combined energy factor (CEF) (lbs/kWh) of the baseline unit is based on existing federal standards energy factor as performed in the ENERGY STAR analysis3. If product class unknown, assume electric, standard.

| Product Class | CEFbase (lbs/kWh) |
| --- | --- |
| Vented Electric, Standard (≥ 4.4 ft3) | 3.11 |
| Vented Gas | 2.844 |

IQAdjD	= Baseline consumption adjustment for IQ program participants to account for a portion of participants who would have utilized the secondary market.

= 1.033 if IQ, 1.0 if non-IQ

CEFeff	= CEF (lbs/kWh) of ENERGY STAR or ENERGY STAR Most Efficient requirements Combination All-in-One Washer-Dryer.

= Actual. If unknown assume values provided below.

| Efficiency Class | CEFeff (lbs/kWh)12 |
| --- | --- |
| ENERGY STAR | 4.97 |
| ENERGY STAR Most Efficient | 6.9 |

%Electric	= The percent of overall savings coming from electricity.

= 100% for electric dryers, 16% for gas dryers.

%Fossil_DHW	= Percentage of DHW savings assumed to be Fossil Fuel

= 100 % for Fossil fuel

= 0 % for Electric

= If unknown, use the following table:

| Product Class | Location |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Utility | Single Family | Single Family Low Income | Multi Family | Multi Family Low Income | Unknown |
| Ameren | 80.3% | 69.4% | 36.7% | 32.7% | 68.6% |
| ComED | 86.0% | 78.5% | 57.0% | 51.6% | 67.1% |
| People’s Gas | 97.9% | 98.0% | 98.3% | 97.6% | 97.8% |
| Northshore Gas | 98.5% | 98.2% | 90.0% | 97.6% | 97.6% |
| Nicor Gas | 92.4% | 90.1% | 85.6% | 77.4% | 90.0% |
| All DUs |  |  |  |  | 71% |

Note: If a measure is supported by a gas and electric utility through a joint program, and it is unknown whether the participant has a gas supply, the electric utility values in the table above should be used. If it is known that the participant has a gas supply, the values from the gas utility above should be applied.

R_eff	= Recovery efficiency factor

=1.26

MMBtu_convert	= Conversion factor from kWh to MMBtu.

= 0.003412

%Gas	= Percent of overall savings coming from gas.

= 0% for electric dryers and 84% for gas dryers.

For example:

Non Fuel Switch example, for a non- IQ Time of Sale, standard, ventless, ENERGY STAR All-in-One Clothes Washer-Dryer:

ΔkWhtotal = ΔkWhclothes washer + ΔkWhdryer

ΔkWhclothes washer = [Capacity * 1/IMEFbase * Ncycles * (%CWbase + (%DHWbase * %Electric_DHW))] - [Capacity * 1/IMEFeff * Ncycles * (%CWeff + (%DHWeff * %Electric_DHW))]

ΔkWhdryer = ((Load/CEFbase* IQAdj) – Load/CEFeff) * Ncycles * %Electric

ENERGY STAR

ΔkWhclothes washer = (4.9 * 1/1.71 * 276 * (6.7% + (15.8% * 100%))) – (4.9 * 1/2.76 * 276 *(6.6% + (13% * 100%)))

= 81.9 kWh

ΔkWhdryer   = ((8.45/3.11*1) – 8.45/4.97) * 276 *100%

= 280.6 kWh

ΔkWhTotal      = 280.6 + 81.9

= 363 kWh

ENERGY STAR Most Efficient/CEE Tier 2

ΔkWhclothes washer = (4.9 * 1/1.71 * 276 * (6.7% + (15.8% * 100%))) – (4.9 * 1/2.92 * 276 *  (6.6% + (13% * 100%)))

= 87.2 kWh

ΔkWhdryer    = ((8.45/3.11*1) – 8.45/6.9) * 276 *100%

= 411.9 kWh

ΔkWhTotal      = 411.9 + 87.2

= 499 kWh

Fuel switch example, for a Time of Sale, an ENERGY STAR All-in-One Clothes Washer-Dryer in place of a clothes washer with gas DHW and vented gas dryer:

Total SiteEnergySavings (MMBTUs) = SiteEnergySavings (MMBTUs)clothes washer + SiteEnergySavings (MMBTUs)dryer

SiteEnergySavings (MMBTUs)clothes washer  = [(ElectricConsumptionBaseline clothes washer  + GasConsumptionBaseline clothes washer) – EfficientConsumptionefficient clothes washer]

ElectricConsumptionclothes washer = [(Capacity * 1/IMEFbase * Ncycles * ((%CWbase +  %Electric_DHW) *MMBtu_convert]

= (4.9 * 1/1.71 * 276 * (6.7% + ( 15.8% * 0%)) * 0.003412)

= 0.18 MMBTU

GasConsumptionBaseline clothes washer  = [Capacity * 1/IMEFbase * Ncycles * (%DHWbase * %Fossil_DHW * R_eff) * MMBtu_convert ]

= (4.9 * 1/1.71 * 276 * (15.8% * 1 * 1.26))* 0.003412)

= 0.54 MMBTU

EfficientConsumptionefficient clothes washer = [Capacity * 1/IMEFbase * Ncycles * (%CWeff + (%DHWeff * %Electric_DHW) * MMBtu_convert]

= (4.9 * 1/2.8 * 276 * (6.6% + (13% * 100%)) * 0.003412)

= 0.32 MMBTU

SiteEnergySavings (MMBTUs)clothes washer

= (0.18 + 0.54 ) – 0.32

= 0.40 MMBTU

SiteEnergySavings (MMBTUs)dryer = [FuelSwitchSavingsdryer] + [NonFuelSwitchSavingsdryer]

FuelSwitchSavingsdryer  = [Load/CEFbaseGas * IQAdj * Ncycles * MMBtu_convert * %GasGas] - [Load/CEFeffElec * Ncycles * MMBtu_convert * %GasGas]

= (8.45/2.84 * 1 * 276 * 0.003412 * 84%) - (8.45/4.97 * 276 *

0.003412 * 84%)

= 1.01 MMBTU

NonFuelSwitchSavingsdryer   = [Load/CEFbaseGas * IQAdj * Ncycles * MMBtu_convert * %ElectricGas] - [Load/CEFeffElec * Ncycles * MMBtu_convert * %ElectricGas]

= (8.45/2.84 * 1 * 276 * 0.003412 * 16%) - (8.45/4.97 * 276 *

0.003412 * 16%)

= 0.19 MMBTU

SiteEnergySavings (MMBTUs)dryer

= 1.01 + 0.19

= 1.2 MMBTU

Total SiteEnergySavings (MMBTUs) = SiteEnergySavings (MMBTUs)dryer + SiteEnergySavings (MMBTUs)clothes washer

= 0.40 +  1.2

= 1.6 MMBTU

If supported by an electric utility:  ΔkWh = ΔTotal SiteEnergySavings(MMBTUs)  * 1,000,000 / 3,412

= 1.6 * 1,000,000 / 3,412

= 469 kWh

If supported by a gas utility:  ΔTherms = ΔTotal SiteEnergySavings(MMBTUs)  * 10

= 1.6 * 10

= 16 Therms

Summer Coincident Peak Demand Savings

ΔkWTotal = ((ΔkWhclothes washer + ΔkWhdryer)/ Hours) * CF

Where:

ΔkWh	= ΔkWhclothes washer + ΔkWhdryer

ΔkWhclothes washer	= Energy Savings for clothes washer. Note: do not include the secondary savings in this calculation.

ΔkWhdryer	= Energy Savings for dryer.

For non-fuel switch measures, use ΔkWh as calcuated in Electric Energy Savings section above, for fuel-switch measures use the ΔkWh as provided in the Cost Effectiveness Screening and Load Reduction Forecasting when Fuel Switching section below.

Hours	= Assumed run hours of unit

= 630 hours

CF	= Summer Peak Coincidence Factor for measure.

For example, for a Time of Sale, an ENERGY STAR All-in-One Clothes Washer-Dryer

ΔkW         = ((81.9 + 280.6) / 630) *0.038

= 0.02 kW

= 0.0387

###### Fossil Fuel Savings

Calculation provided together with Electric Energy Savings above.

###### Water and Other Non-Energy Impact Descriptions and Calculation

ΔWater (gallons)	 = Capacity * ((IWFbase * IQAdjWater) – IWFeff) * Ncycles

Where:

ΔWater (gallons) 	= Water saved, in gallons

IWFbase 		= Integrated Water Factor of baseline clothes washer

= 5.59

IQAdjWater	= Baseline water consumption adjustment for IQ program participants to account for a portion of participants who would have utilized the secondary market.

=1.02 if IQ, 1.0 if non-IQ

IWFeff 	= Water Factor of Efficient Combination All-in-One Washer-Dryer unit

= Actual. If unknown assume average values provided below

Using the default assumptions provided above, the prescriptive water savings for each efficiency level are presented below:

| Effciency Class | IWFeff12 | ΔWater (gallons per year) |
| --- | --- | --- |
| ENERGY STAR | 3.1 | 3,367.5 |
| ENERGY STAR Most Efficient | 2.9 | 3,638.0 |

For example, for a non- IQ Time of Sale, standard, ventless, ENERGY STAR All-in-One Clothes Washer-Dryer:

ENERGY STAR

ΔWater     = 4.9 * ((5.59 * 1) - 3.10) * 276

= 3,367.5 Gallons per year

ENERGY STAR Most Efficient/CEE Tier 2

ΔWater    = 4.9 * ((5.59 *1) - 2.9) * 276

= 3,638.0 Gallons per year

Other factors as defined above.

Secondary kWh Savings for Clothes Washer Water Supply and Wastewater Treatment

The following savings should be included in the total savings for this measure but should not be included in TRC tests to avoid double counting the economic benefit of water savings.

ΔkWhwater       = ΔWater (gallons) / 1,000,000 * Ewater total

Where:

ΔWater (gallons) = Water saved, in gallons – as calculated below.

Ewater total 	     = IL Total Water Energy Factor (kWh/Million Gallons)

= 5010

For example, for a non- IQ Time of Sale, standard, ventless, ENERGY STAR All-in-One Clothes Washer-Dryer:

ENERGY STAR

ΔkWhwater = 3367.5/1,000,000 * 5,010

= 16.9 kWh

ENERGY STAR Most Efficient/CEE Tier 2

ΔkWhwater = 3638.0/1,000,000 * 5,010

= 18.2 kWh

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Cost Effectiveness Screening and Load Reduction Forecasting When Fuel Switching

This measure can involve fuel switching from fossil fuel to electric.

For the purposes of forecasting load reductions due to fuel switch projects per Section 16-111.5B, changes in site energy use at the customer’s meter (using ΔkWh algorithm below) adjusted for utility line losses (at-the-busbar savings), customer switching estimates, NTG, and any other adjustment factors deemed appropriate, should be used.

The inputs to cost effectiveness screening should reflect the actual impacts on the electric and fuel consumption at the customer meter and, for fuel switching measures, this will not match the output of the calculation/allocation methodology presented in the “Electric Energy Savings” and “Fossil Fuel Savings” sections above. Therefore, in addition to the calculation of savings claimed, the following values should be used to assess the cost effectiveness of the measure.

ΔTherms = [Clothes Washer with Gas DHW Consumption Replaced + Gas Dryer Consumption Replaced] – [All-in-One Clothes Washer-Dryer Consumption Added]

= [(Capacity * IQAdj/IMEFbase *  Ncycles * (%DHWbase * %Fossil_DHW * R_eff)) + ((Load/CEFbaseGas * IQAdj) * Ncycles * Therm_convert * %GasGas) + ((Load/CEFeffElec * IQAdj) * Ncycles * Therm_convert * %GasGas))] – [(Capacity * 1/IMEFeff * Ncycles * (%CWeff + (%DHWeff * %Electric_DHW) * Therm_convert) + (Load/CEFeff * Ncycles * %Gasgas* Therm_convert)]

ΔkWh = [Clothes Washer with Gas DHW Electric Consumption Replaced + Gas Dryer Electric Consumption Replaced] - [All-in-One Clothes Washer-Dryer Consumption Added]

= [((Load/CEFbaseGas * IQAdj) * Ncycles * %ElectricGas) + (Capacity * 1/IMEFbase * Ncycles * (%CWbase + (%DHWbase * %Electric_DHWbase)] - [((Load/CEFeff * Ncycles * %Gasgas) + (Load/CEFeff * Ncycles * %Electricgas)) + (Capacity * 1/IMEFeff * Ncycles * (%CWeff + (%DHWeff * %Electric_DHWefficient)]

###### Measure Code: RS-APL-ACWD-V03-260101

###### Review Deadline: 1/1/2030

### Duct Insulation and Sealing

###### Description

This measure describes evaluating the savings associated with adding duct insulation or performing duct sealing using mastic sealant, metal tape, or injection of UL certified and low VOC for sealant to the distribution system of homes with either central air conditioning or a ducted heating system.

Three methodologies for estimating the savings associate from sealing the ducts are provided, one of which can also be used to estimate duct insulation savings. The first preferred method requires the use of a blower door, the second method requires a pressurized duct test, and the third requires careful inspection of the duct work.

- Modified Blower Door Subtraction – this technique is described in detail on the Energy Conservatory website. See ‘The Energy Conservatory_Blower-Door-Subtraction-Method.pdf’.

- Pressurized Duct Test – this technique includes direct measurement of air leaks in the duct system.

- Evaluation of Distribution Efficiency – this methodology can be used to estimate duct insulation or duct sealing savings, and requires the evaluation of three duct characteristics below, and use of the Building Performance Institutes ‘Distribution Efficiency Look-Up Table’.

  - Percentage of duct work found within the conditioned space

  - Duct leakage evaluation

  - Duct insulation evaluation

This measure was developed to be applicable to the following program types:  RF. If applied to other program types, the measure savings should be verified.

For duct insulation and sealing of central systems in multifamily buildings, use Volume 2 Commercial and Industrial Measures.

###### Definition of Efficient Equipment

For duct sealing, the efficient condition is sealed duct work throughout the unconditioned or semi-conditioned space in the home. A non‐conditioned space is defined as a space outside of the thermal envelope of the building that is not intentionally heated for occupancy (crawl space, roof attic, etc.). A semi-conditioned space is defined as a space within the thermal envelop that is not intentionally heated for occupancy (unfinished basement).

For duct insulation, the efficient condition is ductwork insulated with a minimum of R-4 insulation in an unconditioned or semi-conditioned space in the home.

###### Definition of Baseline Equipment

For duct sealing, the existing baseline condition is leaky duct work within the unconditioned or semi-conditioned space in the home.

For duct insulation, the baseline condition is un-insulated ductwork that passes through an unconditioned or semi-conditioned space in the home.

###### Deemed Lifetime of Efficient Equipment

The assumed lifetime of this measure is 20 years.

Note: a mid-life adjustment to account for replacement of HVAC equipment during the measure life should be applied after 10 years. See section below for detail.

###### Deemed Measure Cost

The actual duct sealing or insulating measure cost should be used.

###### Loadshape

Loadshape R08 - Residential Cooling

Loadshape R09 - Residential Electric Space Heat

Loadshape R10 - Residential Electric Heating and Cooling (Shell Measures)

###### Coincidence Factor

The summer peak coincidence factor for cooling is provided in two different ways below. The first is used to estimate peak savings during the utility peak hour and is most indicative of actual peak benefits, and the second represents the average savings over the defined summer peak period and is presented so that savings can be bid into PJM’s capacity market.

CFSSP 	= Summer System Peak Coincidence Factor for Central A/C (during utility peak hour)

= 68%

CFPJM  	= PJM Summer Peak Coincidence Factor for Central A/C (average during PJM peak period)

= 46.6%

Algorithm

###### Calculation of Savings

###### Electric Energy Savings

For Methodology 1: Modified Blower Door Subtraction, follow steps (a) through (c)

For Methodology 2: Pressurized Duct Test, follow step (c)

- Determine Duct Leakage rate before and after performing duct sealing:

Duct Leakage (CFM50DL) 	= (CFM50Whole House – CFM50Envelope Only) * SCF

Where:

CFM50Whole House	= Standard Blower Door test result finding Cubic Feet per Minute at 50 Pascal pressure differential

CFM50Envelope Only	= Blower Door test result finding Cubic Feet per Minute at 50 Pascal pressure differential with all supply and return registers sealed.

SCF	= Subtraction Correction Factor to account for underestimation of duct leakage due to connections between the duct system and the home. Determined by measuring pressure in duct system with registers sealed and using look up table provided by Energy Conservatory.

- Calculate duct leakage reduction, convert to CFM25DL and factor in Supply and Return Loss Factors

Duct Leakage Reduction (∆CFM25DL) 	= (Pre CFM50DL – Post CFM50DL) * 0.64 * (SLF + RLF)

Where:

0.64		= Converts CFM50 to CFM25

SLF		= Supply Loss Factor

= % leaks sealed located in Supply ducts * 1

Default = 0.5

RLF		= Return Loss Factor

= % leaks sealed located in Return ducts * 0.5

Default = 0.25

- Calculate Electric Energy Savings:

ΔkWh		= ΔkWhcooling + ΔkWhheatingElectric + ΔkWhFan

ΔkWhcooling 	= ((∆CFM25DL/ ((OutputCapacityCool/12,000) * 400)) * FLHcool * OutputCapacityCool * TRFcool * %Cool) / 1,000 / ηCool

ΔkWhheatingElectric 	= ((∆CFM25DL /((OutputCapacityHeat/12,000) * 400)) * FLHheatElec * OutputCapacityHeat * TRFheat *%ElectricHeat) / ηHeat / 3412

ΔkWhFan 	If fossil fueled furnace:	= (ΔTherms * Fe * 29.3)

If electric furnace:	= ΔkWh_heating * Fe

Where:

∆CFM25DL	= Duct leakage reduction in CFM25

= For Methodology 1: Modified Blower Door Subtraction,calculated above

= For Methodology 2: Pressurized Duct Test, use actual

OutputCapacityCool	= Output capacity of Air Cooling system (Btu/hr)

= Actual

12,000		= Converts Btu/H capacity to tons

400		= Converts capacity in tons to CFM (400CFM / ton)

FLHcool 		= Full load cooling hours

= Dependent on location as below:

| Climate Zone (City based upon) | FLHcool Single Family | FLHcool Multifamily |
| --- | --- | --- |
| 1 (Rockford) | 547 | 499 |
| 2 (Chicago) | 709 | 629 |
| 3 (Springfield) | 779 | 707 |
| 4 (Belleville) | 1,082 | 982 |
| 5 (Marion) | 956 | 868 |
| Weighted Average ComEd Ameren Statewide | 676 875 731 | 603 791 655 |

Use Multifamily if: Building meets utility’s definition for multifamily and system serves single unit. For residential sized systems serving 2 or more units, assume single family hours. For central systems use Volume 2 Commercial and Industrial Measures.

TRFcool	= Thermal Regain Factor for cooling by space type

= 1.0 for Unconditioned Spaces

= 0.4 for Semi-Conditioned Spaces

%Cool		= Percent of homes that have cooling

| Cooling (Central or Room AC) | %Cool (By Market Segment) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Single Family Non-IQ | Single Family IQ | Multi Family Non-IQ | Multi Family IQ | Unknown |
| Yes | 100% |  |  |  |  |
| No | 0% |  |  |  |  |
| Unknown (for use in program evaluation only) | 98.9% | 96.5% | 99.8% | 98.7% | 98.6% |

1000		= Converts Btu to kBtu

ηCool	= Efficiency (SEER2) of Air Conditioning equipment (kBtu/kWh) * DistEffbase

DistEffbase	= Distribution Efficiency of base condition

= Actual where it is possible to measure or reasonably estimate. If unknown assume 0.85

= Actual. If unknown assume the following:

| Age of Equipment | SEER2 Estimate | ηCool (SEER2 * 0.85) |
| --- | --- | --- |
| Before 2006 | 9.5 | 8.1 |
| After 2006 - 2014 | 12.4 | 10.5 |
| Central AC After 1/1/2015 | 12.4 | 10.5 |
| Heat Pump After 1/1/2015 | 13.3 | 11.3 |
| Unknown (for use in program evaluation only) Single Family Non-IQ Single Family IQ Multi Family Non-IQ Multi Family IQ Unknown |  | 10.5 10.5 10.6 10.5 10.5 |

ΔTherms 	= Therm savings as calculated in Fossil Fuel Savings

Fe		= Furnace Fan energy consumption as a percentage of annual fuel consumption

= 3.14%

29.3		= kWh per therm

For example, duct sealing in unconditioned space a single family house in Springfield with a 36,000 Btu/H, SEER 11 central air conditioning with 85% estimated distribution efficiency, an 80% AFUE, 105,000 Btu/H natural gas furnace and the following blower door test results:

Before: 	CFM50Whole House 	= 4800 CFM50

CFM50Envelope Only = 4500 CFM50

House to duct pressure of 45 Pascals. = 1.29 SCF (Energy Conservatory look up table)

After: 	CFM50Whole House 	= 4600 CFM50

CFM50Envelope Only = 4500 CFM50

House to duct pressure of 43 Pascals = 1.39 SCF (Energy Conservatory look up table)

Duct Leakage:

CFM50DL before 	= (4800 – 4500) * 1.29

= 387 CFM

CFM50DL after 	= (4600 – 4500) * 1.39

= 139 CFM

Duct Leakage reduction at CFM25:

∆CFM25DL	= (387 – 139) * 0.64 * (0.5 + 0.25)

= 119 CFM25

Energy Savings:

ΔkWhcooling	= [((119 / ((36,000/12,000) * 400)) * 779 * 36,000 * 1) / 1000 / (11 * 0.85)] + (179 * 0.0314 * 29.3)

= 297 + 165

= 462 kWh

Heating savings for homes with electric heat:

ΔkWhheatingElectric 	= ((∆CFM25DL /((OutputCapacityHeat/12,000) * 400)) * FLHheatElec * OutputCapacityHeat * TRFheat *%ElectricHeat) / ηHeat / 3412

Where:

OutputCapacityHeat	= Heating output capacity (Btu/hr) of electric heat

=Actual

FLHheatElec		= Full load heating hours for electric heat

= Dependent on location as below:

| Climate Zone (City based upon) | FLH_heat |
| --- | --- |
| 1 (Rockford) | 1924 |
| 2 (Chicago) | 1726 |
| 3 (Springfield) | 1708 |
| 4 (Belleville) | 1195 |
| 5 (Marion/Murphysboro) | 1270 |
| Weighted Average ComEd Ameren Statewide | 1766 1547 1700 |

TRFheat 		= Thermal Regain Factor for heating by space type

= 0.40 for Semi-Conditioned Spaces

= 1.0 for Unconditioned Spaces

%ElectricHeat	= Percent of homes that have electric space heating

= 100 % for Electric Resistance (Baseboard or Electric Furnace) or Heat Pump

= 0 % for Natural Gas

= If unknown, use the following table:

| Utility | Location |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Single Family | Single Family Low Income | Multi Family | Multi Family Low Income | Unknown |
| Ameren | 14.0% | 13.7% | 37.2% | 56.3% | 19.5% |
| ComEd | 14.0% | 21.5% | 43.0% | 48.4% | 32.9% |
| PGL | 1.0% | 1.5% | 4.0% | 2.8% | 2.2% |
| NSG | 1.3% | 0.8% | 32.5% | 1.2% | 3.3% |
| Nicor | 1.6% | 3.8% | 13.5% | 21.6% | 4.7% |
| All DUs |  |  |  |  | 24.6% |

Note: If a measure is supported by a gas and electric utility through a joint program, and it is unknown whether the participant has a gas supply, the electric utility values in the table above should be used. If it is known that the participant has a gas supply, the values from the gas utility above should be applied.

ηHeat 		= Efficiency in COP of Heating equipment * DistEffbase

DistEffbase	= Distribution Efficiency of base condition

= Actual where it is possible to measure or reasonably estimate. If unknown assume 0.85

= Actual. If not available use:

| System Type | Age of Equipment | HSPF2 Estimate | ηHeat (Effective COP Estimate * Distribution Efficiency) = (HSPF2/3.412)*0.85 |
| --- | --- | --- | --- |
| Heat Pump (if age unknown, assume 2006-2014) | Before 2006 | 5.8 | 1.44 |
|  | After 2006 - 2014 | 6.5 | 1.62 |
|  | 2015 on | 7.0 | 1.74 |
| Resistance (Baseboard or Electric Furnace) | N/A | N/A | 1.00 |
| Unknown (for use in program evaluation only) | N/A | N/A | 1.32 |

3412	= Converts Btu to kWh

For example, duct sealing in unconditioned space in a 36,000 Btu/H 2.5 COP heat pump heated single family house in Springfield with the blower door results described above:

ΔkWhheating	= ((119 / ((36,000/12,000) * 400)) * 1,708 * 36,000 * 1 * 1) / 2.5 / 3,412

= 715 kWh

Methodology 3: Evaluation of Distribution Efficiency

Determine Distribution Efficiency by evaluating duct system before and after duct sealing or duct insulating using Building Performance Institute “Distribution Efficiency Look-Up Table”.

ΔkWh	= ((((DEafter – DEbefore) / DEafter) * FLHcool * CapacityCool * TRFcool * %Cool)/1,000 / ηCool) + (ΔTherms * Fe * 29.3)

Where:

DEafter		= Distribution Efficiency after duct sealing, see table below

DEbefore		= Distribution Efficiency before duct sealing, see table below

| Insulation | Sealing | Heating |  |  | Cooling |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Attic | Basement | Vented Crawl | Attic | Basement | Vented Crawl |
| R-0 | Leaky | 69% | 93% | 74% | 61% | 81% | 76% |
|  | Average | 73% | 94% | 78% | 64% | 87% | 83% |
|  | Tight | 77% | 95% | 82% | 73% | 94% | 91% |
| R-2 | Leaky | 76% | 94% | 80% | 65% | 83% | 78% |
|  | Average | 82% | 96% | 85% | 74% | 88% | 85% |
|  | Tight | 87% | 97% | 90% | 84% | 95% | 93% |
| R-4 | Leaky | 79% | 95% | 82% | 67% | 83% | 79% |
|  | Average | 84% | 96% | 87% | 77% | 89% | 86% |
|  | Tight | 90% | 98% | 92% | 87% | 95% | 94% |
| R-8 | Leaky | 80% | 95% | 84% | 69% | 83% | 79% |
|  | Average | 86% | 97% | 89% | 79% | 89% | 87% |
|  | Tight | 92% | 98% | 94% | 90% | 95% | 94% |

FLHcool 		= Full load cooling hours

= Dependent on location as below:

| Climate Zone (City based upon) | FLHcool Single Family | FLHcool Multifamily |
| --- | --- | --- |
| 1 (Rockford) | 547 | 499 |
| 2 (Chicago) | 709 | 629 |
| 3 (Springfield) | 779 | 707 |
| 4 (Belleville) | 1,082 | 982 |
| 5 (Marion) | 956 | 868 |
| Weighted Average ComEd Ameren Statewide | 676 875 731 | 603 791 655 |

Use Multifamily if: Building meets utility’s definition for multifamily and system serves single unit. For residential sized systems serving 2 or more units, assume single family hours. For central systems use Volume 2 Commercial and Industrial Measures.

CapacityCool	= Capacity of Air Cooling system (Btu/hr)

= Actual

TRFcool	= Thermal Regain Factor for cooling by space type

= 1.0 for Unconditioned Spaces

= 0.4 for Semi-Conditioned Spaces

%Cool		= Percent of homes that have cooling

| Central Cooling? | %Cool |
| --- | --- |
| Yes | 100% |
| No | 0% |
| Unknown (for use in program evaluation only) | 66% |

1000		= Converts Btu to kBtu

ηCool		= Efficiency (SEER2) of Air Conditioning equipment (kBtu/kWh) * DistEffbase

DistEffbase	= Distribution Efficiency of base condition

= Actual where it is possible to measure or reasonably estimate. If unknown assume 0.85

= Actual. If unknown assume:

| Age of Equipment | SEER2 Estimate | ηCool (SEER2 * 0.85) |
| --- | --- | --- |
| Before 2006 | 9.5 | 8.1 |
| After 2006 - 2014 | 12.4 | 10.5 |
| Central AC After 1/1/2015 | 12.4 | 10.5 |
| Heat Pump After 1/1/2015 | 13.3 | 11.3 |
| Unknown (for use in program evaluation only) Single Family Non-IQ Single Family IQ Multi Family Non-IQ Multi Family IQ |  | 10.5 10.5 10.6 10.5 |

For example, duct sealing in unconditioned space in a single family house in Springfield, with 36,000 Btu/H SEER 11 central air conditioning and estimated 85% distribution efficiency, an 80% AFUE, 105,000 Btu/H natural gas furnace and the following duct evaluation results:

DEbefore		= 0.85

DEafter		= 0.92

Energy Savings:

ΔkWhcooling	= ((((0.92 – 0.85)/0.92) * 779 * 36,000 * 1 * 1) / 1000 / (11 * 0.85)) + (179 * 0.0314 * 29.3)

= 228 + 165

= 393 kWh

Heating savings for homes with electric heat:

ΔkWhheatingElectric	= ((DEafter – DEbefore)/ DEafter)) * FLHheatElec * OutputCapacityHeat * TRFheat * %ElectricHeat) / ηHeat / 3412

Where:

OutputCapacityHeat	= Heating output capacity (Btu/hr) of the electric heat

= Actual

FLHheatElec		= Full load heating hours for electric heat

= Dependent on location as below:

| Climate Zone (City based upon) | FLH_heat |
| --- | --- |
| 1 (Rockford) | 1924 |
| 2 (Chicago) | 1726 |
| 3 (Springfield) | 1708 |
| 4 (Belleville) | 1195 |
| 5 (Marion) | 1270 |
| Weighted Average ComEd Ameren Statewide | 1766 1547 1700 |

TRFheat 		= Thermal Regain Factor for heating by space type

= 0.40 for Semi-Conditioned Spaces

= 1.0 for Unconditioned Spaces

%ElectricHeat	= Percent of homes that have electric space heating

= 100 % for Electric Resistance (Baseboard or Electric Furnace) or Heat Pump

= 0 % for Natural Gas

= If unknown, use the following table:

| Utility | Location |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Single Family | Single Family Low Income | Multi Family | Multi Family Low Income | Unknown |
| Ameren | 14.0% | 13.7% | 37.2% | 56.3% | 19.5% |
| ComEd | 14.0% | 21.5% | 43.0% | 48.4% | 32.9% |
| PGL | 1.0% | 1.5% | 4.0% | 2.8% | 2.2% |
| NSG | 1.3% | 0.8% | 32.5% | 1.2% | 3.3% |
| Nicor | 1.6% | 3.8% | 13.5% | 21.6% | 4.7% |
| All DUs |  |  |  |  | 24.6% |

Note: If a measure is supported by a gas and electric utility through a joint program, and it is unknown whether the participant has a gas supply, the electric utility values in the table above should be used. If it is known that the participant has a gas supply, the values from the gas utility above should be applied.

ηHeat		= Coefficient of Performance of electric heating system * DistEffbase

DistEffbase	= Distribution Efficiency of base condition

= Actual where it is possible to measure or reasonably estimate. If unknown assume 0.85 for heat pump, 1.0 for resistance heating

= Actual. If not available use:

| System Type | Age of Equipment | HSPF2 Estimate | ηHeat (Effective COP Estimate * Distribution Efficiency) = (HSPF2/3.412)*0.85 |
| --- | --- | --- | --- |
| Heat Pump (if age unknown, assume 2006-2014) | Before 2006 | 5.8 | 1.44 |
|  | After 2006 - 2014 | 6.5 | 1.62 |
|  | 2015 on | 7.0 | 1.74 |
| Resistance (Baseboard or Electric Furnace) | N/A | N/A | 1.00 |
| Unknown (for use in program evaluation only) | N/A | N/A | 1.32 |

For example, duct sealing in unconditioned space in a 36,000 Btu/H, 2.5 COP heat pump heated with estimated 85% distribution efficiency single family house in Springfield with the following duct evaluation results:

DEafter		= 0.92

DEbefore		= 0.85

Energy Savings:

ΔkWhheating	= ((0.92 – 0.85)/0.92) * 1,708 * 36,000 * 1 * 1) / (2.5 * 0.85)) / 3,412

= 645 kWh

###### Summer Coincident Peak Demand Savings

ΔkW	= ΔkWhcooling/ FLHcool * CF

Where:

FLHcool		= Full load cooling hours:

= Dependent on location as below:

| Climate Zone (City based upon) | FLHcool Single Family | FLHcool Multifamily |
| --- | --- | --- |
| 1 (Rockford) | 547 | 499 |
| 2 (Chicago) | 709 | 629 |
| 3 (Springfield) | 779 | 707 |
| 4 (Belleville) | 1,082 | 982 |
| 5 (Marion) | 956 | 868 |
| Weighted Average ComEd Ameren Statewide | 676 875 731 | 603 791 655 |

Use Multifamily if: Building meets utility’s definition for multifamily and system serves single unit. For residential sized systems serving 2 or more units, assume single family hours. For central systems use Volume 2 Commercial and Industrial Measures.

CFSSP  	= Summer System Peak Coincidence Factor for Central A/C (during system peak hour)

= 68%

CFPJM 	= PJM Summer Peak Coincidence Factor for Central A/C (average during peak period)

= 46.6%

###### Fossil Fuel Savings

For homes with Fossil Fuel Heating:

Methodology 1: Modified Blower Door Subtraction

Methodology 2: Pressurized Duct Test

ΔTherm 	= (((∆CFM25DL / (InputCapacityHeat * 0.0123)) * FLHheatFossil * InputCapacityHeat * TRFheat * %FossilHeat * (ηEquipment / ηSystem)) / 100,000

Where:

∆CFM25DL	= Duct leakage reduction in CFM25

InputCapacityHeat	= Heating input capacity (Btu/hr)

=Actual

0.0123		= Conversion of Capacity to CFM (0.0123CFM / Btu/hr)

FLHheatFossil		= Full load heating hours for fossil heating

=Dependent on location as below:

| Climate Zone (City based upon) | FLHheatFossil |
| --- | --- |
| 1 (Rockford) | 1022 |
| 2 (Chicago) | 976 |
| 3 (Springfield) | 836 |
| 4 (Belleville) | 645 |
| 5 (Marion) | 656 |
| Weighted Average ComEd Ameren Statewide | 978 800 928 |

TRFheat 		= Thermal Regain Factor for heating by space type

= 0.40 for Semi-Conditioned Spaces

= 1.0 for Unconditioned Spaces

%FossilHeat	= Percent of homes that have gas space heating

= 100 % for Natural Gas

= 0 % for Electric Resistance (Baseboard or Electric Furnace) or Heat Pump

= If unknown, use the following table:

| Utility | Location |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Single Family | Single Family Low Income | Multi Family | Multi Family Low Income | Unknown |
| Ameren | 86.0% | 86.3% | 62.8% | 43.7% | 80.5% |
| ComEd | 86.0% | 78.5% | 57.0% | 51.6% | 67.1% |
| PGL | 99.0% | 98.5% | 96.0% | 97.2% | 97.8% |
| NSG | 98.7% | 99.2% | 67.5% | 98.8% | 96.7% |
| Nicor | 98.4% | 96.2% | 86.5% | 78.4% | 95.3% |
| All DUs |  |  |  |  | 75.4% |

Note: If a measure is supported by a gas and electric utility, utilize the assumptions above for the gas utility

100,000	= Converts Btu to therms

ηEquipment	= Heating Equipment Efficiency

= Actual. If not available, use 83%.

ηSystem	= Pre duct sealing Heating System Efficiency (Equipment Efficiency * Pre Distribution Efficiency)

= Actual. If not available, use 70%

For example, duct sealing in unconditioned space in a house in Springfield with an 80% AFUE, 105,000 Btu/H (input capacity) natural gas furnace and the following blower door test results:

Before: 	CFM50Whole House 	= 4800 CFM50

CFM50Envelope Only = 4500CFM50

House to duct pressure of 45 Pascals = 1.29 SCF (Energy Conservatory look up table)

After: 	CFM50Whole House 	= 4600 CFM50

CFM50Envelope Only = 4500CFM50

House to duct pressure of 43 Pascals = 1.39 SCF (Energy Conservatory look up table)

Duct Leakage:

CFM50DL before 	= (4800 – 4500) * 1.29

= 387 CFM

CFM50DL after 	= (4600 – 4500) * 1.39

= 119 CFM

Duct Leakage reduction at CFM25:

∆CFM25DL	= (387 – 139) * 0.64 * (0.5 + 0.25)

= 119 CFM25

Energy Savings:

Pre Distribution Efficiency		= 1 – (387/4800) = 92%

ηSystem 			= 80% * 92% 	= 74%

ΔTherm 	= ((119/ (105,000 * 0.0123)) * 836 * 105,000 * 1 *(0.8/0.74)) / 100,000

= 87.4 therms

Methodology 3: Evaluation of Distribution Efficiency

ΔTherm	= ((DEafter – DEbefore)/ DEafter)) * FLHheatFossil * InputCapacityHeat * TRFheat * %FossilHeat * (ηEquipment / ηSystem)) / 100,000

Where:

DEafter		= Distribution Efficiency after duct sealing, refer to table in electric savings section

DEbefore		= Distribution Efficiency before duct sealing, refer to table in electric savings section

Other factors as defined above.

For example, duct sealing in unconditioned space in a house in Springfield an 80% AFUE, 105,000 Btu/H (input capacity) natural gas furnace and the following duct evaluation results:

DEafter		= 0.92

DEbefore		= 0.85

Energy Savings:

ηSystem 	= 80% * 85% 	= 68%

ΔTherm 		= (((0.92 – 0.85)/0.92) * 836 * 105,000 * 1 * 1 * (0.8/0.68)) / 100,067

= 78.5 therm

Mid-Life Adjustment

In order to account for the likely replacement of existing heating and cooling equipment during the lifetime of this measure, a mid-life adjustment should be applied.

For electric HVAC, to calculate the adjustment, re-calculate the savings using the algorithms in the ‘Electric Energy Savings’ section using the following new baseline system efficiency assumptions:

| Efficiency Assumption | System Type | New Baseline Efficiency |
| --- | --- | --- |
| ηCool | Central AC | 13.4 SEER2 |
|  | Heat Pump | 14.3 SEER2 |
| ηHeat | Heat Pump (7.5/3.412) | 2.20 COP |

For gas fueled systems, because the algorithm uses input capacity (which already accounts for the equipment efficiency), the change in equipment efficiency needs to be accounted for. Therefore, re-calculate the savings using the following algorithm:

Methodology 1: Modified Blower Door Subtraction

Methodology 2: Pressurized Duct Test

ΔTherms       = ((∆CFM25DL / (InputCapacityHeat * 0.0123)) * FLHheatFossil * InputCapacityHeat * TRFheat * %FossilHeat * (ηEquipment / (ηEquipmentNew * DEafter)) / 100,000

Where:

ηEquipmentNew		= 80% AFUE

DEafter			= Distribution efficiency after duct sealing

= 1 – (CFM50DL After / CFM50Whole House After)

Methodology 3: Evaluation of Distribution Efficiency

∆Therms 	= ((DEafter – DEbefore)/ DEafter)) * FLHheatFossil * InputCapacityHeat * TRFheat * %FossilHeat * (ηEquipment / (ηEquipmentNew * DEafter)) / 100,000

Where:

ηEquipmentNew		= 80% AFUE

DEafter			= Distribution efficiency after duct sealing

= As evaluated using the Building Performance Institutes ‘Distribution Efficiency Look-Up Table’

The re-calculated reduced annual savings should be applied following the assumed remaining useful life of the existing equipment, estimated to be 10 years. Note: if the existing equipment efficiency is greater than the new baseline efficiency listed above, do not apply a mid-life adjustment.

###### Water Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code: RS-HVC-DINS-V15-260101

###### Review Deadline: 1/1/2028

### 5.7.4	Heat Pump Swimming Pool Heater

###### Description

This measure is applicable to electric heat pump pool heaters in residential applications. Heat pumps capture heat and move it from one place to another. The saving equations presented herein comprise three aspects of pool heating: convective heat loss via pool surface area due to water and air temperature differential, initial heat of full pool volume for seasonal pool use and reheat of pool refill on year round pools, and the heating of added pool water to offset water loss through evaporation. This measure applies to replacing either a gas-fired pool heater or a an electric resistance pool heater. If baseline equipment is a gas-fired pool heater, electric energy impacts result in additional electrical usage, but lower overall site energy usage.

This measure is only applicable to inground or outdoor single family home pools and is not applicable to spas. This measure is not applicable to community pools in multifamily housing complexes.

This measure was developed to be applicable to the following program types: TOS, NC, EREP.

###### Definition of Efficient Equipment

The efficient equipment is defined as a heat pump that is more efficient than Illinois energy code. This type of heat pump is designed to heat pool water for residential sized pools. Compliance condition of the equipment is that it is an AHRI-certified heat pump pool heater.

###### Definition of Baseline Equipment

The baseline reflects the existing pool water heater which could be natural gas, electric resistance or a less electric efficient heat pump water heater. The baseline equipment must be less efficient than that new equipment.

| Heating Type | Heat Pump Efficiency |
| --- | --- |
| Natural Gas | 82% Thermal Efficiency |
| Electric Resistance | 100% |
| Heat Pump | 3.5 COP |

The California Appliance Efficiency Regulations (Title 20) requires a minimum coefficient of performance (COP) of 3.5 for heat pump pool heaters and a minimum thermal efficiency (TE) of 82% for all natural residential pool water heaters.

###### Deemed Lifetime of Efficient Equipment

15 years.

###### Deemed Measure Cost

Estimated gross and incremental installation costs are listed below. Costs include material cost of heat pump, infrastructure for installation, and labor.

| Equipment Type | Gross Cost | Incremental Cost |
| --- | --- | --- |
| Gas Heater | $5,158 | N/A |
| Heat Pump Heater | $7,074 | $1,916 |

###### Loadshape

Loadshape R15 - Residential Pool Pumps

###### Coincidence Factor

The prescribed value for the coincidence factor is 0 for outdoor pools and is 0.8 for indoor pools.

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Non fuel switch measures:

Net site energy consumed at the site is calculated below:

∆kWh= BTUSurface+BTUReheat+BTUEvap3,412*1COPbaseline-1COPeeFfuel baselineEt,baseline+Felec,baselineCOPbaseline-1COPee

Fuel switch measures:

Fuel switch measures must produce positive total lifecycle energy savings (i.e., reduction in Btus at the premises) in order to qualify. This is determined as follows:

SiteEnergySavings (MMBTUs)	= [FossilHeatReplaced] – [ElectricHeatAdded]

FossilHeatReplaced	= BTUSurface+BTUReheat+BTUEvap1,000,000* Et,baseline*Ffuel baselineEt,baseline

ElectricHeatAdded	= BTUSurface+BTUReheat+BTUEvap1,000,000 * COPee*Ffuel baselineEt,baseline+Felec,baselineCOPbaseline-1COPee

If SiteEnergySavings calculated above is positive, the measure is eligible.

The appropriate savings claim is dependent on which utilities are supporting the measure as provided in a table below:

| Measure supported by: | Electric Utility claims (kWh): | Gas Utility claims (therms): |
| --- | --- | --- |
| Electric utility only | SiteEnergySavings * 1,000,000/3,412 | N/A |
| Electric and gas utility (Note utilities may make alternative agreements to how savings are allocated as long as total MMBtu savings remains the same). | %IncentiveElectric * SiteEnergySavings * 1,000,000/3,412 | %IncentiveGas * SiteEnergySavings * 10 |
| Gas utility only | N/A | SiteEnergySavings * 10 |

Where:

BTUSurface 	= Annual heating energy load contributed by convection/radiation heat losses via pool surface

=Tpool-Tamb*Apool*U*hrs- hrscover-ESFcover,surface

BTUReheat 	= Annual heating energy load contributed by heating the full volume of pool water

=Vpool*8.33*Tpool-Tmain*FReheat

BTUEvap 	= Annual heating energy load contributed by evaporation

=0.1*AF*Apool*Pω-Pdp*Tpool-Tmain*hrs-hrscover*ESFcover,evap

Felec,baseline 	= Baseline electric pool heater factor; used to account for the presence or absence of an electric pool heater.

= 1.0 if baseline system is electric resistance pool heater

= 0 if baseline system is not an electric resistance pool heater

Ffuel,baseline	 = Baseline fossil fuel pool heater factor; used to account for the presence or absence of a fossil fuel-fired pool heater.

= 1.0 if baseline system is fossil fuel-fired pool heater

= 0 if baseline system is not a fossil fuel-fired pool heater

COPbaseline 	= Coefficient of performance, ratio of output energy/input energy of baseline electric resistance pool heater, if present.

= 1.0 if heater is electric resistance; 3.5 if heater is a heat pump

COPee 	= Coefficient of performance, ratio of output energy/input energy of heat pump pool heater.

= Actual

Et,baseline 		= Thermal efficiency of baseline fossil fuel-fired pool heater, if present.

= 0.82 if unknown

Tpool 		= Pool temperature set point, (°F).

= Actual

Tamb 	= Average temperature of surrounding ambient air, (°F). If pool is indoors, this is the indoor temperature of room with pool from application. For outdoor pools, see “Ambient Air Temperature and Pressure (Tamb and Pdp)” table below.

Tmain 		= Supply water temperature in water main, (°F). See “Cold Water Inlet Temperature

(Tmain)” table below.

Apool 	= Surface area of pool, (ft2). From application. Assistance in determining the area of common pool shapes as follows:

Elliptical: 3.14 x short radius x long radius

Kidney Shaped: 0.45 x length x (width at one end x width at other end)

Oval: 3.14 x radius2 + (length of straight sides x width)

Rectangular: length x width

Vpool 		= Volume of pool water, (gallons)

= ActualFrom application.

FReheat 	= Factor capturing annual number of times full pool volume is heated to the desired temperature, whether as the result of refill or heating of pool water from ground water temperature at start of season. From application.

= 0 if pool is filled by delivery service providing preheated water

= 1 if otherwise

U		= Surface heat loss coefficient, (BTU/hr ft2 °F)

= 3.9 for indoor pool

= 5.3 for outdoor pool, sheltered

= 6.6 for outdoor pool, unsheltered

AF 	= Activity Factor, consideration of activity within pool, allowing for splashing and a limited area of wetted deck.

= 0.5

Pω 	= Saturation vapor pressure taken at surface water temperature, (in. Hg). See “Saturation Vapor Pressure (Pω)” table below based on pool water temperature.

Pdp 	= Saturation pressure at dew point, (in. Hg). See “Ambient Air Temperature and Pressure (Tamb and Pdp)” table below.

hrs 	= Total annual swimming season hours. From application. Hours shall reflect the total annual hours through the swimming season (number of days between season opening and season closing x 24).

hrscover 	= Total annual hours pool covered during the swimming season. From application. Hours shall reflect the total hours pool covered during the swimming season. Set equal to 0 if pool is left uncovered throughout swimming season.

ESFcover,surface 	= Energy Savings Factor of pool cover to insulate from convective and radiation heat losses

= 0.80

ESFcover,evap 	= Energy Savings Factor of pool cover to insulate from evaporative heat loss

= 0.95

0.1 	= Simplified empirically derived evaporation factor considering latent heat and air flow. Assumes 1,000 BTU/lb of latent heat required to change water to vapor at surface water temperature and air velocity over water surface ranging from 10 to 30 fpm, (lb/hr ft2 in. hg)

8.33 		= Energy required (BTU) to heat one gallon of water by one degree Fahrenheit

3,412 		= Conversion factor, one kWh equals 3,412 BTU

Cold Water Inlet Temperature (Tmain)

Supply water main temperatures vary according to climate, and are approximately equal to the annual average outdoor temperature plus 6°F. Supply main temperatures based on the annual outdoor temperature are shown below.

| Climate Zone | Annual Average Outdoor Temperature (°F) | Tmain (°F) |
| --- | --- | --- |
| 1 (Rockford) | 49.2 | 55.2 |
| 2 (Chicago) | 51.4 | 57.4 |
| 3 (Springfield) | 53.0 | 59.0 |
| 4 (Belleville) | 57.3 | 63.3 |
| 5 (Marion) | 56.5 | 62.5 |

Saturation Vapor Pressure (Pω)

Lookup saturation vapor pressure taken at surface water temperature for indoor and outdoor pools from the table below, based on pool temperature.

| Pool Temperature, Tpool (°F) | Pω (in. Hg) |
| --- | --- |
| 72 | 0.79 |
| 74 | 0.85 |
| 76 | 0.91 |
| 78 | 0.97 |
| 80 | 1.03 |
| 82 | 1.10 |
| 84 | 1.18 |

Ambient Air Temperature and Pressure (Tamb and Pdp)

Indoor pools shall apply ambient air temperature from application based on facility set point temperature. Lookup saturation vapor pressure based on facility set point temperature and relative humidity (RH) from the table below, based on psychrometric analysis. Interpolation may be performed for indoor pool ambient temperatures not listed.

| Indoor Pool Temperature, Tamb (°F) | Indoor Pool, Pdp (in. Hg) |  |  |
| --- | --- | --- | --- |
|  | RH 50% | RH 55% | RH 60% |
| 72 | 0.40 | 0.44 | 0.47 |
| 74 | 0.42 | 0.47 | 0.51 |
| 76 | 0.45 | 0.50 | 0.54 |
| 78 | 0.48 | 0.53 | 0.58 |
| 80 | 0.52 | 0.56 | 0.62 |
| 82 | 0.55 | 0.61 | 0.66 |
| 84 | 0.59 | 0.65 | 0.71 |
| 86 | 0.63 | 0.69 | 0.75 |

For outdoor pools, lookup Tamb and Pdp from the table below based on location. Ambient temperature averages for outdoor pools apply a 4-month swimming season.

| Climate Zone | Outdoor Pool Temperature Tamb (°F) | Outdoor Pool Pdp (in. Hg) |
| --- | --- | --- |
| 1 (Rockford) | 69.6 | 0.52 |
| 2 (Chicago) | 73.4 | 0.53 |
| 3 (Springfield) | 72.9 | 0.58 |
| 4 (Belleville) | 73.9 | 0.60 |
| 5 (Marion) | 74.8 | 0.62 |

Fuel Switch Example A gas pool heater is replaced with a heat pump pool heater at a single family home located near Chicago. The swimming season spans 4 months (2,904 hours) per year and the pool is left uncovered at night. The pool is 15 ft by 30 ft and has a volume of 17,600 gallons, and is sheltered from winds by the house and backyard trees. The pool temperature is maintained at 80°F. The replaced gas pool heater has an efficiency of 82% and the heat pump pool heater has an efficiency of 5.0 COP. Annual Electric Energy Savings, Summer Peak Coincident Demand Savings and Annual Fossil Fuel Energy Savings are calculated as below. Δ𝑘𝑊ℎ=(𝐵𝑇𝑈𝑆𝑢𝑟𝑓𝑎𝑐𝑒+𝐵𝑇𝑈𝑅𝑒ℎ𝑒𝑎𝑡+𝐵𝑇𝑈𝐸𝑣𝑎𝑝)/3,412×(𝐹𝑒𝑙𝑒𝑐,𝑏𝑎𝑠𝑒𝑙𝑖𝑛𝑒/𝐶𝑂𝑃𝑏𝑎𝑠𝑒𝑙𝑖𝑛𝑒−1/𝐶𝑂𝑃𝑒𝑒) Δ𝑘𝑊=Δ𝑘𝑊ℎ/ℎ𝑟𝑠×𝐶𝐹 Δ𝑀𝑀𝐵𝑡𝑢=(𝐵𝑇𝑈𝑆𝑢𝑟𝑓𝑎𝑐𝑒+𝐵𝑇𝑈𝑅𝑒ℎ𝑒𝑎𝑡+𝐵𝑇𝑈𝐸𝑣𝑎𝑝)/1,000,000 × 𝐹𝑓𝑢𝑒𝑙,𝑏𝑎𝑠𝑒𝑙𝑖𝑛𝑒/𝐸𝑡,𝑏𝑎𝑠𝑒𝑙𝑖𝑛𝑒 where: 𝐵𝑇𝑈𝑆𝑢𝑟𝑓𝑎𝑐𝑒=(𝑇𝑝𝑜𝑜𝑙−𝑇𝑎𝑚𝑏)×𝐴𝑝𝑜𝑜𝑙×𝑈×[ℎ𝑟𝑠−(ℎ𝑟𝑠𝑐𝑜𝑣𝑒𝑟×𝐸𝑆𝐹𝑐𝑜𝑣𝑒𝑟,𝑠𝑢𝑟𝑓𝑎𝑐𝑒)] 𝐵𝑇𝑈𝑅𝑒ℎ𝑒𝑎𝑡=𝑉𝑝𝑜𝑜𝑙×8.33×(𝑇𝑝𝑜𝑜𝑙−𝑇𝑚𝑎𝑖𝑛)×𝐹𝑅𝑒ℎ𝑒𝑎𝑡 𝐵𝑇𝑈𝐸𝑣𝑎𝑝=0.1×𝐴𝐹×𝐴𝑝𝑜𝑜𝑙×(𝑃𝜔−𝑃𝑑𝑝)×(𝑇𝑝𝑜𝑜𝑙−𝑇𝑚𝑎𝑖𝑛)×[ℎ𝑟𝑠−(ℎ𝑟𝑠𝑐𝑜𝑣𝑒𝑟×𝐸𝑆𝐹𝑐𝑜𝑣𝑒𝑟,𝑒𝑣𝑎𝑝)] Tpool = 80, from application Tamb = 73.4, from Ambient Air Temperature and Pressure section based on location from application Apool = width x length = 15’ x 30’ = 450 square feet Width and length from application U = 5.3, from Summary of Variables and Data Sources table based on conditions from application hrs = 2,904, from 121 day season or application hrscover = 0, from application ESFcover,surface = 0.8, from Summary of Variables and Data Sources table Vpool = 17,600, from application Tmain = 57.4, from Cold Water Inlet Temperature table based on location from application FReheat = 1, from Summary of Variables and Data Sources table AF = 0.5, from Summary of Variables and Data Sources table Pω = 1.03, from Saturation Vapor Pressure section based on pool temperature from application Pdp = 0.53, from Ambient Air Temperature and Pressure section based on location from application ESFcover,evap = 0.95, from Summary of Variables and Data Sources table Felec,baseline = 0, from Summary of Variables and Data Sources table based on application COPee = 5.0, from application CF = 0, from Summary of Variables and Data Sources table based on application Ffuel,baseline = 1, from Summary of Variables and Data Sources table based on application Et,baseline = 0.82, from application 𝐵𝑇𝑈𝑆𝑢𝑟𝑓𝑎𝑐𝑒=(80−73.4)×450×5.3×[2,904−(0)]=45,711,864 𝐵𝑡𝑢 𝐵𝑇𝑈𝑅𝑒ℎ𝑒𝑎𝑡=17,600×8.33×(80−57.4)×1=3,313,341 𝐵𝑡𝑢 𝐵𝑇𝑈𝐸𝑣𝑎𝑝=0.1×0.5×450×(1.03−0.53)×(80−57.4)×[2,904−(0)]=738,342 𝐵𝑡𝑢 ElectricHeatAdded =(45,711,864+3,313,341+738,342)/(1,000,000×5) = 10.0 MMBtu FossilHeatReplaced =(45,711,864+3,313,341+738,342)/1,000,000×0.82 =60.7 MMBtu Δ𝑀𝑀𝐵𝑡𝑢 Site Energy Savings is = 60.7 𝑀𝑀𝐵𝑡𝑢 – 10.0 𝑀𝑀𝐵𝑡𝑢 = 50.7 𝑀𝑀𝐵𝑡𝑢

###### Summer Coincident Peak Demand Savings

∆kW= BTUSurface+BTUReheat+BTUEvap3,412*Felec,baselineCOPbaseline-1COPee*CFhrs

Where CF value depends on location of pool

CF = 0 for outdoor pools

CF = 0.8 for indoor pools

###### Fossil Fuel Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

N/A

###### Deemed O&M Cost Adjustment Calculation

N/A

###### Measure Code:  RS-MSC-HPPH-V02-260101

###### Review Deadline: 1/1/2028

### 6.2.1	Voltage Optimization

###### Description

Voltage optimization (VO) is a smart grid technology that flattens voltage profiles and lowers average voltage levels on an electric power distribution grid. Lowering voltage reduces the instantaneous power consumed by customers on VO-enabled feeders, which in turn results in energy and demand savings. Voltage optimization is achieved through the operation of distributed sensors, two-way communications infrastructure, remote controls on substation transformer load-tap changers, voltage regulators and line capacitor banks, and integrating/optimizing software.

Unlike energy efficiency programs that achieve savings by providing financial incentives to encourage customers to adopt energy-efficient equipment or behavioral suggestions to encourage them to adopt no-cost energy-saving behaviors, VO involves no direct customer engagement. Instead, savings are achieved by operating the voltage and reactive power controls on VO-enabled feeders in a manner designed to maintain the voltages delivered to affected customers in the lower part of the allowable voltage range.

In general, reducing the voltage on a feeder reduces power consumed by the connected loads, assuming all other factors of the feeder remain constant. This is a realistic assumption for many types of consumer devices. However, there are several scenarios in which decreasing voltage does not directly result in energy and demand savings. For example, some devices (e.g., electronics) have self-contained control systems that maintain constant power consumption despite the delivered voltage. Other devices increase their power draw when presented with reduced voltage due to nonlinear inefficiencies. Still other devices (e.g., resistive heating) might decrease instantaneous power draw but operate for longer periods; thus their total energy consumption remains approximately constant (similar to the time-shifting effects of demand response programs). This means VO is more effective in reducing load for some device types than others. This may lead it to be more or less effective for specific feeders depending on the exact mix of device types the feeder has.

This measure was developed to be applicable to the following program types: Voltage Optimization. This measure is unique and does not apply to other program types.

###### Definition of Efficient Equipment

To qualify for this measure, feeders must be enabled with VO technology and have VO fully commissioned and operational.

###### Definition of Baseline Equipment

The baseline assumption is a feeder without any VO technology.

###### Deemed Lifetime of Efficient Equipment

VO Energy Savings can be renewed every 15 years and have a maximum measure life of 50 years . The renewal would claim the same savings as the original measure for an additional 15 years (up to a maximum of 50 years) after verifying that VO is still operational on the feeder in a manner consistent with the operation that led to the original TRM savings estimate.  This does not preclude future consideration of (and TRM development for) a potential new measure that provides greater savings than the VO measure characterized here.

Within the EE Plan submittal ComEd and Ameren shall prepare a planned activation summary of all feeders whose energy savings are set to expire within the timeframe the EE Plan is active. This planned activation summary will indicate the planned activation status of VO feeders in an ‘enabled’ or ‘disabled’ format along with the total energy savings in MWh of each activation status. This check-in will be performed at the same cadence the EE plan is submitted. Once confirmed, the energy savings shall be credited for 15 years until the next renewal period and for a maximum of 50 years. However, if the utility ever ceases to operate VO in such a manner on any circuits, it will report such changes to evaluators and stop claiming persisting savings on such circuits in the year following the year in which operations ceased (even if less than the TRM measure life).

###### Deemed Measure Cost

The costs vary by feeder. Actual costs should be used.

###### Loadshape

Loadshape C67 –  Voltage Optimization – Ameren

Loadshape C68 –  Voltage Optimization –  ComEd

###### Coincidence Factor

N/A

Algorithm

###### Calculation of Energy Savings

###### Electric Energy Savings

Annualized savings should be calculated separately for each VO-enabled feeder. The savings reductions during VO On/Off testing shall not be a basis to reduce the estimated savings. The off periods from testing shall be treated as if they were on during the evaluation period.

ΔkWh = kWhBASE * ΔV * CVRf

Where:

kWhBASE		= Baseline kWh consumption on the feeder per year

For Ameren territory, use the average annual customer energy use for each feeder over the 2019-2021 timeframe, less energy use by exempt customers.

For ComEd territory, use annual energy consumption using the actual energy measurement during the time when VO was off (as appropriate; this may include the actual measurements prior to VO activation during the given program year and from prior program years and VO OFF periods from subsequent program years) and a calculated VO OFF value for the time when VO was on. The VO OFF baseline energy for the periods when VO is on shall be calculated using:

EVO_OFF=EVO_ON1-(CVRf*∆V)

Where:

EVO_OFF 	= the calculated VO OFF energy consumption when VO is on (activated)

EVO_ON 	= the actual measured energy consumption during the period when VO is on

∆V 	= the voltage reduction

CVRf 	= the CVR factor

      - Where power (MW) data has not been established yet, best available data from the feeder line measurement devices should be considered.

      - Data are clustered into bins according to temperature range, season, day type (weekday/weekend), and hour of the day based on the VO OFF and ON statuses to create a lookup table. If multiple data points are found (i.e., same temperature range, same season, same day type, same hour of the day, and same VO status), the average of  multiple references are placed into the lookup table. Various combinations of these variables may be used in an order of decreasing priority when no data points are found that match all of them.

      - The independent evaluator shall use best practices, including an appropriate technique that is transparent, replicable, and most accurate, to address any data quality issues, with input from interested stakeholders, including ComEd.

      - The following approach will be used for claiming kWh savings from no-load and future feeders. ComEd installs new feeders every year to accommodate area load growth. Some of them are sourced from previously claimed VO-activated substations or exist with no-load on transformers where VO is being activated in a given year. Examples of when a new feeder will be installed include, as part of a new business project to accommodate a new or existing customer’s load addition, or to relieve area loading congestion and contingency planning for the purpose of increasing capacity. ComEd projects load on some of these feeders over a future period, however, there are uncertainties regarding when the projected target loads will materialize.

ComEd cannot claim VO savings for a newly commissioned feeder while there is no load but can claim when a pre-defined threshold of the feeder’s projected load is reached. A threshold of 70% of projected load for 6 months is adopted for ComEd.  To be eligible for savings, the feeder must add load to the substation transformer rather than simply splitting existing load among the feeders sourced from same transformer.

ComEd will maintain a list of existing feeders with no-load along with their projected load, to be updated as needed, and will share it with their evaluator so they can make comparisons to the threshold when the feeder is claimed. Changes can be made to the projected load, as needed, with justification. When such feeders reach the threshold of 70% of their projected load for 6 months, ComEd will notify their evaluator and provide relevant feeder and associated substation transformer data to evaluators for the purpose of verifying savings to claim in the annual impact evaluation report.

ΔV		= Percentage voltage reduction on the feeder caused by VO

For Ameren territory, voltage reduction shall be calculated using a pre-post regression model (i.e., comparing pre-VO and post-VO installation). The model specification will be selected based on model fit and may vary year to year. The model will be run in accordance with the terms provided in subsections (i) through (iv) below:

- The model utilizes pre-period (VO OFF) data from the feeders in question from the prior calendar year.

- Voltage (V) data is sourced from customer AMI meters. The feeder average voltage is calculated as the average of at least 70% of the AMI meters on the feeder, whenever possible. AMI voltage readings are normalized by their nominal voltage before averaging voltage across the AMI meters on a given feeder.

- Ameren and stakeholders have agreed on a list of excludable events, during which Ameren may claim VO savings if the system is down for reasons deemed appropriate. Please see Table 1 below for further explanation and list of excludable and non-excludable events.

- The independent evaluator shall use best practices, including an appropriate technique that is transparent, replicable, and most accurate, to address any data quality issues, with the input from interested stakeholders, including Ameren.

For ComEd territory, voltage reduction shall be calculated from voltage measurements taken from the feeder’s head end primary voltage source using the following equation and in accordance with the terms provided in subsections (i) through (iv) below:

∆V=VOFF-VONVOFF

- When VO is off, the voltage if VO was on needs to be estimated and vice versa. Actual measurements shall be used for the off voltage when VO is off and the on voltage when VO is on.

- Data are clustered into bins in accordance to temperature range, season, day type (weekday/weekend), and hour of the day based on the VO OFF and ON statuses to create a lookup table. If multiple data points are found (i.e., same temperature range, same season, same day type, same hour of the day, and same VO status), the average of  multiple references are placed into the lookup table. Various combinations of these variables may be used in an order of decreasing priority when no data points are found that match all of them.

- The independent evaluator shall use best practices, including an appropriate technique that is transparent, replicable, and most accurate, to address any data quality issues, with the input from interested stakeholders, including ComEd.

- The counterfactual VO ON and VO OFF profiles shall be created for each feeder for the entire program year using the lookup table for temperature range, season, day type (weekday/weekend), and hour of the day.

- If VO is ON in a continuous basis throughout the year, previous year’s voltage data along with temperature, day type, and time of the day can be correlated in accordance to present year’s temperature data, day type, and time of the day to create the VO OFF profile.  This correlation shall use the data created from the most representative feeder or feeders that have undergone testing.

- For the no-load and future feeders, ComEd’s evaluator will use the evaluated historical transformer voltage reduction for each feeder going back to the year when the station or transformer was originally VO-enabled.

CVRf	= conservation voltage reduction factor relating the change in voltage to a change in energy

= 0.80  (for both Ameren and ComEd territories)

###### Summer Coincident Peak Demand Savings

Peak demand savings should be calculated separately for each VO-enabled feeder. The savings reductions during  VO On/Off testing shall not be a basis to reduce the estimated savings. The off periods from testing shall be treated as if they were on during the evaluation period.

ΔkW = kWBASE * ΔVPEAK * CVRf,PEAK

Where:

kWBASE	= Baseline kW usage on the feeder during the peak period, defined as 1:00-5:00 pm CDT on non-holiday weekdays from June 1 to August 31.

For Ameren territory, this will be calculated as the average demand in the peak hour for each feeder over the 2019-2021 timeframe, adjusted by a calibration factor that describes the relationship between demand in the peak hour and average demand over the peak period (defined as 1:00-5:00 pm CDT on non-holiday weekdays from June 1 to August 31).  This calibration factor will be calculated based on a sample of feeders for which 2019-2021 data is available.

For ComEd territory, this will be calculated in the same manner as kWhBASE for energy savings but with the intent of estimating the baseline just for the peak period as opposed to for the entire year.

ΔVPeak	= Percentage voltage reduction on the feeder caused by VO during the peak period, defined as 1:00 – 5:00 pm CDT on non-holiday weekdays from June 1 to August 31.

For Ameren territory, this will be calculated in the same manner as ΔV for energy savings but with the intent of estimating ΔV just for the peak period as opposed to for the entire year.

For ComEd territory, this will be calculated in the same manner as ΔV for energy savings but with the intent of estimating ΔV just for the peak period as opposed to for the entire year.

CVRf,PEAK	= conservation voltage reduction factor relating the change in voltage to a change in energy specifically for the peak period, defined as 1:00 – 5:00 pm CDT on non-holiday weekdays from June 1 to August 31

For Ameren territory, 0.68.

For ComEd territory, 1.02.

###### Excludable and Not-Excludable Events In Calculating Electric Savings

Both Ameren and ComEd have established a set of excludable (where VO is off, but savings can be claimed as if VO is on) and not-excludable (where VO is off, and savings cannot be claimed) events. These events can be accounted for either by: 1) determining the percentage of time non-excludable events occur and de-rating the savings by this percentage (ComEd’s approach), or 2) removing the excludable events from the dataset used to calculate savings (Ameren’s approach).

Below are tables of events each utility has established as excludable and non-excludable. Changes or additions can be made to these tables with the consensus of the utilities, the independent evaluator, and ICC staff (none of whose

consensus shall not be unreasonably withheld).

Table 1. Ameren Excludable and Non-Excludable VO Events

| Event | Description | Reason/Explanation | Category |
| --- | --- | --- | --- |
| Feeder Outage | Anytime the majority of a feeder is out due to any reason. | Feeder outages are typically not predictable or planned and are outside of Ameren’s control. They are an anomaly and are not certain to occur on the same feeder in subsequent years. | Excludable |
| Repair / Maintenance | Repair or maintenance work is performed on a VO feeder causing VO to be disabled. | Repair and maintenance of Ameren’s system is an operational necessity to provide customers with safe and reliable electric service. These events are not certain to occur on the same feeder in subsequent years. | Excludable |
| Switching | Dispatch disables VO on the feeder for any necessary switching event. | Ameren will perform switching for storms, outages, repair, maintenance, safety, and work to support new customer growth. These events are not certain to occur on the same feeder in subsequent years. | Excludable |
| Technology | A failure of the Information and/or Communication Technology which results in "all" VO feeders being disabled simultaneously due to events outside of Ameren’s control. | VO is dependent upon third party infrastructure that Ameren has no control over. Examples include the loss of the cellular communications network (AT&T and Verizon), the failure of the VO Software provided by the outside vendor, or a Cyber event. Events of this nature are an anomaly and are not certain to occur year after year. This event is not predictable or planned and is outside of Ameren’s control. | Excludable |
| Worldwide Pandemic / Orders by Civil Authorities | Repairs and maintenance may take longer due to limited crew availability or other restrictions/priorities. Example: COVID-19 | Due to restrictions, repairs and maintenance may take longer. This reasonable delay is outside the control of Ameren. | Excludable |
| Disaster Recovery (DR) Testing | Ameren periodically performs Disaster Recovery testing on systems (AMI, ADMS, VO, etc.) which could result in VO disabling. Typically all VO feeders would be affected during DR testing. | Disaster Recovery is necessary and critical to ensure that Ameren can operate safely and effectively during an unforeseen event. | Not-Excludable |
| Server patching/issues | Anytime servers go down or patching takes place and the VO system does not come back online due to servers not rebooting correctly. | Events of this nature are unavoidable, but should be addressed by Ameren in a timely fashion. This should result in negligible impacts to energy savings. | Not-Excludable |
| Configuration Changes | Anytime VO is disabled for making updates to the Orion, go-live testing, or to make changes on the system resulting in shutting down services. | Events of this nature are unavoidable, but should be addressed by Ameren in a timely fashion. This should result in negligible impacts to energy savings. | Not-Excludable |
| VO field hardware failures | The loss or failure of a voltage regulator control, LTC control, or switched capacitor control on a feeder. | Events of this nature are unavoidable, but should be addressed by Ameren in a timely fashion. This should result in negligible impacts to energy savings. | Not-Excludable |
| Loss of communications | Anytime a device has a communications failure that would result in VO disabling. This event does not include 3rd party cellular communications network (AT&T and Verizon) failures. | Events of this nature are unavoidable, but should be addressed by Ameren in a timely fashion. This should result in negligible impacts to energy savings. | Not-Excludable |

Table 2. ComEd Excludable and Non-Excludable VO Events

| Event | Description | Reason/Explanation | Category |
| --- | --- | --- | --- |
| System Operational Requirements | OCC takes control and disables VO due to station/feeder out of configuration, major alarm, repair/maintenance or switching events. | Feeder outages are typically not predictable or planned and are outside of ComEd control. ComEd will take necessary steps to ensure the reliability and safety of the system during storms and outages, maintenance, and work to support new customer growth. These events are not certain to occur on the same feeder in subsequent years. | Excludable |
| Loss of communication | Any unplanned interruption to the communication network. | Natural causes or unplanned repair due to equipment failure occasionally disrupting communication network. | Excludable |
| VO Control System | System component failure requires vendor upgrade or revision. | The failure of the VO Software provided by the outside vendor (OSI), or a Cyber event. Events of this nature are an anomaly and are not certain to occur year after year. This event is not predictable or planned and is outside of ComEd’s control. | Excludable |
| VO On/Off Cycling Schedule | Supervision over the transitional states from on to off, and vice versa. | When adding or commissioning substations or feeders to the VO Control system. | Excludable |
| Customer Maintenance | VO is disabled to investigate power quality issues. | Possible VO deactivation may be required to facilitate certain investigation requirements. | Not-Excludable |
| Worldwide Pandemic / Orders by Civil Authorities | Repairs and maintenance may take longer due to limited crew availability or other restrictions and priorities. Example: COVID-19 | Due to restrictions, repairs and maintenance may take longer. This reasonable delay is outside the control of ComEd. | Excludable |
| VO Control System | Anytime VO system fails to operate due to model error in VO software, or inappropriate manual settings (human error). | Events of this nature should be addressed by ComEd in a timely manner, resulting in negligible impacts to energy savings. | Not-Excludable |
| Loss of communication | Any planned system upgrade that interrupts communication. | Planned system patching or upgrades interfere with the communication network and disable VO. This should be addressed by ComEd in a timely manner, resulting in negligible impacts to energy savings. | Not-Excludable |
| Equipment | Equipment failure that results in VO feeders being disabled (MJ5/DCIAB). | The equipment failure should be addressed by ComEd in a timely manner. This should result in negligible impacts to energy savings. | Not-Excludable |
| Server patching/ issues | Anytime servers would go down or if patching took place and VO system did not come back online due to servers not rebooting correctly. | Events of this nature are unavoidable but should be addressed by ComEd in a timely manner. This should result in negligible impacts to energy savings. | Not-Excludable |

###### Fossil Fuel Savings

N/A

###### Water and Other Non-Energy Impact Descriptions and Calculation

VO may provide non-monetized energy benefits in the form of improved ability to manage the grid “downstream” of the substation. This could result in improved reliability, lower spending on other grid improvements, or both. Further research is needed to understand the scope and impact of these potential benefits. There are no water savings or non-energy impacts from VO.

###### Deemed O&M Cost Adjustment Calculation

There are annual O&M costs incurred by the utility as a result of implementation of VO. Cost-effectiveness analysis should include estimates of annual O&M costs over the initial 15-year period and then for each incremental renewal period up to 50 years of the VO investment, discounted to present value for the year in which the VO investment is being analyzed. O&M cost estimates should include (a) labor and equipment costs to maintain the system and (b) third-party software costs.

###### Measure Code: CC-SYS-VOPT-V04-260101

###### Review Deadline: 1/1/2028

Consistent with the definition of Review Deadline in TRM Volume 1 (Overview), the Voltage Optimization working group collectively acknowledges that this date does not represent a commitment or obligation to revise TRM content by this dat

Iowa State University Ag Extension, “Computing a Grain Storage Rental Rate”, October 2013. The useful life of grain storage bins was estimated to be between 15 and 25 years and the drying equipment useful life was estimated to be between 10 and 12 years. Combined with engineering judgement, the estimated measure life for a high efficiency grain dryer is estimated to be 20 years, which is corroborated by the Wisconsin Focus on Energy 2025 Technical Reference Manual, Cadmus, Publish Service Commission of Wisconsin – Energy Efficient Grain Dryer, January 2025.

Alliant Energy Custom Rebate project data from 2012-2014; original Alliant table was modified, adding a new column of hours per year use and renaming labels.  Annual tier production quantities (bushels/yr) were divided by the maximum nominal tier capacities (bushels/hr @ rated capacity) to obtain Hours per Year @ Rated Capacity.  Arithmetic average hours of use was 336.3 per year.

Wisconsin Focus on Energy project data; 13 recent grain dryer projects in Wisconsin were used as the source of average pre- and post- moisture content (23% and 15%, respectively) and baseline and proposed dryer efficiency.

The National Corn Handbook. “Energy Conservation and Alternative Sources for Corn Drying.” NCH-14, page 3, Table 4.

Based on customer project data as sourced from Wisconsin Focus on Energy implementation database and reproduced in the 2025 Wisconsin Focus on Energy TRM, Energy Efficient Grain Dryer, January 2025 (project data:13 recent grain dryer projects in Wisconsin were used as the source of average pre- and post- moisture content (23% and 15%, respectively) and baseline and proposed dryer efficiency.)

“Tables for Weights and Measurement: Crops”. Murphy, William J.

"Reducing Grain Drying Costs". Sanford, Scott., University of Wisconsin Rural Energy Program, 2013. Notes 20-30% savings in bin dryers through the use of stirrers and ambient air low temperatiure drying. Based on this, 71% is used as a conservative value, but Actual values can be used if available. Accessed August 19, 2020.

Alliant Energy Custom Rebate project data from 2012-2014; same comments apply as in prior footnote.

The Standard Dryer Fan Power using the fan brakehorsepower equation.

The same Dryer Fan Power formula as in the above footnote.

”Gates Corporation Announces New EPDM Molded Notch V-Belts,” The Gates Rubber Co., June 2010 (Assumed 3% efficiency improvement).

“Synchronous Belt Drives Offer Low Cost Energy Savings,” Baldor. February 2009. (attached in Reference Documents).

"Energy Savings from Synchronous Belts," The Gates Rubber Co., February 2014. (Assumed 5% efficiency improvement).

“Motor System Tip Sheet #5, Replace V-Belts with Cogged or Synchronous Belt Drives,” USDOE-EERE, September 2005. (Assumed 2% efficiency improvement).

ComEd Trm June 1, 2010 page 139. The Office hours is based upon occupancy from the eQuest model developed for EFLH, since it was agreed the ComEd value was too low.

“DEER2014-EUL-table-update_2014-02-05.xlsx,” Database for Energy Efficiency Resources (DEER), DEER2014 EUL Table. (attached in Reference Documents).

Grainger catalog on-line web-site for Dayton v-belt pricing.

Assumed to be $150 based on mechanical contractor estimate.

Based on review and trend fitting cost data from Grainger online. See reference document “Notched V Belts costs.xlsx” for derivation.

Note that kWConnected may be determined using various methodologies. The examples provided use rated HP and assumed load factor. Other methodologies include rated voltage and full load current with assumed load factor, or actual measured voltage and current.

Com Ed TRM June 1, 2010.

Efficiency values for motors less than one HP taken from Baldor Electric Catalog 501, standard motor product catalog.

Hours per year are estimated using the eQuest models as the total number of hours the fans are operating for heating, cooling and ventilation for each building type.

Based on information found in Advanced Manufacturing Office, US DOE, “Replace V-Belts with Notched or Synchronous Drives”, (US Department of Energy Motor Systems Tip Sheet #5, DOE/GO-102012-3740,  November 2012). V-belt drives can have a peak efficiency of 95% and synchronous belts operate at 98%, therefore ESF is (1-95%/98%) = 3.1%.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

ASHRAE 2010 6.5.1.2.1 Design Capacity. Water economizer systems shall be capable of cooling supply air by indirect evaporation and providing up to 100% of the expected system cooling load at outdoor air temperatures of 50° F dry bulb/45° F wet bulb and below.

(2008 Database for Energy-Efficiency Resources (DEER), Version 2008.2.05, “Effective/Remaining Useful Life Values”, California Public Utilities Commission, December 16, 2008)

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Waterside Economizers: Tower Side Temperatures (online), Norm Hall, June 2023

NCEI NCDC 15 year climate normals (2006 – 2020) total hours per year less than 50° F

The measure life is sourced from the PG&E Workpaper, “Add Doors to Open Medium Temperature Cases – PGE3PREF116 R3”, June 2019.

The incremental cost is sourced from the PG&E Workpaper, “Add Doors to Open Medium Temperature Cases – PGE3PREF116 R3”, June 2019. The incremental cost for retrofitting new doors on existing refrigerated display cases is the material cost of the door and the labor cost required for installation. The material cost of the doors is $331 per linear foot with LED lighting and $301 per linear foot without LED lighting. And the installation cost is $88 per linear foot.

The change in heat gain is sourced as the typical value for a medium temperature vertical display case adding doors from the PG&E Workpaper, "Add Doors to Open Medium Temperature Cases - PGE3PREF116 R3", June 2019. The workpaper assumes a net reduction in heat gain with the installation of doors on open refrigerated display cases. The primary benefits account for the decrease in excess heat entering the display case from air infiltration. Radiation and conduction heat gains were also included in the derivation of this value. Additionally, the net heat gain has built in assumptions on how often the refrigerated case doors will be used and the display case accessed by customers and site associates, reducing some of the air infiltration benefits of the new door.

Average load difference between Hussmann open horizontal cases and lid horizontal cases across various configurations.

Average EER values were calculated as the average of standard reciprocating and discus compressor efficiencies, using a typical condensing temperature of 90°F and saturated suction temperatures (SST) of 20°F for medium temperature applications. The efficiency analysis and product review are sourced from the Efficiency Vermont TRM, which utilizes data from Emerson Climate Technology software. Medium temperature cases have an EER value of 11.36.

The measure assumes the baseline equipment is not employing night covers or any other covering but is in fact left open for the duration of its operation.

The MMBtu increase on the HVAC cooling equipment is based on an outdoor air temperature bin analysis, the total hours of operation of the cooling system, and the building's overall loss of additional cooling because of the installation of the doors on the open refrigerated display case. The analysis assumes a certain amount of conditioned air has to be treated to replace the air previously cooled by the display case. Furthermore, the analysis assumes an increased load on the cooling system, at outdoor temperatures above 60°F. A 25% disabling factor was also applied to account for some of the cold air pouring out of the display case and subcooling the site's conditioned space, which will not trigger a thermostatic response from the HVAC equipment. For more information on the analysis used to derive the load increase on the HVAC cooling equipment per linear foot of display case, please see the 'HVAC IE' tab in the "IL TRM_Add Doors_Analysis_Mar 2021.xlsx".

Based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Nonresidential Baseline Study Results”, Oct 31 2024. Note SEER value converted to SEER2 by multiplying by 0.95, and multiplied by 0.95 distribution efficiency.

Southern California Edison Refrigeration Technology and Test Center. Effects of the Low Emissivity Shields on Performance and Power Use of a Refrigerated Display Case. 1997. Southern California Edison, Rancho Cucamonga, CA. See ‘4.6.9 Night Covers’ for more detail.

Technischer Uberwachungs-Verein Rheinland E.V. Laboratory test results for energy savings on refrigerated dairy case, conducted for Econofrost. See ‘4.6.9 Night Covers’ for more detail.

The total combined hours in which the site is providing cooling is based on an outdoor air temperature bin analysis, where the site is conditioning cold air at outdoor temperatures of 60°F and above. Weather data was sourced from TMY3 data for the specific locations. For more information on the derivation of these hours, please see 'HVAC IE' tab in the "IL TRM_Add Doors_Analysis_Mar 2021.xlsx" Night covers are not included in the peak demand savings algorithm because night covers are deployed at night, outside of the peak demand period.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The AC load during the utility’s peak hour is divided by the maximum AC load during the year.

The MMBtu decrease on the HVAC heating equipment is based on an outdoor air temperature bin analysis, the total hours of operation in which the site is providing heat, and the building's overall reduced heating load as a result of the installation of the doors on the open refrigerated display case. The analysis assumes a certain reduction of conditioned air that had to be treated to make up for the air previously cooled by the display case. The reduced heat gain on the refrigerated display case equals the reduced heat loss by the site and a heating load that no longer has to be provided by the HVAC system. Furthermore, the analysis assumes a decrease load on the heating system, at outdoor temperatures below 60°F. A 25% disabling factor was also applied to account for some of the cold air pouring out of the display case and subcooling the site's conditioned space, which will not trigger a thermostatic response from the HVAC equipment. For more information on the analysis used to derive the load decrease on the HVAC heating equipment per linear foot of display case, please see the 'HVAC IE' tab in the "IL TRM_Add Doors_Analysis_Mar 2021.xlsx".

Based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Nonresidential Baseline Study Results”, Oct 31 2024. Total heating capacity provided by 54% Furnace and 46% Boiler at 83.1% and 85.8% AFUE respectively, multiplied by estimate of distribution losses of 95%.

Public Service Commission of Wisconsin, “Evaluation – Business Program: Measure Life Study,” Focus on Energy (2009): page 1-4, Table 1-2 Recommended Measure Life by WISeerts Group Description for Building Shell Equip or Tech measure type, accessed March 26, 2019,  https://focusonenergy.com/sites/default/files/bpmeasurelifestudyfinal_evaluationreport.pdf.

Leakage area is estimated based on average door size of installations previously completed in Wisconsin and reported in the Wisconsin Focus on Energy Technical Reference Manual. Average door size is 10 ft x 12 ft, with a side and top perimeter equal to 1 top * (10 ft * 12 in/1 ft) + 2 sides* (12 ft * 12 in/1ft) = 408 in. At 1/8 in perimeter gap, the leakage area is 408 in * 1/8 in = 51 in2.

2017 ASHRAE Handbook—Fundamentals, 16.24, Table 4 “Basic Model Stack Coefficient Cs”, assumed average building height of 16 feet, two-story.

2017 ASHRAE Handbook—Fundamentals, 16.24, Table 6 “Basic Model Wind Coefficient Cw”, assumed average building height of 16 feet and shelter class 3: “Typical shelter caused by other buildings across street from building under study.”

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL, for the average outdoor temperature when the heating system is expected to be operating.

Energy Center of Wisconsin, “Baseline Building Energy Models – Nonresidential Heating Thermostat Setpoint,” ComEd Portfolio Modeling Report (July 2010): page 6.

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL, for the average wind speed when the heating system is expected to be operating, defined as hours where the average temperature is lower than 55°F.

Engineering ToolBox, (2003). Air - Density, Specific Weight and Thermal Expansion Coefficient at Varying Temperature and Constant Pressures. [online] Available at: https://www.engineeringtoolbox.com/air-density-specific-weight-d_600.html [Accessed March 2019].

Engineering ToolBox, (2004). Air - Specific Heat at Constant Pressure and Varying Temperature. [online] Available at: https://www.engineeringtoolbox.com/air-specific-heat-capacity-d_705.html [Accessed March 2019].

Based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Nonresidential Baseline Study Results”, Oct 31 2024. Note HSPF value converted to HSPF2 by multiplying by 0.85. Effective COP estimated as 7.37/3.413 * 0.95 (to estimate distribution losses).

Based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Nonresidential Baseline Study Results”, Oct 31 2024. Value based on weighting AFUE and Thermal Efficiency, and incorporating estimate of distribution losses of 0.95.

Presentation on the “Operating Cost Reduction Strategies for Oxidizers”, presented by Rich Grzanka, during the Chem Show Technology Exposition on October 31, 2007.

Ibid.

EPA Air Pollution Control Cost Manual, Chapter 2, November 2017. The system capital recovery cost is based on an estimated 20-year equipment life. This estimate of oxidizer equipment life is consistent with information available to EPA and is consistent with statements from large vendors for incinerators and oxidizers.

U.S. Environmental Protection Agency, Incinerators and Oxidizers, Chapter 2, November 2017.

ICAC Guidance Method for Estimation of Gas Consumption in a Regenerative Thermal Oxidizer (RTO), July 2002.

Ibid.

National Centers for Environmental Information (NCEI) 15 yr US Climate Normals 2006-2020. Average Annual Temperatures taken for each climate zone (ANN-TAVG-NORMAL)

Biomass Energy Data Book, 2011, Appendix A: Lower and Higher Heating Values of Gas, Liquid, and Solid Fuels.

Heat content of natural gas delivered to consumers per the Energy Information Administration, Independent Statistics & Analysis, 2018.

U.S. Environmental Protection Agency, Incinerators and Oxidizers, Chapter 2, November 2017.

In the event that the ENERGY STAR program is ended, the last effective ENERGY STAR specification should continue to be used through the effective period of this TRM.

DOE Energy Conservation Standards for Clothes Washers, Appliance and Equipment Standard, 10 CFR Part 430.32(g)

Weighted average IMEF of Federal Standard rating for Front Loading and Top Loading units. Weighting is based upon the relative top v front loading percentage of available non-ENERGY STAR product in the CEC database (products accessed on 04/21/2022).

ENERGY STAR Draft 2 Version 1.0 Clothes Dryers Data and Analysis

Federal standards report CEF for gas clothes dryers in terms of lbs/kWh. To determine gas savings, this number is later converted to therms.

Lifetime of 14 years per Residential Clothes Washers Life-Cycle Cost Analysis Spreadsheet posted by the Energy Efficiency and Renewable Energy Office on Sep 23, 2021.

The cost of buying a new market available all-in-one clothes washer-dryer with HP technology from Home Depot have been averaged for three different manufacturers. These products are ENERGY STAR certified. See “Incremental Cost R&D.xls” for information.

The baseline cost is assumed to be the cost of a standard efficiency clothes washer in addition to the cost of a standard efficiency clothes dryer. A standard clothes washer cost ($763.98) is based on analysis of cost data provided in the Retail Price Data from DOE Analytical Tool (Lifecycle Cost and Payback Period Analysis) for Negotiated Standards, 2017, and weighted by a market share of 49.4% Top-Loading to 50.6% Front-Loading machines. The cost of a standard dryer ($564) is from “ACEEE Clothes Dryers.pdf.”

IQ Incremental costs factor in the assumption that a secondhand unit costs on average 50% of a new baseline unit, and that 1/3 of IQ participants would have purchased a unit on the secondhand market. See “IQ Appliance Calculations.xls” for information.

Calculated from Itron eShapes, 8760 hourly data by end use for Missouri, as provided by Ameren.

Non-Fuel Switch Measures apply in cases where inefficient electric equipment is being replaced with efficient electric equipment. Assume DHW fuel remains consistent between baseline and efficient scenario. Clothes washer unit savings are always non-fuel switch; however thermal savings can exist in applications with gas DHW.

The energy savings algorithm from the clothes dryer and clothes washer has been calculated individually to create the final algorithm for the Energy Star Combination All-in-One Clothes Washer-Dryer. The dryer section from the clothes washer algorithm has been excluded. See “Energy Star Combination All-in-One Clothes Washer-Dryer Calculations.xls” for information.

Electric consumption that accounts for the fact that some of the consumption on gas DHW Clothes Washer comes from electricity (motors, controls, etc).

Average of ENERGY STAR & ENERGY STAR MOST EFFICIENT Residential Combination All-in-One Washer-Dryer. April 2024. https://www.energystar.gov/productfinder/product/certified-clothes-washers.

Weighted average IMEF of Federal Standard rating for Front Loading and Top Loading units. Weighting is based upon the relative top v front loading percentage of available non-ENERGY STAR product in the CEC database (products accessed on 04/21/2022).

It is assumed that a second-hand unit is on average 2/3 of a measure’s EUL years old (9 years). The baseline consumption of a unit meeting the pre 03/2015 Federal Standard was increased by an estimate of 0.4% * 9 years (based on review of the refrigerator/freezer regression algorithm used in the 5.1.8 Refrigerator and Freezer Recycling measure) to account for degradation of performance over time. For 2025 on, the post 03/2015 Federal Standard is utilized. This second hand consumption was then weighted 1/3: 2/3 current new baseline to estimate a multiplier for IQ participants. See “IQ Appliance Calculations.xls” for information.

The energy measurements are performed at an ISO/IEC accredited lab as specified in the application process for the ENERGY STAR & ENERGY STAR Most Efficient. Approved products on the ENERGY STAR Qualified Products List 2024-04-23 have IMEF, IWF values listed for clothes washer and CEF values for clothes dryer.

Loads per week was estimated by taking the weighted average of the number of loads per week (midpoint used where loads per week is a range and the weights are the share of respondents falling into each number of loads per week response bin). This estimate was scaled to an IL-specific value by applying a ratio developed using the 2009 state specific values for the states in the East North Central portion of the Midwest Region. This value was then scaled to apply to a consistent amount of laundry washed over time.

The percentage of total energy consumption that is used for the machine, heating the hot water or by the dryer is different depending on the efficiency of the unit. Values are based on a weighted average of top loading and front loading units based on data from the 2017 DOE Life-Cycle Cost and Payback Period Excel-based analytical tool. See “IL TRM_CW Analysis_082024.xlsx” for the calculation.

Ameren and Nicor values are based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Residential Baseline Study Results”, Oct 31 2024. ComEd values based on 2019 Baseline Survey and People’s Gas and Northshore Gas values are based on implementation contractors data for PY2022-2023.

For the weighted average calculations, please see the Analysis file. PGL, NSG, Nicor & gas customers were assumed to follow the provided split. ComEd total customers, minus overlap with PGL,NSG & Nicor, therefore electric only homes. Ameren is total customers minus Nicor.

Based on ENERGY STAR test procedures

It is assumed that a second-hand unit is on average 2/3 of a measure’s EUL years old (11 years). The current Federal Standard became effective in 2015 so the previous standard is used to estimate base consumption for a second hand unit, and further increased by an estimate of 0.4% * 11 years (based on review of the refrigerator/freezer regression algorithm used in the 5.1.8 Refrigerator and Freezer Recycling measure) to account for degradation of performance over time. This second hand consumption was then weighted 1/3: 2/3 current new baseline to estimate a multiplier for IQ participants. See “IQ Appliance Calculations.xls” for information.

%Electric accounts for the fact that some of the savings on gas dryers comes from electricity (motors, controls, etc). 16% was determined using a ratio of the electric to total savings from gas dryers given by ENERGY STAR Draft 2 Version 1.0 Clothes Dryers Data and Analysis.

Ameren and Nicor values are based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Residential Baseline Study Results”, Oct 31 2024. ComEd values based on 2019 Baseline Survey and People’s Gas and Northshore Gas values are based on implementation contractors data for PY2022-2023.

For the weighted average calculations, please see the Analysis file. PGL, NSG, Nicor & gas customers were assumed to follow the provided split. ComEd total customers, minus overlap with PGL,NSG & Nicor, therefore gas only homes. Ameren is total customers minus Nicor.

To account for the different efficiency of electric and Natural Gas hot water heaters (gas water heater: recovery efficiencies ranging from 0.74 to 0.85 (0.78 used), and electric water heater with 0.98 recovery efficiency (see ENERGY STAR Waste Water Recovery Guidelines). Therefore a factor of 0.98/0.78 (1.26) is applied.

%Gas accounts for the fact that some of the savings on gas dryers comes from electricity (motors, controls, etc). 84% was determined using a ratio of the gas to total savings from gas dryers given by ENERGY STAR Draft 2 Version 1.0 Clothes Dryers Data and Analysis.

The peak energy savings algorithm from the clothes dryer and clothes washer has been calculated individually to create the final algorithm for the Energy Star Combination All-in-One Clothes Washer-Dryer. The dryer section from the clothes washer algorithm has been excluded. See “Energy Star Combination All-in-One Clothes Washer-Dryer Calculations.xls” for information.

Based on an average of reported cycle times for a normal load of models on the ENERGY STAR QPL.

Weighted average IWF of Federal Standard rating for Front Loading and Top Loading units. Weighting is based upon the relative top v front loading percentage of available non-ENERGY STAR product in the CEC database (products accessed on 04/21/2022).

It is assumed that a second-hand unit is on average 2/3 of a measure’s EUL years old (9 years). The baseline consumption from the TRM in 2015 is assumed the second hand water consumption (note we do no assume a degradation over time for water consumption) was then weighted 1/3: 2/3 current new baseline to estimate a multiplier for IQ participants. See “IQ Appliance Calculations.xls” for information.

Baseline clothes washer capacity is assumed to have 4.9 cu.ft. with 233 wash cycles for clothes washer.

This factor includes 2571 kWh/MG for water supply based on Illinois energy intensity data from a 2012 ISAWWA study and 2439 kWh/MG for wastewater treatment based on national energy intensity use estimates. For more information, please review Elevate Energy’s ‘IL TRM: Energy per Gallon Factor, May 2018 paper’.

Building Performance Institute, Distribution Efficiency Look-up Tables. https://www.bpi.org/sites/default/files/Guidance%20on%20Estimating%20Distribution%20Efficiency.pdf

Definition matches Regain factor discussed in Home Energy Services Impact Evaluation, prepared for the Massachusetts Residential Retrofit and Low Income Program Area Evaluation, Cadmus Group, Inc., August 2012

Measure Life Report, Residential and Commercial/Industrial Lighting and HVAC Measures, GDS Associates, June 2007.

This is intentionally longer than the assumptions found in the early replacement measures as the application of this measure will occur in a variety of homes that will not be targeted for early replacement HVAC systems.

Based on metering of 24 homes with central AC during PY4 and PY5 in Ameren Illinois service territory.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

25 Pascals is the standard assumption for typical pressures experienced in the duct system under normal operating conditions. To convert CFM50 to CFM25 you multiply by 0.64 (inverse of the “Can’t Reach Fifty” factor for CFM25; see Energy Conservatory Blower Door Manual).

Assumes that for each percent of supply air loss there is one percent annual energy penalty. This assumes supply side leaks are direct losses to the outside and are not recaptured back to the house. This could be adjusted downward to reflect regain of usable energy to the house from duct leaks. For example, during the winter some of the energy lost from supply leaks in a crawlspace will probably be regained back to the house (sometimes 1/2 or more may be regained). More information provided in “Appendix E Estimating HVAC System Loss From Duct Airtightness Measurements” from Energy Conservatory ‘Minneapolis Duct Blaster Operation Manual’.

Assumes 50% of leaks are in supply ducts.

Assumes that for each percent of return air loss there is a half percent annual energy penalty. Note that this assumes that return leaks contribute less to energy losses than do supply leaks. This value could be adjusted upward if there was reason to suspect that the return leaks contribute significantly more energy loss than “average” (e.g. pulling return air from a super heated attic), or can be adjusted downward to represent significantly less energy loss (e.g. pulling return air from a moderate temperature crawl space) . More information provided in “Appendix E Estimating HVAC System Loss From Duct Airtightness Measurements” from Energy Conservatory ‘Minneapolis Duct Blaster Operation Manual’.

Assumes 50% of leaks are in return ducts.

This conversion is an industry rule of thumb; e.g. see ‘Why 400 CFM per ton.pdf’.

Based on Full Load Hours from ENERGY STAR with adjustments made in a Navigant Evaluation, other cities were scaled using those results and CDD. There is a county mapping table in Volume 1, Section 3.7 providing the appropriate city to use for each county of Illinois. During update cycle for version v.12, applied percent change of CDD65, NCEI Annual Normals from 30 yr data set (1981-2010) to more recent 15 yr data (2006-2020) to all FLHcool values.

Weighting for Ameren is based on electric accounts in each of the cooling zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Thermal regain (i.e. the potential for conditioned air escaping from ducts not being lost to the atmosphere) for residential pipe insulation measures is discussed in Home Energy Services Impact Evaluation, prepared for the Massachusetts Residential Retrofit and Low Income Program Area Evaluation, Cadmus Group, Inc., August 2012.

Based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Residential Baseline Study Results”, Oct 31 2024.

Based on Building Performance Institute Inc., “Duct Efficiency Tables”.

These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Central AC was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time mean that using the minimum standard is appropriate. Note all ratings have been converted to SEER2 equivalents – since the new rating better reflects the actual efficiency of the units.

Efficiencies presented above are weighted as per data provided by GDS Associates Inc., “2023-2024 Illinois Baseline Study: Residential Baseline Study Results”, Oct 31 2024.

Fe is not one of the AHRI certified ratings provided for residential furnaces, but can be reasonably estimated from a calculation based on the certified values for fuel energy (Ef in MMBtu/yr) and Eae (kWh/yr).  An average of a 300 record sample (non-random) out of 1495 was 3.14%.  This is, appropriately, ~50% greater than the ENERGY STAR version 3 criteria for 2% Fe. See “Programmable Thermostats Furnace Fan Analysis.xlsx” for reference.

Heating EFLH based on ENERGY STAR EFLH for Rockford, Chicago, and Springfield and on NCDC/NOAA HDD for the other two cities. In all cases, the hours were adjusted based on average natural gas heating consumption in IL.

Weighting for Ameren is based on electric heat accounts in each of the heating zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Thermal regain (i.e. the potential for conditioned air escaping from ducts not being lost to the atmosphere) for residential pipe insulation measures is discussed in Home Energy Services Impact Evaluation, prepared for the Massachusetts Residential Retrofit and Low Income Program Area Evaluation, Cadmus Group, Inc., August 2012.

Ameren and Nicor values are based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Residential Baseline Study Results”, Oct 31 2024. ComEd values based on 2019 Baseline Survey and People’s Gas and Northshore Gas values are based on implementation contractors data for PY2022-2023.

For the weighted average calculations, please see the Analysis file. PGL, NSG, Nicor & gas customers were assumed to follow the provided split. ComEd total customers, minus overlap with PGL,NSG & Nicor, therefore electric only homes. Ameren is total customers minus Nicor.

Based on Building Performance Institute Inc., “Duct Efficiency Tables”.

These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Heat Pumps was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time means that using the minimum standard is appropriate. Note all ratings have been converted to HSPF2 equivalents – since the new rating better reflects the actual efficiency of the units.

Calculation assumes 35% Heat Pump and 65% Resistance, which is based upon data from Energy Information Administration, 2009 Residential Energy Consumption Survey, see “HC6.9 Space Heating in Midwest Region.xls”, using average for East North Central Region. Average efficiency of heat pump is assumed consistent with the baseline for 2006-2014. Program or evaluation data should be used to improve this assumption if available.

Building Performance Institute, Distribution Efficiency Look-up Tables, Climate Zones 4-5. https://www.bpi.org/sites/default/files/Guidance%20on%20Estimating%20Distribution%20Efficiency.pdf

Ibid

Based on Full Load Hours from ENERGY STAR with adjustments made in a Navigant Evaluation, other cities were scaled using those results and CDD. There is a county mapping table in Volume 1, Section 3.7 providing the appropriate city to use for each county of Illinois. During update cycle for version v.12, applied percent change of CDD65, NCEI Annual Normals from 30 yr data set (1981-2010) to more recent 15 yr data (2006-2020) to all FLHcool values.

Weighting for Ameren is based on electric accounts in each of the cooling zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Thermal regain for residential pipe insulation measures is discussed in Home Energy Services Impact Evaluation, prepared for the Massachusetts Residential Retrofit and Low Income Program Area Evaluation, Cadmus Group, Inc., August 2012.

Percentage of homes in Illinois that have central cooling from “Table HC7.9 Air Conditioning in Homes in Midwest Region, Divisions, and States, 2009” from Energy Information Administration, 2009 Residential Energy Consumption Survey

Based on Building Performance Institute Inc., “Duct Efficiency Tables”.

These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Central AC was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time means that using the minimum standard is appropriate. Note all ratings have been converted to SEER2 equivalents – since the new rating better reflects the actual efficiency of the units.

Efficiencies presented above are weighted as per data provided by GDS Associates Inc., “2023-2024 Illinois Baseline Study: Residential Baseline Study Results”, Oct 31 2024.

Heating EFLH based on ENERGY Star EFLH for Rockford, Chicago, and Springfield and on NCDC/NOAA HDD for the other two cities. In all cases, the hours were adjusted based on average natural gas heating consumption in IL.

Weighting for Ameren is based on electric heat accounts in each of the heating zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Thermal regain for residential pipe insulation measures is discussed in Home Energy Services Impact Evaluation, prepared for the Massachusetts Residential Retrofit and Low Income Program Area Evaluation, Cadmus Group, Inc., August 2012.

Ameren and Nicor values are based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Residential Baseline Study Results”, Oct 31 2024. ComEd values based on 2019 Baseline Survey and People’s Gas and Northshore Gas values are based on implementation contractors data for PY2022-2023.

For the weighted average calculations, please see the Analysis file. PGL, NSG, Nicor & gas customers were assumed to follow the provided split. ComEd total customers, minus overlap with PGL,NSG & Nicor, therefore electric only homes. Ameren is total customers minus Nicor.

Note that the HSPF2 of a heat pump is equal to the COP * 3.412.

Based on Building Performance Institute Inc., “Duct Efficiency Tables”.

These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Heat Pumps was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time means that using the minimum standard is appropriate. Note all ratings have been converted to HSPF2 equivalents – since the new rating better reflects the actual efficiency of the units.

Calculation assumes 35% Heat Pump and 65% Resistance, which is based upon data from Energy Information Administration, 2009 Residential Energy Consumption Survey, see “HC6.9 Space Heating in Midwest Region.xls”, using average for East North Central Region. Average efficiency of heat pump is assumed consistent with the baseline for 2006-2014. Program or evaluation data should be used to improve this assumption if available.

Based on Full Load Hours from ENERGY Star with adjustments made in a Navigant Evaluation, other cities were scaled using those results and CDD. There is a county mapping table in Volume 1, Section 3.7 providing the appropriate city to use for each county of Illinois. During update cycle for version v.12, applied percent change of CDD65, NCEI Annual Normals from 30 yr data set (1981-2010) to more recent 15 yr data (2006-2020) to all FLHcool values.

Weighting for Ameren is based on electric accounts in each of the cooling zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Based on metering of 24 homes with central AC during PY4 and PY5 in Ameren Illinois service territory.

Based on analysis of Itron eShape data for Missouri, calibrated to Illinois loads, supplied by Ameren. The average AC load over the PJM peak period (1-5pm, M-F, June through August) is divided by the maximum AC load during the year.

Based on Natural Draft Furnaces requiring 100 CFM per 10,000 Btu, Induced Draft Furnaces requiring 130CFM per 10,000Btu and Condensing Furnaces requiring 150 CFM per 10,000 Btu (rule of thumb from ‘Practical Standards to Measure HVAC System Performance’). Data provided by GAMA during the federal rule-making process for furnace efficiency standards, suggested that in 2000, 24% of furnaces purchased in Illinois were condensing units. Therefore, a weighted average required airflow rate is calculated assuming a 50:50 split of natural v induced draft non-condensing furnaces, as 123 per 10,000Btu or 0.0123/Btu.

Full load hours for Chicago, are based on findings in ‘Energy Efficiency / Demand Response Nicor Gas Plan Year 1 (6/1/2011-5/31/2012) Research Report: Furnace Metering Study (August 1, 2013), prepared by Navigant Consulting, Inc. Values for other cities are then calculated by comparing relative HDD at base 60F.

Weighting for Ameren is based on gas accounts in each of the heating zones. Weighting for ComEd and Statewide average is based on number of occupied residential housing units in each zone. ComEd is weighted average of Zones 1-2. Alternative program-weighted assumptions can be used if appropriate.

Thermal regain for residential pipe insulation measures is discussed in Home Energy Services Impact Evaluation, prepared for the Massachusetts Residential Retrofit and Low Income Program Area Evaluation, Cadmus Group, Inc., August 2012.

Ameren and Nicor values are based on GDS Associates Inc., “2023-2024 Illinois Baseline Study: Residential Baseline Study Results”, Oct 31 2024. ComEd values based on 2019 Baseline Survey and People’s Gas and Northshore Gas values are based on implementation contractors data for PY2022-2023.

For the weighted average calculations, please see the Analysis file. PGL, NSG, Nicor & gas customers were assumed to follow the provided split. ComEd total customers, minus overlap with PGL,NSG & Nicor, therefore gas only homes. Ameren is total customers minus Nicor.

The Equipment Efficiency can be obtained either by recording the AFUE of the unit, or performing a steady state efficiency test.

If there are more than one heating systems, the weighted (by consumption) average efficiency should be used.

If the heating system or distribution is being upgraded within a package of measures together with the insulation upgrade, the new average heating system efficiency should be used.

This has been estimated assuming that natural gas central furnace heating is typical for Illinois residences (66% of Illinois homes have a Natural Gas Furnace (based on Energy Information Administration, 2009 Residential Energy Consumption Survey). In 2000, 24% of furnaces purchased in Illinois were condensing (based on data from GAMA, provided to Department of Energy during the federal standard setting process for residential heating equipment - see Furnace Penetration.xls). Furnaces tend to last up to 20 years and so units purchased 10 years ago provide a reasonable proxy for the current mix of furnaces in the State. Assuming typical efficiencies for condensing and non-condensing furnaces and duct losses, the average heating system efficiency is estimated as follows:

(0.24*0.92) + (0.76*0.8) =  0.829

The Distribution Efficiency can be estimated via a visual inspection and by referring to a look up table such as that provided by the Building Performance Institute: (see ‘DistributionEfficiencyTable-Blue Sheet’) or by performing duct blaster testing.

Estimated as follows: 0.829 * (1-0.15) =  0.70

This is intentionally longer than the assumption found in the early replacement measures as the application of this measure will occur in a variety of homes and will not be targeting those homes appropriate for early replacement HVAC systems.

ASHRAE Handbook: HVAC Applications, 2019, pg 51.25. ASHRAE states that except in aboveground pools and rare cases where cold groundwater flows past the pool walls, conductive losses through pool walls are small and can be ignored. ASRHAE additionally indicates that radiation losses that occur due to sky temperature differentials at night may be offset by solar heat gains of an unshaded pool during the day.

New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs –  Residential, Multi-family, and Commercial/Industrial Measures Version 9

Department of Energy. “10 CFR 430.32 - Energy and water conservation standards and their effective dates.” Section (k) (2).

Database for Energy Efficient Resources (DEER). “2014 DEER Update Study.” July 17, 2013. http://www.deeresources.com/files/home/download/DEER2014UpdatePlan-July2013-v1.pdf

California Technical Reference Manual for Energy Efficiency. Southern California Edison (SCE). 2021. "SWRE005-01 Cost Analysis.xlsm.”

ASHRAE Handbook: HVAC Applications, 2019, Ch 51 Service Water Heating, Swimming Pools/Health Clubs.

Ibid, eqn. 14

ASHRAE Handbook: HVAC Applications, 2019, Ch 6 Indoor Swimming Pools, eqn. 3, multiplied by required heating temperature difference

Guidance for determining surface area of common pool shapes can be found at ASHRAE Handbook: HVAC

Applications, 2019.

The water temperature of an undrained pool between swim seasons is assumed to have reached the water main

temperature by the beginning of the next swim season. If the pool remains open throughout the year, it is assumed

the pool undergoes one effective full pool volume reheat from water main temperature for cleaning and other

maintenance (CDC, Healthy Swimming, Operating Public Swimming Pools).

ASHRAE Handbook: HVAC Applications, 2019, Ch 51, eqn. 15. Surface heat loss coefficient adjusted from

ASHRAE Handbook rolled up surface heat transfer conservations by discounting contribution of evaporation (50-

60%) and applying the following assumption for wind velocity: Indoor pools experience average wind speeds less

than 3.5 mph (10.5x0.5x0.75), outdoor sheltered pools experience wind speeds between 3.5 and 5 mph (10.5x0.5),

and outdoor unsheltered pools experience wind speeds above 5 mph (10.5x0.5x1.25).

ASHRAE Handbook, Applications, 2019, Ch 6, Table 1

U.S. D.O.E., Swimming Pool Covers.

National Plasterers Council, Effectiveness of Pool Covers to Reduce Evaporation from Swimming Pools,

prepared by California Polytechnic State University, January 2016.

Simplified constant presented in ASHRAE Handbook: HVAC Application 2019 Ch 6 based on empirically derived eqn (2) constants and ASHRAE’s variable assumptions

Burch, Jay and Christensen, Craig, “Towards Development of an Algorithm for Mains Water Temperature.”

National Renewable Energy Laboratory, January 2007

Average annual outdoor temperatures taken from NCDC 1981-2010 climate normals.  https://www.ncdc.noaa.gov/cdo-web/datatools/normals

ASHRAE Handbook: Fundamentals 2017, Ch 1 Psychrometrics, Table 3 Thermodynamic Properties of Water at

Saturation

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL. Adjusted to apply to outside air temperature from June 1 to September 30 in each climate zone.

DOE Weather Data, TMY3 (Typical Meteorological Year), developed by NREL. Saturation pressure at dew point calculated as a function of dew point and atmospheric pressure. Values averaged from June 1 to September 30 in each climate zone.

Voltage optimization is also referred to a volt-var optimization (VVO) or conservation voltage reduction (CVR).

For the purposes of this measure, the term feeder is synonymous with circuit.

The bulk of the energy savings that occurs is thus expected to occur on the customer side of the meter, although additional savings is expected from reduced current flows along the full length of the affected feeders.

Note that any VO On/Off testing for the purposes of evaluation or updating the TRM will not be counted against the utility in claiming savings. VO On/Off testing is an experimental design that involves enabling and disabling the VO system under a predefined schedule for the purposes of testing its functionality. By following a predefined schedule, the VO On/Off design enables modeling of the impact of VO while controlling for factors that may vary over time, such as weather or weekday vs. weekend loads.

For ComEd, the first renewal can start in CY2033 with the renewal of CY2018 feeders.  For Ameren, the first renewal can start in CY2034 with the renewal of CY2019 feeders

Climate and Equitable Jobs Act (CEJA), Public Act 102-0662, “(b-20) Each electric utility subject to this Section may include cost-effective voltage optimization measures in its plans submitted under subsections (f) and (g) of this Section, and the costs incurred by a utility to implement the measures under a Commission-approved plan shall be recovered under the provisions of Article IX or Section 16-108.5 of this Act. For purposes of this Section, the measure life of voltage optimization measures shall be 15 years. The measure life period is independent of the depreciation rate of the voltage optimization assets deployed. Utilities may claim savings from voltage optimization on circuits for more than 15 years if they can demonstrate that they have made additional investments necessary to enable voltage optimization savings to continue beyond 15 years. Such demonstrations must be subject to the review of independent evaluation.”

VO On/Off testing is an experimental design that involves enabling and disabling the VO system under a predefined schedule for the purposes of testing its functionality. By following a predefined schedule, the VO On/Off design enables modeling of the impact of VO while controlling for factors that may vary over time, such as weather or weekday vs. weekend loads.

If the energy consumption baseline is measured at the feeder head, an adjustment will be made to recognize line losses and loss savings.

Temperature bins are to the ceiling of the nearest 5°F interval.

Seasons are defined as follows; Spring: March through May; Summer: June through August; Fall: September through November; and Winter: December through February.

Weekdays are Monday to Friday and weekends are Saturday and Sunday.

This threshold was determined based on the discussion between ComEd’s Capacity planning and Voltage Optimization group. To determine the value, ComEd considered several factors including the timeline of commissioning any future feeder, load ramping up for large customers, and the comments received from ICC and Guidehouse to claim the feeders as soon as ComEd expects to have full load. ComEd considers a feeder to have reached its full load when 70% of the projected load (at the minimum) has been materialized.

In cases when less than 70% of the AMI meters are programmed to record voltage data, all available meters will be used, with the goal of utilizing as close to 70% of the meters as possible.

Temperature bins are to the ceiling of the nearest 5°F interval.

Seasons are defined as follows; Spring: March through May; Summer: June through August; Fall: September through November; and Winter: December through February.

Weekdays are Monday to Friday and weekends are Saturday and Sunday.

Temperature bins are to the ceiling of the nearest 5°F interval.

Seasons are defined as follows; Spring: March through May; Summer: June through August; Fall: September through November; and Winter: December through February.

Weekdays are Monday to Friday and weekends are Saturday and Sunday.

This is recommended by ComEd to ensure consistency that all the feeders under the same transformer receive same average voltage reduction using both timeseries VO ON and OFF data from the testing period.

Guidehouse. 2020. Supporting Documentation for Voltage Optimization TRM Measure. <Add hyperlink when available>

Ibid.

Ibid.